ERCOT Operations Report

Feb 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 2/15/2012 4:03 | 59.804 | 148 | Unit trip with 560 MW net. |
| 2/18/2012 2:48 | 59.890 | 20 | Unit trip with 185 MW net. Expected Gen Deviation -800 including the unit trip. |
| 2/18/2012 19:00 | 59.878 | 12 | Unit trips with 274 MW net. Expected Gen Deviation -800 including the unit trip. |
| 2/18/2012 21:17 | 59.729 | 128 | Unit trip with 740 MW net. |
| 2/25/2012 6:34 | 59.893 | 4 | Unit trips with 297 MW net. Expected Gen Deviation -800 including the unit trip |
| 2/28/2012 10:55 | 59.892 | 36 | Unit trip with 681 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 2/15/12 4:03:22 | 2/15/12 4:07:06 | 0:03:44 | 610.43 |  |
| 2/18/12 2:48:26 | 2/18/12 2:54:10 | 0:05:44 | 171.31 |  |
| 2/18/12 19:00:58 | 2/18/12 19:02:42 | 0:01:44 | 215.7 |  |
| 2/18/12 21:17:17 | 2/18/12 21:20:14 | 0:02:57 | 1059.3 |  |
| 2/26/12 21:04:56 | 2/26/12 21:09:28 | 0:04:32 | 431.15 | Expected Gen Deviation -1100. Frequency went to 59.904 |
| 2/28/12 10:53:15 | 2/28/12 10:57:28 | 0:04:13 | 112.54 |  |

RUC Commitments

None

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Bluff Creek 345/138 kV XFMR2 | Nicole - Oak Creek AEP 138kV | 18 |
| Aspermont - Spur 138kV | Spur - Girard Tap 69 kV | 18 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North 345/138 kV AXFMR1 | 13 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 9 |
| Pawnee - Lon Hill 345kV | Sinton - Skidmore 69 kV | 9 |
| Sacroc - Snyder 138 kV | Sun Switch - Morgan Creek SES 138 kV | 8 |
| Salt Creek BEPC - Spur 138 kV | Spur - Girard Tap 69 kV | 7 |
| Basecase | Enas Snyder Wind - Wkn_BKR 69 kV | 6 |
| Sun Switch - Morgan Creek SES 138 kV | Sun Switch - Sacroc 138 kV | 6 |
| Wharton - East Bernard 138 kV | Lane City - Blessing 138 kV | 4 |
| DCKT Graham SES - Parker 345 kV | Barton Switch - Oran Sub 138 kV | 4 |
| Lewisville Switch - Carrolton Northwest 345kV | Jones Street TNP - Lewisville Switch | 4 |
| DCKT Graham SES - Long Creek 345 kV | Hamilton - Maverick 138 kV | 3 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 3 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 3 |
| Nelson Sharpe - Ajo 345kV | Harlingen Switch - Raymondville 69kV | 3 |
| Basecase | Eskota Switch 138/69 kV AXFMR1 | 2 |
| Brackettville - Asphalt Mine 138 kV | Harlingen Switch – Raymondville 69 kV | 2 |
| Brackettville - Asphalt Mine 138 kV | Hamilton - Maverick 138 kV | 2 |
| Ajo - Riohondo 345kV | Celanese Bishop - Kleberg 138 kV | 2 |
| Crane Arco Tap - Pegasus 138 kV | Woodward 2 - 16th Street TNP 138 kV | 2 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 2 |
| DCKT Graham SES - Long Creek 345 kV | Paint Creek - Murray 138 kV | 1 |
| Ajo - Riohondo 345kV | Celanese Bishop - Nelson Sharpe 138 kV | 1 |
| Coleman Lake Ivie Tap - East Coleman 138 kV | Ballinger - Humble Ballinger 69kV | 1 |
| DCKT Big Brown SES - Richland Chambers 345 kV | Trinidad SES 345/138kV AT6 | 1 |
| Lon Hill 138/69 kV AXFMR2 | Lon Hill 138/69 kV AXFMR1 | 1 |
| Fort Worth Substation - West Denton 138 kV | West Denton - Jim Christal Substation 138kV | 1 |
| DCKT Morgan Creek SES - Bitter Creek & Sweetwater Cogen 345 kV | Tonkawa Switch - Morgan Creek SES 345 kV | 1 |
| San Angelo Red Creek 345/138 kV XFMR T2 | San Angelo Red Creek 345/138 kV XFMR1 | 1 |
| Victoria - Coleto Creek 138 kV | Coleto Creek - Victoria 138 kV | 1 |
| Rodd Field - Holly 138 kV | Airline - Cabaniss 138 kV | 1 |
| DCKT Willow Creek - Parker Switch 345 kV | West Denton - Fort Worth 138 kV | 1 |
| Salt Creek BEPC - Spur 138 kV | Spur - Girard Tap 69 kV | 1 |
| DCKT Tradinghouse SES - Venus Switch 345 kV | Elm Mott - Rogers Hill 138 kV | 1 |
| DCKT Sandow Switch - Austrop 345kV | Temple Switch - Salado Switch 345 kV | 1 |
| Red Oak - Trumbull 138 kV | Ennis West Switch - Waxahachie 138 kV | 1 |
| Coleto Creek - Pawnee Switch 345 kV | Coleto Creek - Victoria 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 17 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

2/02 14:40  	ERCOT issued an emergency notice for SCED failure for intervals 14:40 through 15:15. The notice was cancelled at 15:15.

Communication Issues

None

## ERCOT peak (Unofficial)

02/13 08:00 42,035MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | NA |
| April | 2.66 | 2.47 | 3.55 | NA |
| May | 2.90 | 2.63 | 3.27 | NA |
| June | 2.89 | 2.84 | 2.28 | NA |
| July | 2.83 | 2.39 | 1.63 | NA |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.73 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 2/8/2012 | 10:00 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/8/2012 | 18:38 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/12/2012 | 20:12 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/15/2012 | 7:23 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/18/2012 | 21:34 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/24/2012 | 19:11 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/27/2012 | 10:08 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/28/2012 | 19:10 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 2/29/2012 | 11:20 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Watch

None

Emergency Notice

SCED failure listed above in applications issues.

Texas RE Event Analysis

None