## Slide 1: Reliability Requirements
Bill Blevins
Manager of Operations Support
ERCOT

## Slide 2: New Record-Higher Coastal Wind
A new wind record of 7,599 MW occurred on 3/7/2012 at 20:41. This instantaneous value surpassed 3/6/2012 record of 7,403 MW.
Previous Record Stats (3/6/2012)
Non-Coastal Wind = 6,614 MW (80.5% of installed capacity)
Coastal Wind = 788 MW (64.9% of installed capacity)
Wind was supplying 24.08% if the 30,742 MW load.
Record Stats:
Non-Coastal Wind = 6,581 MW (80.1% of installed capacity)
Coastal Wind = 1,018 MW (83.8% of installed capacity)
Wind was supplying 22.15% of the 34,318 MW load.

## Slide 3: West to North TSAT implementation comparison

## Slide 4: AVR status impacts
Why is VSAT lower than planning numbers on the last few days.
Suspect this is due to the number of generators in the West which are telemetering AVR status of “OFF”
  Several units in the West have AVR status is Off
  ERCOT will be reviewing those with mitigation plans submitted and following up to ensure they are being met.
  ERCOT will be doing RFIs for any other Resources that do not have documented mitigation plans.
Expect higher VSAT and TSAT limits once get more AVRs working in real-time.

## Slide 5: Basic DRAP flow Key features
DRAP will execute only if the RTCA execution produces contingency constraints whose flows exceed the Emergency (2-hour limit) limits.
ERCOT has telemetry for high and low unit MW limits. These represent the high and low sustained ( or emergency limit) for the units telemetered from the market participants. In the current implementation of DRAP (for testing purposes), the resource MW limits for use in DRAP are computed using a ramp rate of 5% of MVA rating in MW/min, and a time period of 5 minutes. Ultimately, the High and Low Dispatch Limits (HDL and LDL) computed by RLC and stored in SCADA will be used by DRAP.

## Slide 6: DRAP update
ERCOT has minor defects
  3 Sev 3 which require work around
  2 Sev 4 defects
  2 Sev 5 defects
  1 enhancement which should be included to support NERC audits.