| NOGRR Number | 088 | NOGRR Title | Synchronization with NPRR424, Reactive Capability Testing Requirements for IRRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | March 8, 2012 |  |  |
| Proposed Effective Date |  | May 1, 2012 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Sections Requiring Revision |  | 3.3.2.2, Non-Coordinated Reactive Testing 3.3.2.3, Coordinated Reactive Testing |  |  |
| Protocol Section Requiring Revision |  | 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guides with Nodal Protocol Revision Request (NPRR) 424, which defines the reactive capability testing requirement for Intermittent Renewable Resources (IRRs). |  |  |
| Reason for Revision |  | To synchronize the Nodal Operating Guides with NPRR424. |  |  |
| Procedural History |  | - On 12/12/11, NOGRR088 and an Impact Analysis were posted. - On 1/30/12, the Operations Working Group (OWG) considered NOGRR088. - On 2/15/12, the OWG considered the 1/30/12 OWG Report and Impact Analysis for NOGRR088. - On 3/8/12, ROS considered NOGRR088. |  |  |
| OWG Decision |  | On 1/30/12, the OWG was in consensus to recommend approval of NOGRR088 as revised by OWG. On 2/15/12, the OWG was in consensus to endorse and forward the 1/30/12 OWG Report and Impact Analysis to ROS. |  |  |
| Summary of OWG Discussion |  | On 1/30/12, it was clarified that ERCOT communicates with Transmission Operators (TOs) during reactive tests. On 2/15/12, there was no discussion. |  |  |
| ROS Decision |  | On 3/8/12, ROS unanimously voted to recommend approval of NOGRR088 as recommended by OWG in the 2/15/12 OWG Report. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 3/8/12, there was no discussion. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | Clarifies the testing requirements for IRRs. |
|  | 2 | Aligns the Operating Guide testing requirements proposed by NPRR424. |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6531 |
| Cell Number | 512-565-9117 |
| Market Segment | ERCOT |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512-248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

- 3.3.2.2	Non-Coordinated Reactive Testing

(1)	The QSE representing the Generation Resource shall give ERCOT at least two hours advance Notice prior to the start of the test.  ERCOT shall Notify the host TO prior to the test.  ERCOT retains the right to cancel the reactive test if ERCOT believes, in its sole judgment, that conducting the test at the requested time could jeopardize the reliability of the ERCOT System.  For example, ERCOT can cancel a requested leading capability test during a time when system voltages are low or expected to be low due to factors such as high import power levels, transmission line Outages, capacitor bank Outages, or Generation Resource Outages or exciter limitations.

(2)	It is recommended, but not required, that tests to verify maximum lagging reactive capability shall be conducted during times when ERCOT System Loads are typically high, such as during the months of May through September, but not necessarily at the time of system peak.  ERCOT has the authority to not allow a reactive capability test to be conducted if it believes system conditions at the requested time of the test are unfavorable.  Generation Resources being tested shall be operating at or above 95% of net dependable real power (MW) output.  Generation Resources that are classified as Intermittent Renewable Resources (IRRs) shall be tested when generating at or above 60% of their seasonal HSL.  If the Generation Resource being tested is unable to achieve adequate lagging reactive capability per the CURL, the Generation Resource, at its discretion, may utilize the capability of another Generation Resource in the same plant to offset (take in VArs) the lagging test that is under way.  This circulation of VArs must leave the high side of the Generator Step-Up (GSU) of the Generation Resource being tested and flow through the GSU of the Generation Resource taking in the VArs.  Under no circumstances shall VArs be circulated between Generation Resources on the same low side bus.

(3)	It is recommended, but not required, that tests to verify maximum leading reactive capability be conducted during times when ERCOT System Loads are typically low, during the months of October through April.  Generation Resources being tested shall be operating at a real power (MW) output representative of its usual loading during such light Load periods.  Generation Resources that are classified as IRRs shall be tested when generating below 60% of their seasonal HSL.  ERCOT has the authority to not allow a reactive capability test to be conducted if it believes system conditions at the requested time of the test are unfavorable.

(4)	The Resource Entity shall measure the tested reactive capability on the Generation Resource output terminals.  The value recorded shall represent the gross MVAR output of the Generation Resource.  This value shall have the Generation Resource’s auxiliary reactive consumption deducted from the Generation Resource’s gross reactive output.  Additionally, the net reactive capability shall be measured at the high side of the GSU transformer if metering is available.  If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side.  Both high side of the GSU transformer and Generation Resource output terminal values are required and must be submitted through the MIS Certified Area.  CURLs shall be attached to the test results submitted, and shall be clearly defined.  All fields shown on the form in the MIS Certified Area shall be completed in order for a submittal to be considered complete by ERCOT.

(5)	The QSE representing a Generation Resource shall be responsible for scheduling reactive verification tests in accordance with the conditions outlined above.  If ERCOT does not issue an alternative reactive testing interval, the Generation Resource shall complete a reactive qualification test at least every two years.

(6)	ERCOT shall have the option to waive the requirement to test and verify the maximum leading reactive capability of any Generation Resource that seldom runs during such light Load periods.  The granting of such a waiver shall be effective for two years.  Initial test results and the two-year reactive test results beginning December 1, 2008, as provided to ERCOT, shall be posted to the MIS Certified Area.  Initial test results and two-year reactive test results conducted prior to December 1, 2008 do not need to be resubmitted to the MIS Certified Area and will remain on file with ERCOT in the original hard copy format.

(7)	The minimum duration for any reactive verification test, leading or lagging, is 15 minutes.  The CURL should be posted in the Resource Entities control room, where the tests are conducted, at the QSE’s Real-Time/generation dispatch desk, and copies should be provided to ERCOT Operations.  During any test, the Generation Resource must maintain its generator cooling system at normal operating level.  Tests will be conducted to produce MVArs at a level not less than 90% of the amount indicated by the existing reactive capability curve (original manufacturer’s unit reactive capability curve, or the most recent CURL).

(8)	The QSE representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT.  The QSE representing a Generation Resource shall be responsible for the timely submittal to ERCOT of an updated CURL reflecting any known changes in the reactive output of the Generation Resource.  A QSE must properly complete all required data fields on the MIS Certified Area for a test to be considered valid.

- 3.3.2.3	Coordinated Reactive Testing

(1)	“Coordinated Testing” is the testing of a Generation Resource’s reactive capability to verify the Generation Resource’s most current CURL.  The verification test will be a coordinated effort between the Resource Entity, the Resource Entity’s QSE, the TO which the Resource Entity is connected, and ERCOT Operations.  Coordinated Testing is at the option of the Resource Entity.  Coordinated Testing can be ordered by ERCOT if a retest is required.

(2)	The Resource Entity requesting to perform a Coordinated Test will provide ERCOT Operations and the TO with a minimum of 48 hours notice of the proposed test date. Requests shall be made between 0800 and 1700 on Business Days.  Upon receipt of a request for test, ERCOT Operations and the TO will evaluate the expected conditions and determine whether transmission system conditions conducive to a valid test can be created through coordinated network switching, modification of the generation reactive dispatch of nearby Generation Resources, or by some other means.  Having established that suitable  ERCOT System conditions exist or can be created, ERCOT Operations, and the TO shall confirm with the Resource Entity and the QSE the agreed upon test time and date or a rejection of the test time and date within 24 hours of the receipt of the request.

(3)	The Coordinated Test shall begin and end within the standard work day (nominally 0800 to 1700).  Since leading tests will often occur in off-peak periods, the coordinated leading test shall begin and end at times agreed to by ERCOT, the TO, QSE and Resource Entity.  The minimum duration for any reactive verification test, leading or lagging, is 15 minutes.  The CURL should be provided to ERCOT Operations and posted in the Resource Entity’s control room and at the QSE’s Real-Time/generation dispatch desk.  The testing period shall be scheduled such that sufficient time is given for any transmission switching.  During the test, the QSE shall be in communication with the TO in order to coordinate the reactive output of adjacent Generation Resources, capacitor switching, reactor switching, and any other activity needed to perform the scheduled reactive test accurately.

(4)	Lagging Reactive Tests - Generation Resources shall be tested to verify lagging reactive capability at or above 95% of net dependable real power output as indicated on the CURL.  Generation Resources that are classified as IRRs shall be tested when generating at or above 60% of their seasonal HSL.  Maximum lagging capability is most likely to be needed during times when ERCOT System Loads are typically high, and transmission system voltages are relatively low, such as during the months of May through September.  ERCOT has the authority to not allow a reactive capability test to be conducted if it believes ERCOT System conditions at the requested time of the test are unfavorable.  The transmission voltage at the switchyard to which the Generation Resource is connected should be at or below the ERCOT currently scheduled voltage prior to starting the test.  If the Generation Resource being tested is unable to achieve adequate lagging reactive capability per the CURL, the Generation Resource, at its discretion, may utilize the capability of another Generation Resource in the same plant to offset (take in VArs) the lagging test that is under way.  This circulation of VArs must leave the high side of the GSU of the Generation Resource being tested and flow through the GSU of the Generation Resource taking in the VArs.  Under no circumstances shall VArs be circulated between Generation Resources on the same low side bus.

(5)	Leading Reactive Tests - Generation Resources shall be tested to verify leading reactive capability at a MW loading level representative of expected Generation Resource MW loading during minimum Load conditions as indicated on the CURL.  Generation Resources that are classified as IRRs shall be tested when generating below 60% of their seasonal HSL.   Maximum leading capability is most likely to be needed when ERCOT System Loads are typically light and transmission system voltages are relatively high, such as during the months of October through April.  ERCOT has the authority to not allow a reactive capability test to be conducted if it believes the system conditions at the requested time of the test are unfavorable.  The transmission voltage at the switchyard to which the Generation Resource is connected should be at or above the ERCOT currently scheduled voltage prior to starting the test.  At ERCOT’s sole discretion, the requirement to test leading capability may be waived for peaking Generation Resources which seldom, if ever, run during light Load conditions.

(6)	The Resource Entity shall measure the tested reactive capability at the Generation Resource terminals.  The reading recorded shall represent the net MVAr output of the generator and shall have the Generation Resource’s auxiliary reactive consumption deducted from the Generation Resource’s gross reactive output at the machine’s terminals.  Additionally, the tested reactive capability shall be measured at the high side of the GSU transformer if metering is available.  If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side.  Both high side and generator terminal values are required for proper submittal of the test results.

(7)	The QSE representing a Generation Resource shall be responsible for scheduling reactive tests in accordance with the conditions outlined above, and for the timely and accurate reporting of test results to ERCOT.  All test documents (the CURL and the CURL with the test point indicated) shall be submitted by the Resource Entity’s QSE.  The Resource Entity must properly complete all required data fields on the MIS Certified Area for a test to be considered complete.

(8)	The minimum duration for any reactive verification test, leading or lagging, is 15 minutes.  The CURL should be posted in the Resource Entities control room, where the tests are conducted, at the QSE’s Real-Time/generation dispatch desk, and copies should be provided to ERCOT Operations.  During any test, the Generation Resource must maintain its generator cooling system at normal operating level.  Tests will be conducted to produce MVArs at a level not less than 90% of the amount indicated by the existing reactive capability curve (original manufacturer’s unit reactive capability curve, or the most recent CURL).

(9)	The QSE representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT.  The QSE representing a Generation Resource shall be responsible for the timely submittal to ERCOT of an updated CURL reflecting any known changes in the reactive output of the Generation Resource.  A QSE must properly complete all required data fields on the MIS Certified Area for a test to be considered valid.