ERCOT Operations Report

Feb 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 3/3/2012 22:06 | 59.882 | 56 | Expected Gen Deviation -800 MW in 3 mins. Frequency was at 59.96 before it started declining. Ran out of URS. |
| 3/6/2012 1:11 | 59.713 | 192 | Unit trip with 840 MW net online. |
| 3/9/2012 16:52 | 59.753 | 152 | Unit trip with 830 MW net online. |
| 3/14/2012 21:53 | 59.858 | 19 | Unit trip with 480 MW net online. |
| 3/15/2012 1:03 | 59.862 | 112 | Multiple unit trips with 427 MW net online. |
| 3/19/2012 17:32 | 59.870 | 32 | Unit trip with 555 MW net online. |
| 3/22/2012 3:36 | 59.740 | 152 | Unit trip with 836 MW net online. |
| 3/22/2012 5:57 | 60.111 | 32 | Expected Gen Deviation +1400 MW in 5 mins. |
| 3/22/2012 19:44 | 59.879 | 20 | Unit trip with 493 MW net online. |
| 3/30/2012 2:56 | 59.777 | 184 | Unit trip with 855 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 3/3/12 22:06:15 | 3/3/12 22:10:54 | 0:04:39 | 537.8 |  |
| 3/6/12 1:11:14 | 3/6/12 1:16:10 | 0:04:56 | 1106.2 |  |
| 3/9/12 16:52:30 | 3/9/12 16:56:18 | 0:03:48 | 914.82 |  |
| 3/14/12 21:53:12 | 3/14/12 21:55:32 | 0:02:20 | 253.81 |  |
| 3/15/12 1:03:44 | 3/15/12 1:08:20 | 0:04:36 | 691.73 |  |
| 3/19/12 6:35:42 | 3/19/12 6:38:10 | 0:02:28 | 237.8 | Expected gen deviation dropped 800 MW in 2 mins. Out of URS. |
| 3/19/12 16:58:36 | 3/19/12 17:00:40 | 0:02:04 | 12.83 | Multiple unit trips with 455 MW net online. |
| 3/19/12 17:32:20 | 3/19/12 17:34:48 | 0:02:28 | 42.02 |  |
| 3/22/12 3:36:54 | 3/22/12 3:40:58 | 0:04:04 | 1206.3 |  |
| 3/22/12 19:44:02 | 3/22/12 19:46:22 | 0:02:20 | 574.37 |  |
| 3/30/12 14:56:24 | 3/30/12 15:03:28 | 0:07:04 | 923.35 |  |

RUC Commitments

SCED Congestion Management Activity (146) (97 Feb 11, 146 Feb 12)

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Lewisville Switch - Carrolton Northwest 345kV | Lewisville Switch - Lewisville Jones Street 138kV | 23 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 16 |
| Sacroc - Snyder 138 kV | Sun Switch - Morgan Creek SES 138 kV | 14 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 12 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North 138/69 kV AXFMR1 | 9 |
| Sun Switch - Morgan Creek SES 138 kV | Sun Switch - Sacroc 138 kV | 8 |
| Spur - Aspermont 138 kV | Spur - Girard Tap 69 kV | 8 |
| Crane Arco Tap - Pegasus 138 kV | Woodward 2 - 16th Street TNP 138 kV | 6 |
| Basecase | Enas - WKN_BKR 69 kV | 4 |
| DCKT Graham SES - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 4 |
| Falcon Seaboard - Midland East 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 4 |
| Scurry Switch - Sun Switch 138 kV | Spur - Aspermont 138 kV | 4 |
| Sun Switch - Morgan Creek SES 138 kV | China Grove Switch - Snyder 138 kV | 3 |
| Falcon Seaboard - Morgan Creek SES 345 kV | Mc Donald - Forsan Tap 138 kV | 3 |
| Midland East - Moss Switch 345 kV | Odessa North - North Cowden 69 kV | 3 |
| DCKT Austrop - Garfield & Zorn 345 kV | Austrop 345/138 kV AXFMR2 | 3 |
| Brackettville - Asphalt Mine 138 kV | Hamilton - Maverick 138 kV | 3 |
| Salt Creek BEPC - Salt Creek Reactor 138 kV | Spur - Girard Tap 69 kV | 3 |
| Falcon Seaboard - Morgan Creek SES 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |
| DCKT Graham SES - Parker Switch 345 kV | Hasse 138/69 kV AXFMR2 | 2 |
| Falcon Seaboard - Midland East 345 kV | Mc Donald - Forsan Tap 138 kV | 2 |
| Midland East - Moss Switch 345 kV | Odessa North 138/69 kV AXFMR1 | 2 |
| Ajo - Riohondo 345kV | North Edinburg Series Reactor XC2 | 2 |
| Ajo - Riohondo 345kV | Raymondville 2 - Raymondville 1 138 kV | 2 |
| Sandy Creek Switchyard - Pittsburg 138 kV | Sandy Creek 138/69 kV AT1 | 2 |
| Odessa Basin Switch - Odessa North 69 kV | Odessa North - North Cowden 69 kV | 2 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North - North Cowden 69 kV | 1 |
| Falcon Seaboard - Morgan Creek SES 345 kV | Sprayberry Switch - Midland Downtown 138 kV | 1 |
| Falcon Seaboard - Morgan Creek SES 345 kV | CRMWD7 Tap - Sprayberry Switch 138 kV | 1 |
| Falcon Seaboard - Morgan Creek SES 345 kV | Forsan Tap - CRMWD7 Tap 138 kV | 1 |
| Scurry Switch - Sun Switch 138 kV | Spur - Girard Tap 69 kV | 1 |
| DCKT Austrop - Lost Pines 345 kV | Fayette Plant 1 - Fayette Plant 2 | 1 |
| DCKT Austrop - Lost Pines 345 kV | Austrop 345/138 kV AXFMR2 | 1 |
| DCKT Morgan Creek SES - Quail Switch & Longshore Switch 345 kV | Odessa EHV Switch - Big Three Odessa Tap 138 kV | 1 |
| DCKT Morgan Creek SES - Quail Switch & Longshore Switch 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |
| DCKT Odessa EHV Switch - Morgan Creek & Quail Switch 345kV | Midland East - Windwood 138 kV | 1 |
| DCKT Odessa EHV Switch - Morgan Creek & Quail Switch 345kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |
| Freeway Park TNP - Heights Sub 138 kV | Heights TNP - PH Robinson 138 kV | 1 |
| Heights TNP - Caddo Switch Station 138 kV | Heights TNP 138/69 kV AT2 | 1 |
| China Grove Switch - Morgan Creek SES 138 kV | Morgan Creek SES - China Grove Switch 138 kV | 1 |
| Bluff Creek Switch - China Grove Switch 138 kV | Odessa North 138/69 kV AXFMR1 | 1 |
| DCKT Martin Lake SES - Stryker Creek SES & Mt. Enterprise 345 kV | Tyler Grand - White House 138 kV | 1 |
| DuPont Switch Ingleside - Ingleside Cogen Switch 138 kV | DuPont Switch Ingleside - Ingleside Cogen Switch 138 kV | 1 |
| Yellow Jacket - Fort Mason 138 kV | Yellow Jacket - Hext 69 kV | 1 |
| Kiamichi Switch - Kiowa Switch 345 kV | Kiamichi - Kiowa Switch 345 kV | 1 |
| Snyder - China Grove Switch 138 kV | Snyder 138/69 kV AXFMR1 | 1 |
| Muenster - Valley View BEPC 138 kV | St Jo TMPP 138/69 kV XFMR2 | 1 |
| DCKT Benbrook - Sycamore & Rocky Creek 345 kV | Edgecliff - Rogers Fort Worth 138 kV | 1 |
| Kiamichi Switch - Kiowa Switch 345 kV | Kiamichi - Kiowa Switch 345 kV | 1 |
| Sacroc - Snyder 138 kV | Rincon - Gregory 69 kV | 1 |
| Pawnee - Lon Hill 345kV | Kennedy Switch - Kennedy Sub 69 kV | 1 |
| Ennis Creek Switch - Knapp 138 kV | Golden Switch - Sun Switch 138 kV | 1 |
| Amoco Goldsmith - Goldsmith 138 kV | Odessa North 138/69 kV AXFMR1 | 1 |
| Monahans - Monahans Tap 2 138 kV | Moss Switch - Permian Basin SES 138 kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Comanche Switch - Comanche Tap 138 kV | 1 |
| Ackerly Vealmoor Switch - Lamesa 69 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |
| Moss Switch 345/138 kV AXFMR1 | Midland East - Windwood 138 kV | 1 |
| China Grove Switch - Morgan Creek SES 138 kV | Morgan Creek SES - China Grove Switch 138 kV | 1 |
| Gaf TNP - Greenbelt TNP 138 kV | Heights TNP - PH Robinson 138 kV | 1 |
| Whitehouse - Walnut Grove 138 kV | Stryker Creek SES - Douglas 138 kV | 1 |
| DCKT Venus Switch - Liggett Switch 345 kV | Davis Tap - Euless Trinity Blvd 138 kV | 1 |
| Westover - Amoco South Foster 138 kV | Holt Switch - North Cowden 69 kV | 1 |
| San Angelo Red Creek - Twin Buttes 345 kV | Twin Buttes 345/138kV AXFMR | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 16 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

04/02 Carrolton North West – Lewisville 345 kV RAP

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

3/08 08:02  	ERCOT issued an Emergency Notice for SCED failure.  This was due to data input error into SCED, the credit limits and three-part offers were transferred into the Market System with zeros.  The Emergency Notice was cancelled at 8:32; however it was issued again at 8:42 because the output schedules were also zero.  The Emergency Notice was cancelled at 09:22.   The Emergency Base Point flag was active from 08:01 – 09:22.  Root cause was data transfer errors that required manual intervention to perform credit validation for the Day Ahead Market.  During this manual process, the target data was incorrectly set causing the energy offers and output schedules to be dropped from the real-time market.

Communication Issues

None

## ERCOT peak (Unofficial)

03/31 18:00 42,711MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | NA |
| May | 2.90 | 2.63 | 3.27 | NA |
| June | 2.89 | 2.84 | 2.28 | NA |
| July | 2.83 | 2.39 | 1.63 | NA |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.98 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 3/2/2012 | 09:40. | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/3/2012 | 22:11 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/8/2012 | 15:25 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/9/2012 | 16:30 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/9/2012 | 16:56 | ERCOT issued a Watch for PRC below 2500 MW. |
| 3/15/2012 | 14:30 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/18/2012 | 20:00 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/22/2012 | 19:56 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/22/2012 | 21:16 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/23/2012 | 09:39 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/23/2012 | 14:51 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/25/2012 | 16:19 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/30/2012 | 15:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 3/31/2012 | 15:10 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

3/08 13:32  	ERCOT issued a Transmission Watch for contingency overload of Raymondville1- Raymondville2 69 kV line on loss of Ajo/Rio Hondo 345 kV line resulting in the curtailment of schedules on the Railroad dc tie.

3/19 13:50  	ERCOT issued a Transmission Watch for a post contingency overload on the Sterrett auto transformer due to forced outages in the Hillsboro area. A TOAP was developed and put in place.

3/26 13:56  	ERCOT issued a transmission watch for the Far West area. The Contingency loss of the 345kV line Midland East to Falcon Seaboard will cause low voltage problems in the Far West area.

3/27 11:31  	ERCOT issued a Transmission watch for the loss of Falcon seaboard- Midland East 345kV line. Line loss will cause low voltage in far west Texas.

3/29 14:47  	ERCOT issued a Transmission Watch for the Far West area due to a planned Moss 138 kV bus outage. Loss of 345kV double circuit Morgan to Quail Switch and Longshore Switch causes low voltage in the Far West area.

Watch

None

Emergency Notice

SCED failure listed above in applications issues.

Texas RE Event Analysis

None