ERCOT Operations Report

Apr 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 4/1/2012 12:28 | 59.890 | 12 | Expected Gen Deviation -800 MW in 3 mins. Frequency was at 59.96 before freq started declining. Ran out of URS. |
| 4/2/2012 17:54 | 59.772 | 164 | Unit trip with 856 MW net online. |
| 4/3/2012 2:08 | 59.803 | 144 | Unit trip with 735 MW net online. |
| 4/4/2012 7:17 | 59.838 | 129 | Unit trip with 594 MW net online. |
| 4/18/2012 8:16 | 59.891 | 4 | Unit trip with 399 MW net online. |
| 4/19/2012 16:08 | 59.893 | 10 | Unit trip with 440 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 4/1/12 12:28:44 | 4/1/12 12:28:56 | 0:00:12 | 153.4 |  |
| 4/2/12 17:54:52 | 4/2/12 17:58:36 | 0:03:44 | 861.06 |  |
| 4/3/12 2:08:03 | 4/3/12 2:12:00 | 0:03:57 | 733.53 |  |
| 4/4/12 7:17:44 | 4/4/12 7:22:16 | 0:04:32 | 490.97 |  |
| 4/26/12 10:09:29 | 4/26/12 10:13:34 | 0:04:05 | 156.92 | Related to EMS R2 Migration. Please refer to application issues below. |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 18 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 17 |
| DCKT Odessa EHV Switch - Morgan Creek & Quail Switch 345kV | China Grove Switch - Bluff Creek Switch 138 kV | 9 |
| Bluff Creek Switch - China Grove Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 9 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North 138/69 kV AXFMR1 | 8 |
| Lewisville Switch - Carrolton Northwest 345kV | Lewisville Switch - Lewisville Jones Street 138kV | 7 |
| Gail Sub - Key Sub 138 kV | Bluff Creek Switch - China Grove Switch | 7 |
| Sacroc - Snyder 138 kV | Sun Switch - Morgan Creek SES 138 kV | 7 |
| Sun Switch - Morgan Creek SES 138 kV | Sun Switch - Sacroc 138 kV | 6 |
| Abilene Mulberry Creek - Bluff Creek 345 kV | Nicole - Orient 138 kV | 5 |
| Abilene Mulberry Creek - Bluff Creek 345 kV | Callahan - Abilene Northwest 138kV | 5 |
| DCKT Roanoke Switch - West Denton and Lewisville 345kV | West Denton - Fort Worth 138 kV | 5 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 5 |
| Abilene Mulberry Creek - Bluff Creek 345 kV | Bluff Creek - Abilene South 138kV | 4 |
| DCKT Roanoke Switch - West Denton and Lewisville 345kV | Jim Christal - North Denton 138kV | 4 |
| Scurry Switch - Sun Switch 138 kV | Aspermont - Spur 138kV | 4 |
| Comanche Peak Units 1& 2 | Austrop - Sandow Switch 345kV | 4 |
| Monahans - Monahans Tap 2 138 kV | Moss Switch - Permian Basin SES 138 kV | 3 |
| Brackettville - Asphalt Mine 138 kV | Hamilton - Maverick 138 kV | 3 |
| Big Brown- Jewett 345 kV CKT 40 | Big Brown- Jewett 345 kV CKT 50 | 3 |
| DCKT Odessa EHV Switch - Morgan Creek & Quail Switch 345kV | San Angelo Concho - San Angelo Mathis Field 69 kV | 2 |
| DCKT Graham SES - Long Creek 345 kV | Paint Creek - Murray 138 kV | 2 |
| DCKT Austrop - Lost Pines 345 kV | Austrop 345/138 kV AXFMR2 | 2 |
| DCKT Greens Bayou - King 345 kV | Greens Bayou 345/138kV AXFRM | 2 |
| Camp Springs Energy Center - Golden Switch 138 kV | China Grove - Bluff Creek Switch 138kV | 2 |
| DCKT Dilley Switch - North Laredo Switch and San Miguel 138kV | Pleasanton - Big Foot 138kV | 2 |
| Brackettville - Asphalt Mine 138 kV | Hamilton - Maverick 138 kV | 2 |
| Meadow Sub - PH Robinson 345 kV | Hastings - Friendswood Tap 138 kV | 2 |
| DCKT Graham - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 2 |
| Basecase | Enas - Wkn_Bkr 69 kV | 1 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North 138/69 kV AXFMR1 | 1 |
| Lewisville Switch - Carrolton Northwest 345kV | Highlands TNP - West TNP | 1 |
| Scurry Switch - Sun Switch 138 kV | Aspermont - Aspermont Continental 69kV | 1 |
| Scurry Switch - Sun Switch 138 kV | Aspermont 138/69 kV XFMR1 | 1 |
| DCKT Graham SES - Long Creek 345 kV | Abilene Northwest 138/69kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Santa Anna Tap - Dressey 69 kV | 1 |
| DCKT Graham - Long Creek 345 kV | Nicole - Orient 138 kV | 1 |
| Sacroc - Snyder 138 kV | Sun Switch - Morgan Creek SES 138 kV | 1 |
| DCKT Austrop - Lost Pines 345 kV | Fayette Plant 1 - Fayette Plant 2 | 1 |
| DCKT Greens Bayou - King 345 kV | Greens Bayou 345/138kV AXFRM | 1 |
| Amoco Midland Farms - Unocal Parker Bakke 138 kV | China Grove - Bluff Creek Switch 138kV | 1 |
| Rodd Field to Holly 138 KV | Airline - Cabaniss 138 kV | 1 |
| Big Brown- Jewett 345 kV CKT 50 | Big Brown- Jewett 345 kV CKT 40 | 1 |
| DCKT Garfield -Lytton Spring and Austrop 345kV | Austrop 345/138 kV AXFMR2 | 1 |
| Aspermont -Spur 138 KV | PADR - PADU 69kV | 1 |
| DCKT STP Units 1 & 2 | Lolita - Blessing 138kV | 1 |
| Morgan Creek SES 345/138kV AXFMR 4 | Morgan Creek SES 345/138kV AXFMR 2 | 1 |
| Victoria 138/69 AXFMR 2 | Victoria - Victoria Du Pont Switch 138 kV | 1 |
| Lake Ivey Booster - Lake Ivey Intake Pump | Ballinger - Humble Ballinger 69kV | 1 |
| Ajo - Riohondo 345kV | North Edinburg Series Reactor XC2 | 1 |
| Ferguson - Coronado 138kV | FERGUSON - WIRTZ 138kV | 1 |
| Paloduro - Pearsall 138 138 kV | Pearsall Switching Station 138/69 kV XFMR | 1 |
| STP Switch - Celanese Bay City 138 kV | Blessing - Lane City 138kV | 1 |
| DCKT Twinbutte - Schkad & Big Lake 138 kV | Tankersley - Mertzon 69 kV | 1 |
| Formosa Unit Formosg11 | Victoria - Victoria Du Pont Switch 138 kV | 1 |
| Granite Mountain to Ferguson 138kV | FERGUSON - WIRTZ 138kV | 1 |
| Crane Arco Tap - Pegasus 138 kV | Hackberry Draw Tap - Permian Basin SES 138 kV | 1 |
| Ferguson - Wirtz 138kV | Sandy Creek 138/69 kV AT1 | 1 |
| Hill Country - Lasierra & Helotes 138 kV | Cagnon 345/138 kV XFM4H | 1 |
| Salt Creek BEPC - Salt Creek Reactor 138 kV | Aspermont 138/69 kV XFMR1 | 1 |
| DCKT Skyline - Calavers 345 kV | Cagnon 345/138 kV XFM4H | 1 |
| Big Foot Sub - Charlotte Sub 69 kV | Pearsall Switching Station - Poteet Sub 69 kV | 1 |
| San Angelo Red Creek - Twin Buttes 345 kV | San Angelo Red Creek 345/138 kV T2 | 1 |
| DCKT Fratt - Kirby & Kirby - Tuttle 138 kV | Hunt Lane - Medinabs 138 kV | 1 |
| Collie Field TNP- Pyote TNP 69 kV | Lonestar Tap TNP - Pecos TNP 69 kV | 1 |
| Long Creek Switching Station - Sweet Water East 345 kV | Sweetwater East Switch - Abilene Mulberry Creek 345 kV | 1 |
| DCKT Cagnon - Kendal (345 kV) & Txresrch 138 kV | Kendall CTEC - Mountain Top 138 kV | 1 |
| Lytton Springs 345/138kV AXFRM 3 | Lytton Springs 345/138kV AXFRM 1 | 1 |
| Airco AEP - North Carbide 1 138 kV | Rincon - Bonnieview 69kV | 1 |
| DCKT Marion - Zorn & Clear Springs 345 kV | Mc Queeney - Structural Metals Inc 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 17 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

4/26 10:00    	ERCOT issued an Emergency Notice for SCED failure.  Directly following the EMS R2 migration, the RLC application within the EMS failed to read the SCED solution results for intervals 09:55 and 10:00 which resulted in stale Base Points being telemetered to the MP’s.  Emergency Notice was cancelled at 10:15.

Communication Issues

None

## ERCOT peak (Unofficial)

04/25 18:00 48,750 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | NA |
| June | 2.89 | 2.84 | 2.28 | NA |
| July | 2.83 | 2.39 | 1.63 | NA |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.93 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 4/5/2012 | 13:20 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1700 - 1900 |
| 4/10/2012 | 15:03 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 4/23/2012 | 17:20 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 4/26/2012 | 4:15 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1500 -1800 |
| 4/26/2012 | 15:04 | ERCOT issued a watch for Projected Reserve Capacity shortage for hours 1700 - 1800 with no market solution available. |

Transmission Watch

None

Watch

None

Emergency Notice

SCED failure listed above in applications issues.

Texas RE Event Analysis

None