## Scenario 1
Scenario 1
Only a storage facilitiy and its auxiliary facilities (station power)
-20
|  |  |  | M1 |  |  | M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
| Non ESR energy losses |  |  | 0
| ESR gen | 50
| ESR load | 40 |  | Aux Load | 30 |  | M2 energy is not netted over the 15 minute interval
|  | M2 | [5 empty] | there will be a value for ESR generation flows and a value for ESR load flows
| Battery |  |  | Aux Load
M1 is site net and is used for calculations to determine site retail load | [8 empty] | -20
M2 gen is ESR Generation | [7 empty] | M2 gen | 50 |  | ESR Generation | 50
M2 load is ESR Load | [7 empty] | M2 load | 40 |  | ESR Load | 40 | DATA
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 30 |  | Auxiliary Load | 30 | ENTRY
Site retail load calculation = ESR generation-ESR load-site net | [7 empty] | ESI ID | 30 |  | Non ESR energy losses | 0
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0
Settlement values
ESR Generation | [6 empty] | 50
ESR Wholesale Storage Load | [6 empty] | 40
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 30
-20
[6 empty] | M1 |  |  |  | M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
|  |  | Non ESR energy losses |  |  | 0
M2 is a load only meter
| ESR load | 40 |  | ESR gen | 50 |  | Aux Load | 30
|  | M2 |  |  | M3 |  |  |  |  | M3 is a generation only meter
| CAES Load |  |  | CAES Gen |  |  | Aux Load
M1 is site net and is used for calculations to determine site retail load | [8 empty] | -20
M3 is ESR GenerationLoad | [7 empty] | M3 gen | 50
M2 is ESR Load | [7 empty] | M2 load | 40
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 30
Site retail load calculation = ESR generation-ESR load-site net | [7 empty] | ESI ID | 30
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0
Settlement values
ESR Generation | [6 empty] | 50
ESR Wholesale Storage Load | [6 empty] | 40
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 30
In the first scenario, where there is only a storage facility and its auxiliary facilities, the storage facility purchases electricity from the ERCOT system to charge. This purchase of electricity is a wholesale transaction because the stored energy will subsequently be injected into the ERCOT system for a wholesale sale. Energy losses resulting from the energy conversion process and during storage are in the chain between the wholesale purchase and wholesale sale by the storage facility and therefore remain wholesale, like energy losses that occur in delivering energy from a generation facility through the ERCOT system to an end-use customer. However, the electricity purchased from the ERCOT system for the auxiliary facilities is consumed by those facilities and should be treated as a retail sale, like electricity purchased off the ERCOT system for a non-storage generation facility and its auxiliary facilities are net consumers of energy from the ERCOT system.

## Scenario 2
Scenario 2
A storage facilitiy, auxiliary facilities, and other consuming facilities, all under common ownership
-25
|  |  |  | M1 | [5 empty] | M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
| Non ESR energy losses |  |  | 0
| ESR gen | 40 | [7 empty] | M2 energy is not netted over the 15 minute int.
| ESR load | 45 |  | Aux Load | 12 |  | Retail Load | 8 |  |  | there will be a value for ESR generation flows and a value for ESR load flows
|  | M2 | [5 empty] | M3
| Battery |  |  | Aux Load |  |  | Retail Load
M1+M3 is site net and is used for calculations to determine site retail load | [8 empty] | -17
M2 gen is ESR Generation | [7 empty] | M2 gen | 40 |  |  | ESR Generation |  | 40
M2 load is ESR Load | [7 empty] | M2 load | 45 |  |  | ESR Load |  | 45 | DATA
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 12 |  |  | Auxiliary Load |  | 12 | ENTRY
Site retail load calculation = ESR generation-ESR load-site net | [7 empty] | ESI ID | 12 |  |  | Non ESR Energy losses |  | 0
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0 |  |  | Retail Load |  | 8
M3 Retail load submitted by the TDSP on an ESI ID | [7 empty] | ESI ID | 8
Settlement values
ESR Generation | [6 empty] | 40
ESR Wholesale Storage Load | [6 empty] | 45
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 12
TDSP Reported retail load assigned to an ESI ID | [6 empty] | 8
-25
[6 empty] | M1 | [6 empty] | M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
|  |  | Non ESR energy losses |  |  | 0
M2 is a load only meter
| ESR load | 45 |  | ESR gen | 40 |  | Aux Load | 12 |  | Retail Load | 8 |  | M3 is a generation only meter
|  | M2 |  |  | M3 | [5 empty] | M4
M4 is a load only meter
| CAES Load |  |  | CAES Gen |  |  | Aux Load |  |  | Retail Load
M1+M4 is site net and is used for calculations to determine site retail load | [8 empty] | -17
M3 is ESR GenerationLoad | [7 empty] | M3 gen | 40
M2 is ESR Load | [7 empty] | M2 load | 45
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 12
Site retail load calculation = ESR generation-ESR load-site net | [7 empty] | ESI ID | 12
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0
M4 Retail load submitted by the TDSP on an ESI ID | [7 empty] | ESI ID | 8
Settlement values
ESR Generation | [6 empty] | 40
ESR Wholesale Storage Load | [6 empty] | 45
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 12
TDSP Reported retail load assigned to an ESI ID | [6 empty] | 8
In the second scenario, where there is a storage facility, auxiliary facilities, and other consuming facilities, all under common ownership, the other consuming facilities’ use of electricity should be treated as a retail sale, like for consuming facilities that do not share interconnection points with generation facilities. Otherwise, the owner could use the storage facility to make wholesale energy purchases from the ERCOT system for the end-use consumption of the energy at the consuming facilities.

## Scenario 3
Scenario 3
A storage facilitiy, auxiliary facilities,other consuming facilities, and a non-storage generation facility, all under common ownership
17
|  |  |  | M1 | [6 empty] | M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
| Non ESR energy losses |  |  | 0
| ESR gen | 20 | [8 empty] | M2 energy is not netted over the 15 minute int.
| ESR load | 5 |  | Aux Load | 10 | Non ESR Gen | 12 |  |  |  |  | there will be a value for ESR generation flows and a value for ESR load flows
M2
| Battery |  |  | Aux Load |  | Non ESR Gen
[11 empty] | Site Net | M2 load | absolute value of site net | ESR Load | Gen Site Retail Load
[11 empty] | -3 | 5 | 3 | 3 | 0
Site net = M1net-M2gen and is used to determine settlement values | [8 empty] | -3
M2 gen is ESR Generation | [7 empty] | M2 gen | 20
M2 load is ESR consumed Load and is used in calculating load | [7 empty] | M2 load | 5
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 10
ESR Wholesale Storage Load (conditional calculation) | [8 empty] | 3
Gen Site retail load calculation (conditional calculation) | [7 empty] | ESI ID | 0
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0
Non ESR generation = Site net if site net positive or zero, otherwise zero | [8 empty] | 0
Settlement values | [11 empty] | ESR Generation |  | 20 | DATA
ESR Generation | [6 empty] | 20 |  |  |  |  | ESR consumed Load |  | 5 | ENTRY
ESR Wholesale Storage Load | [6 empty] | 3 |  |  |  |  | Auxiliary Load |  | 10
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 0 |  |  |  |  | Non ESR Energy losses |  | 0
Non ESR Generation | [6 empty] | 0 |  |  |  |  | Non ESR generation |  | 12
17
M1
M1 energy is netted by ERCOT over the 15 minute interval to determine net energy flow for the site
|  |  | Non ESR energy losses |  |  | 0
M2 is a load only meter
| ESR load | 5 |  | ESR gen | 20 | Aux Load | 10 | Non ESR Gen | 12 |  |  | M3 is a generation only meter
|  | M2 |  |  | M3
[11 empty] | Site Net | M2 load | absolute value of site net | ESR Load | Gen Site Retail Load
| CAES Load |  |  | CAES Gen |  | Aux Load |  | Non ESR Gen |  |  | -3 | 5 | 3 | 3 | 0
Site net = M1net-M3 and is used to determine settlement values | [8 empty] | -3 | Site Net = M1net-M3
M3 is ESR GenerationLoad | [7 empty] | M3 gen | 20 | ESR Gen = M3
M2 load is ESR consumed Load and is used in calculating load | [7 empty] | M2 load | 5 | Non ESR Generation = site net
Aux Load not separately metered (provided for site net calculation) | [7 empty] | Aux load | 10 | For site net positive or zero
ESR Wholesale Storage Load (conditional calculation) | [7 empty] | ESR Load | 3 |  | ESR Load = 0
Gen Site retail load calculation (conditional calculation) | [7 empty] | ESI ID | 0 | For site net positive or zero
Non ESR energy losses not separately metered (provided for site net calculation) | [8 empty] | 0 |  | Gen Site Retail Load = 0
Non ESR generation = Site net if site net positive or zero, otherwise zero | [8 empty] | 0 | For site net negative: conditional compare between the absolute value of site net and M2
if M2 load < or = the absolute value of site net then
Settlement values | [11 empty] | ESR Load is equal to M2
ESR Generation | [6 empty] | 20 |  |  |  |  | Gen Site Retail Load = the absolute value of Site net - M2 (ESR Load)
ESR Wholesale Storage Load | [6 empty] | 3 |  |  |  | if M2 load > the absolute value of site net then
Generation Site Retail Load assigned to an ESI ID | [6 empty] | 0 |  |  |  |  | ESR Load is equal to the absolute value of site net
Non ESR Generation | [6 empty] | 0 |  |  |  |  | Gen Site Retail Load = 0
In the third scenario, where there is a storage facility, auxiliary facilities, other consuming facilities, and a non-storage generation facility, all under common ownership, the energy produced by the non-storage generation facility to charge the storage facility is self-use energy and should therefore not be treated as a retail sale, like energy generated by a non-storage generation facility and used for its auxiliary facilities.