MEMORANDUM

To:	Transmission Owners (TOs), Distribution Providers (DPs) that own transmission Protection System(s), and Generator Owners (GOs)

From:	Texas Reliability Entity (Texas RE)

Date:	April 30, 2012

Re:	PRC-004-2a Protection System Misoperation Reporting Procedures Revision 1

This memorandum is being sent to all registered Transmission Owners (TOs), Distribution Providers (DPs) that own transmission Protection System(s), and Generator Owners (GOs) in the ERCOT Region. Attached is the Texas RE Procedure referenced in PRC-004-2a, Requirements R1, R2 and R3.  This revised procedure incorporates changes requested by Registered Entities and becomes effective on May 1, 2012.

Quarterly misoperation reports will be due on the last day of the second month after each calendar quarter per the table below.  All protection system misoperations shall be reported via the reporting procedure.

| Reporting Period | Due Date |
| --- | --- |
| January 1 through March 31 | May 31 |
| April 1 through June 30 | August 31 |
| July 1 through September 30 | November 30 |
| October 1 through December 31 | February 28 |

Please see attached procedural document and refer to the periodic data submittal form on the Texas RE website (http://www.texasre.org).

NOTE:  The technical requirements, definitions, periodic data submission requirements and submission frequency are similar to those currently in the ERCOT Nodal Operating Guide, Section 6 and Section 8b, as developed with the ERCOT System Protection Working Group.   New components in this procedure include the timeline for analysis and implementation of corrective action plans.

Texas Reliability Entity

Regional Criteria

Procedure For

Analysis, Mitigation and Reporting of Transmission and Generation Protection System Misoperations

NERC Reliability Standards

PRC-004-2a, PRC-016-0.1, and PRC-022-1

Procedure for Analysis, Mitigation and Reporting of Transmission and Generation Protection System Misoperations

- Introduction/Purpose

This document sets forth the Texas Reliability Entity (Texas RE) procedures for the identification, analysis and reporting of Misoperations of transmission and generation Protection Systems, Special Protection Systems (SPS) Undervoltage Load Shed (UVLS) and Underfrequency Load Shed (UFLS), as well as the development and implementation of corrective actions taken to mitigate future Misoperations per NERC Reliability Standards PRC-004, PRC-016 and PRC-022. In addition, for the purpose of streamlining reporting requirements for ERCOT market participants, this document may also serve as the reporting procedure for ERCOT-region Misoperation reporting related to ERCOT Protocols and Operating Guides pursuant to Texas RE’s role as the ERCOT Region Reliability Monitor.

While protective relaying systems operate with a high degree of reliability and security, on occasion, relays and relaying schemes misoperate.  Such misoperations can result in widespread disturbances and can have adverse effects on neighboring entities and systems.  It is therefore imperative that all protective relaying operations be monitored for correctness, and if a misoperation occurs, that appropriate analysis is performed and corrective actions are taken to prevent re-occurrence.

Information submitted on Protection System Misoperations as part of this process will be treated as confidential.  Such information will be maintained, distributed, and communicated in a manner consistent with Section 1500 of the NERC Rules of Procedure.

- References

- NERC Standard PRC-004-2a, ‘Analysis and Mitigation of Transmission and Generation Protection System Misoperations’

- NERC Standard PRC-016-0.1, ‘Special Protection System Misoperations’

- NERC Standard PRC-022-1, ‘Undervoltage Load Shedding Program Performance’

- Texas RE Misoperation Reporting Template

- Texas RE Misoperation Reporting Attestation Form

- Applicability

This procedure applies to the following Registered Entities:

  - Transmission Owners (TOs)

  - Distribution Providers (DPs) that own transmission Protection System(s)

  - Generator Owners (GOs)

- Protection System Misoperation Requirements

In the ERCOT Region, all possible Protection System Misoperations (unwanted trips, failures to trip when intended, failures to automatically reclose when intended, etc.) shall be analyzed by the facility owner(s) promptly and any deficiencies shall be investigated and corrected per the following NERC requirements:

- PRC-004-2a R1:  The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures.

- PRC-004-2a R2:  The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures.

- PRC-004-2a R3:  The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures.

- PRC-016-0.1 R3:  The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request.

- PRC-022-1 R1.5:  Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include:  (R1.5) For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature.

- Definitions

Protection System:  Per the current NERC Glossary of Terms definition as modified by the bold-face text below.

- Protective relays which respond to electrical quantities,

- Communications systems necessary for correct operation of protective functions

- Voltage and current sensing devices providing inputs to protective relays,

- Station dc supply associated with protective functions (including batteries, battery chargers, and non-battery-based dc supply), and

- Control circuitry associated with protective functions through the trip coil(s) of the circuit breakers or other interrupting devices.

For ERCOT-region PUCT Reliability Monitor Misoperation reporting purposes only, this procedure includes reporting requirements for the following additional protection and control equipment:

- Transformer sudden pressure relays and fault pressure relays

- Control circuitry and relays associated with automatic reclosing of transmission circuits (not including the circuit breaker mechanism or close coil)

Special Protection System:  Per the current NERC Glossary of Terms definition.

Corrective Action Plan:  Per the current NERC Glossary of Terms definition.

Applicable Elements:  Protection System Misoperations shall be analyzed, mitigated and reported according to this procedure for the following applicable elements:

a.	Transmission lines operated at 100kV or higher;

b.	Circuit breakers operated at 100kV or higher;

c.	Transformers with one primary terminal and at least one secondary terminal operated at 100kV or higher;

d.	 Generation resources with gross individual nameplate ratings greater than 20 MVA or gross plant/facility aggregate nameplate ratings greater than 75 MVA, either directly-connected or connected through the high-side of the step-up transformer(s) at a voltage of 100 kV or above;

e.	Any generation resource that is a Blackstart Resource;

f.	Buses operated at 100kV or higher;

g.	Series/Shunt capacitors operated at 100kV or higher;

h.	Series/Shunt reactors operated at 100kV or higher;

i.	HV DC systems operated at 100kV or higher;

j.	Dynamic reactive systems operated at 100kV or higher;

k.	Special Protection Systems/Remedial action schemes;

l.	Undervoltage load shed systems (UVLS) (* See Note);

m.	Underfrequency load shed systems (UFLS) (* See Note); and

n.	(For ERCOT-region PUCT Reliability Monitor Misoperation reporting purposes only) Generation resources with gross individual nameplate ratings greater than 20 MVA or gross plant/facility aggregate nameplate ratings greater than 75 MVA, either directly-connected or connected through the high-side of the step-up transformer(s) at a voltage between 60 kV and 100 kV:

* NOTE:	For the purposes of this procedure, for multi-function relays applied at less than 100kV, only a misoperation of the UVLS or UFLS function shall be reported.

Protection System Misoperation:

NERC Glossary Definition of Misoperation:

• 	Any failure of a Protection System element to operate within the specified time when a fault or abnormal condition occurs within a zone of protection.

• 	Any operation for a fault not within a zone of protection (other than operation as backup protection for a fault in an adjacent zone that is not cleared within a specified time for the protection for that zone).

• 	Any unintentional Protection System operation when no fault or other abnormal condition has occurred unrelated to on-site maintenance and testing activity.

For the purposes of this procedure, Protection System Misoperations include the following items.

a.	Failure to Trip – Any failure of a Protection System to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device (zone of protection includes both the reach and time characteristics);

b.	Slow Trip – An operation of a Protection System for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intent;

c.	Unnecessary Trip During a Fault – Any unnecessary Protection System operation for a fault not within the zone of protection;

d.	Unnecessary Trip Other Than Fault – Any unnecessary Protection System operation for non-fault conditions such as power swings, under-voltage, over-excitation, etc. for which the Protection System is not intended to operate; and

e.	Failure to Reclose – Any failure of an automatic reclosing control scheme to automatically reclose following a fault, within its design intent (NOTE:  Failure to Reclose is an ERCOT-region PUCT Reliability Monitor definition only).

The following events ARE NOT reportable Protection System Misoperations subject to these requirements:

a.	Trip Initiated by a Control System – Operations which are initiated by control systems (not by protective relay system), such as those associated with generator controls, or turbine/boiler controls, Static VAR Compensators, Flexible AC Transmission devices, HVDC terminal equipment, circuit breaker mechanism, or other facility control systems, are not considered protective relay system misoperations;

b.	Facility owner authorized personnel action that directly initiates a trip is not considered a misoperation.  It is the intent of this reporting process to identify misoperations of the protective relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the protective relay system.  If an individual directly initiates an operation, it is not counted as a misoperation (e.g. unintentional operation during tests); however, if a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a protective relay system misoperation;

c.	Failure of Relay Communications – A communication failure in and of itself is not a misoperation if it does not result in misoperation of the associated protective relay system.

d.	Lack of targeting, such as when a high-speed pilot system is beat out by high-speed zone is not a reportable misoperation;

e.	Fault clearing consistent with the time normally expected with proper functioning of at least one protection system, then a primary or backup protection system failure to operate is not required to be reported;

f.	Operation of properly coordinated backup Protection System relays to clear the fault in an adjacent zone is not a misoperation if the primary protection fails to clear the fault within the specified time;

g.	Correct breaker failure relay operation in association with a failed breaker, unless the breaker failed to operate due to a defective trip coil;

h.	Human and operational errors or equipment failures occurring while work is being performed (e.g. maintenance, construction and/or commissioning activities) in the substation (e.g., a cover being replaced in an incorrect manner, secondary leads replaced in the wrong position, an incorrect test switch being used to isolate equipment resulting in a trip);

i.	Generator mechanical trips, such as turbine or fuel system trips;

j.	Generator trips caused by automatic voltage regulator, exciter control, or power system stabilizer (however, misoperation of protection functions within the excitation system shall be reported per examples of reportable misoperations); and

k.	An operation of a generator Protection System that does not result in the loss of generation, while a unit is being brought on or off line and is not synchronized with the system.

SPS Misoperation:  SPS misoperations are defined as follows:

a.	Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occurs;

b.	Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed;

c.	Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s);

d.	Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s); and

e.	Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the system design intent.

Protection System Misoperation Causes:  Causes of Protection System misoperations, including SPS misoperations, shall be classified as follows in reports provided to the Regional Entity:

- AC system – This category includes misoperations due to problems in the AC inputs to the Protection System. Examples would include misoperations associated with CT saturation, loss of potential, or rodent damaged wiring in voltage or current circuit;

- As-left personnel error – This category includes misoperations due to the as-left condition of the protection system following maintenance or construction procedures. These include test switches left open, wiring errors not associated with incorrect drawings, carrier grounds left in place, or settings placed in the wrong relay, or incorrect field settings left in the relay that do not match engineering approved settings;

- Communication failure – This category includes misoperations due to failures in the communication systems associated with Protection System schemes inclusive of transmitters and receivers. Examples would include misoperations caused by loss of carrier, spurious transfer trips associated with noise, telecommunication errors resulting in malperformance of communications over leased lines, loss of fiber optic communication equipment, or microwave problems associated with weather conditions;

- DC system – This category includes misoperations due to problems in the DC control circuits. These include problems in the battery or charging systems, trip wiring to breakers, or loss of DC power to a relay or communication device;

- Incorrect setting/logic/design error – This category includes misoperations due to “engineering” errors by the Protection System owner. These include setting errors, errors in documentation, and errors in application. Examples would include uncoordinated settings, incorrect schematics, or multiple CT grounds in the design;

- Relay failure/malfunction – This category includes misoperations due to improper operation of the relays themselves. These may be due to component failures, physical damage to a device, firmware problems, or manufacturer errors. Examples would include misoperations caused by changes in relay characteristic due to capacitor aging, misfiring thyristors, damage due to water from a leaking roof, relay power supply failure, or internal wiring/logic error. Failures of auxiliary tripping relays fall under this category; and

- Unknown – This category includes misoperations where no clear cause can be determined. Requires extensive documentation of investigative actions if this cause code is utilized.

- Analysis and Corrective Action Plan Requirements

Timely analysis of Misoperations and development and implementation of Corrective Action Plans is of critical importance to Bulk Electric System reliability in the ERCOT Region.

When it analyzes a Protection System or SPS Misoperation, the responsible entity shall, to the best of their ability, accurately identify the underlying or “root” cause in sufficient detail to develop a Corrective Action Plan that remedies the problem to prevent Misoperation recurrence.  Where a cause cannot be identified, a thorough documentation of the investigation is required to aid future investigation of the Misoperation, particularly if it recurs.  It is expected that the responsible entity will perform due diligence to identify the Misoperation cause.   Evidence which may assist in analysis of Misoperations includes sequence of events data, relay targets, Disturbance Monitoring Equipment (DME) records, relay calibration and simulation tests, communication noise and attenuation tests, CT/VT ratio tests, DC continuity checks and functional tests, and studies (e.g. short circuit and coordination studies) performed in the attempt to determine the root cause.

The owner of the protective system that is found to have misoperated is responsible for reporting the Misoperation.  If a Misoperation occurs on a tie line between two entities responsible for reporting Misoperation data per this procedure, the Misoperation shall be reported by one or the other entity, but not both.  The entities shall reach agreement on which party submits the Misoperation.  Texas RE may be consulted for input on this decision.

When a root cause of a Misoperation is identified, a Corrective Action Plan must be developed to address the cause(s), and which will improve the performance and reliability of the Protection System.  Registered Entities must have a process in place for developing Corrective Action Plans. A Corrective Action Plan should include interim corrective actions (if necessary), final corrective actions, and a timeline for completion delivery dates.  Interim corrective actions may be useful to quickly address some of the aspects of the Misoperation prior to implementation of a final solution.

Registered Entities shall complete Misoperation analyses and Corrective Action Plans per the following timelines:

| Corrective Action Item | Due Date |
| --- | --- |
| Analyze Misoperation to determine root cause | Within 90 calendar days of event |
| Develop Corrective Action Plan and timetable for implementation (if root cause identified) | Within 120 calendar days of event |
| Develop additional investigation steps and work timetable (if root cause not identified) | Within 120 calendar days of event |
| Complete implementation of Corrective Action Plan | Within 180 calendar days after development of Corrective Action Plan or per Corrective Action Plan timetable, whichever is longer |

- Periodic Data Submittal Requirements

The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide documentation to Texas RE of its Protection System and SPS Misoperation analyses and Corrective Action Plans according to the these procedures.

Transmission Owners shall document the performance of their protective relay systems utilizing the method described in the paper “Transmission Protective Relay System Performance Measuring Methodology,” IEEE/PSRC Working Group I3 September 16, 1999 (Reference Attachment 3).  The performance data reported shall include the total number of protective relay system and automatic reclosing misoperations, the total number of events, and the factor “k.”

Periodic Data Submittals consist of two forms:

- Attestation form.  Total number of events and “k” factor will be submitted on the attestation form.  Reference Attachment 2 for a sample attestation form.

- Protection System Misoperation Report Template.  Protection System Misoperation reports shall be submitted on the most recent version of the Misoperation Report Template posted on Texas RE website (http://www.texasre.org).  Reference Attachment 1 for a description of the Misoperation Report Template fields and the information that is to be provided.

All forms and reports are to be submitted via webCDMS.

Changes, updates or corrections to the analysis of a specific Misoperation or Corrective Action Plan will be submitted in a subsequent quarterly report following the update.  Resubmittal(s) of Misoperation information will be identified on the Misoperation Report Template by selecting “Yes” in the “Resubmittal Check” column.  Each responsible entity will report the status of each of its Misoperation Corrective Action Plan or interim action plans in the periodic data submittal until the Corrective Action Plan is reported complete.

Each responsible entity should retain its complete documentation concerning Misoperations, analyses, Corrective Action Plans, etc. in accordance with NERC requirements for data retention.  Additional information should not be submitted to Texas RE unless requested.

- Submission Frequency

Quarterly, per the following schedule:

| Reporting Period | Due Date |
| --- | --- |
| January 1 through March 31 | May 31 |
| April 1 through June 30 | August 31 |
| July 1 through September 30 | November 30 |
| October 1 through December 31 | February 28 |

If the due date falls on a non-working day (i.e. weekend or state/federal holiday), the data submittal will be due on the next business day.

- Texas RE Review and Oversight

The Texas RE Reliability Services group will review the required data submittals within 30 calendar days after the end of each reporting period.  Each Protection System Misoperation submittal will be reviewed for completeness of 1) Misoperation description; 2) Cause; 3) Corrective actions taken or planned; and 4) Submittal completeness.  Appropriate follow-up actions will be taken to ensure all Misoperations are resolved and that corrective actions are implemented for all outstanding Misoperation investigations.  Additional follow-up actions, if any, will be completed no later than 45 calendar days after the end of each reporting period.  Texas RE submits Protection System Misoperation data to NERC 45 to 60 calendar days after the end of each reporting period.  Any submitted Misoperations related to a failure of automatic reclosing, misoperations for components that are not included under the NERC definition of a Protection System, “k” factor event data, and other ERCOT Region only data are removed by Texas RE from the Misoperation data prior to submitting to NERC for the ERCOT Region.  The removed data is not subject to a PRC-004 audit scope.

On an annual basis, Texas RE will assess the Misoperation data and develop a regional Misoperation summary report.  This regional Misoperation summary report will be shared with the ERCOT System Protection Working Group.  The report may include overall regional Misoperation performance, summary data of Misoperation causes, observed Misoperation trends, and recommendations for follow-up from a regional perspective.  Individual Registered Entity identities will be redacted.

- Revision History

This procedure is considered to be the effective on the first day of the next calendar quarter after approval by Texas RE management.  Texas RE will continue to work with the Registered Entities on changes to this procedure and the related Misoperation Report Template.

| Revision | Date | Approved By | Comments |
| --- | --- | --- | --- |
| 0 | March 23, 2012 | Mark Henry | Initial |
| 1 | April 30, 2012 | Mark Henry | Revised to incorporate stakeholder comments regarding non-NERC defined Protection System equipment |

- Review and Retention Requirements

The Texas RE Reliability Services group will review this document every three years or as appropriate for possible revision.  The existing or revised document will be publicly posted and distributed to all affected Transmission Owners, Generator Owners, and Distribution Providers within 30 calendar days of approval of these procedures.  Texas RE will retain documentation of any changes to this procedure for a period of six years.

Additionally, Texas RE will keep the required Misoperation data submittals for each Registered Entity for a minimum of six years.

ATTACHMENT 1 – Quarterly Misoperation Report Form Fields

| Field Name | Description |
| --- | --- |
| Resubmittal Check | Select ‘Yes’ or ‘No’ from drop-down list |
| Regional Entity | Select ‘TRE’ from drop-down list |
| Entity Name | Enter Registered Entity name |
| Misoperation Date | Enter Date of misoperation in MM/DD/YYYY format |
| Misoperation Time | Enter Time of misoperation in HH:MM:SS format |
| Time Zone | Select the standard time zone from drop-down list |
| Facility Name | Substation or generation station where the misoperation occurred) |
| Equipment Name | Identify by name the generator, transmission line, transformer, bus or equipment protected by the Protection System that Misoperated. |
| Equipment Type | Select equipment type (i.e. line, bus, transformer, generator, etc.) from dropdown list |
| Facility Voltage | Select facility voltage, in kV, from drop-down list |
| Equipment Unavailable | Enter names of the equipment becoming unavailable due to the Misoperation (equipment only refers to circuits, transformers, busses, but not breakers UNLESS the breaker is the only element. Breaker should only be used if a single breaker tripped and did not interrupt an element). |
| Event Description | Provide a brief description of the event and detailed description of Misoperation root causes. |
| Misoperation Category | Select Misoperation Category from drop-down list. |
| Cause(s) of Misoperation | Select root cause(s) of the Misoperation from drop-down list. |
| Protection Systems/Components that Misoperated | Provide information on the components/protection systems that misoperated including relay models (types) and protection schemes. |
| Relay Technology | Select ‘Electromechanical’, ‘Solid State’, or ‘Microprocessor’ from drop-down list |
| TADS Reportable? | Automatically populated based on voltage selection and equipment type |
| TADS Cause Code | Automatically populated based on TADS Reportable column |
| TADS Event ID | Enter TADS Event ID, if applicable |
| Corrective Action Status | Select Corrective Action status (‘Analysis in Progress’, ‘Analysis Complete’, Corrective Action in Progress’, or ‘Corrective Action Complete’) from drop-down list |
| Corrective Action Plan | Provide a brief description of the corrective action plan |
| Actual Analysis Completion Date | If analysis of misoperation is complete, enter actual completion date in MM/DD/YYYY format |
| Actual Corrective Action Completion Date | If corrective actions are complete, enter Corrective action actual completion date in MM/DD/YYYY format |
| Name of Person Filing Report | Name of person filing the misoperation report |
| Phone Number | Phone number of person filing the misoperation report |
| Email Address | Email address of person filing the misoperation report |
| Date of Report | Enter date of the misoperation report in MM/DD/YYYY format |

ATTACHMENT 2 – Periodic Data Submittal Attestation Form

#### Protection System Misoperation Data Submittal

PRC-004 and PRC-016

Reporting Period: (FILL IN REPORTING PERIOD QUARTER)

Submission Period: (ENTER DATES FOR REPORTING PERIOD)

Responding Entity is a:

Transmission Owner	     Generator Owner	     Distribution Provider

Please mark all the following that are applicable:

Entity has experienced a misoperation during this quarter. (Entities experiencing a Misoperation are required to upload a Misoperation Report Template.  The Misoperation Report Template is available in the document download section in webCDMS)

Entity has NOT experienced a misoperation during this quarter

Entity does not own a Transmission or Generation Protection System (PRC-004)

Entity does not own a Special Protection System (PRC-016)

Please provide total system events by quarter and by voltage level for transmission events.

| Quarter | 138 kV | 138 kV ‘k’ Factor | 345 kV | 345 kV ‘k’ Factor |
| --- | --- | --- | --- | --- |
| 1st |  |  |  |  |
| 2nd |  |  |  |  |
| 3rd |  |  |  |  |
| 4th |  |  |  |  |

As a member of senior management (Vice President, Director, or other senior management), I am the responsible person for the oversight of the entity’s implementation of, and compliance with the applicable NERC-approved reliability standard requirements.  I certify that the answers provided above are true to the best of my knowledge for the Reporting Period and Submission Period noted above.

Signature:		_________________________________

Name (print):	_________________________________

Title:		_________________________________

Registered Entity:	 _________________________________

NCR: 		_________________________________

Signature Date:		_________________________________

The completed and signed form should be uploaded via webCDMS.

ATTACHMENT 3 – IEEE/PSRC Working Group Paper, “Transmission Protective Relay System Performance Measuring Methodology”, September 16, 1999

# Footnotes

In addition to its role as a Regional Entity, Texas RE also acts as the Reliability Monitor for the Public Utility Commission of Texas (PUCT), and as such is responsible for monitoring, investigating, auditing and reporting to the PUCT regarding compliance with the reliability-related ERCOT Protocols and Operating Guides by ERCOT Market Entities.

This equipment is not subject to compliance monitoring and enforcement activities under the NERC Reliability Standards.

This equipment is not subject to compliance monitoring and enforcement activities under the NERC Reliability Standards.