## Slide 1: 2012 Load Resources Assessment Study
ERCOT System Planning Department

## Slide 2: Study Objectives
This study was initiated to determine whether the limitation on the percent of Responsive Reserves Service (RRS) provided by Load Resources (LRs) could be increased
  [Concern: if too much LRs MW is tripped it could lead to an over frequency issue]
The study also assessed the adequacy of the RRS program in ERCOT
  [Concern: does RRS arrest the frequency decline for the simultaneous loss of the two largest units in ERCOT]
Several things have changed during course of the study; therefore modifications were made in response
  Amount of RRS procured increased to 2800 MW from 2300 MW
  The limitation on the portion of a unit that can be used to provide RRS was increased from 20% to 24%
  The NERC BAL-003-1 standard (Project-2012 Frequency Response, currently a draft), assigns Frequency Response Obligation to ERCOT based on not activating the UFLS for the loss of 2750 MW (two largest units)

## Slide 3: Performance Criteria
At a minimum, ERCOT is required to assess system frequency response for TPL-002 requirements:
[A] For the loss of a single generation unit, the system frequency shall be arrested between 59.4 Hz and 60.4 Hz, without other machines cascading into out-of-step conditions and without activating the firm load UFLS schema.
Additional criterion, to maintain reliable performance and address likely future NERC requirements:
[B] For the loss of two largest units, the system frequency shall be arrested between 59.4 Hz and 60.4 Hz, without other machines cascading into out-of-step conditions and without activating the firm load UFLS schema.
Notes: NERC PRC-024-1, on Generation Units Frequency Performance ask for upper f-limit of 60.5 Hz
UFLS: total 25% of total system load; stage 1: 5% of total system load; stage 2 & 3: additional 10% of total system load

## Slide 4: Methodology
VARIABLE | COMMENTS
Network Model | 2012 High Wind Low Load Case 29.2 GW total generation including 7.4 GW wind 28.4 GW load (including self-serve) 12 GW of spinning capacity (Pmax - Pgen)
System RRS obligation | 2800 MW. Sum of LRs and effective spinning reserve held at RRS obligation
Generation tripped | Single unit dispatched between 600 MW and 1375 MW Two largest units dispatched at 100% capacity (total loss of 2750 MW)
Spinning reserve/ Generator governor response | Governor response allowed for only RRS participating units limited by the 24%Pmax or 20%Pmax rule
LRs amount | Varied percentage of total RRS obligation
LRs location | Existing locations
LR relay frequency trip | Use existing settings
LR relay trip delays | Use existing settings

## Slide 5: Effect of smaller unit trips (24% rule)
The initial power unbalance caused by a unit loss is counteracted by the trip of LRs and the governor action from units providing RRS. Smaller unit trips could result in frequency response that remains below 60 Hz even though there are enough LRs available - respect to the amount of generation dropped - simply because network conditions did not allow enough LRs to trip, i.e: traces for 600 MW & 800 MW generation drop.
60.5
59.5
Frequency Hz
60.0
50%LR (2800 RRS) = 1400 MW
60.5
59.5
Frequency Hz
60.0
800MW
600MW
1000MW
1375MW
1200MW
70%LR (2800 RRS) = 1960 MW
1375MW
1200MW
1000MW
800MW
600MW
1745MW
1697MW
982MW
294MW
266MW
LRs trip
LRs trip
1228MW
1038MW
237MW
199MW
0 MW
Gen size
Gen size
Notes: System frequency responds to the difference of Pgen-Pload at all times.

## Slide 6: LRs % - Criterion A
System frequency response monitored at 345 kV Jewett bus
Test: loss of one generator unit (1200 MW)
60.5
59.5
Frequency Hz
60.0
30%LR
20% rrs rule
60.5
59.5
Frequency Hz
60.0
50%LR
70%LR
70%LR
50%LR
30%LR
24% rrs rule
Notes: Generation unit Pgen tested from 600 MW to 1375 MW

## Slide 7: LRs % - Criterion B
System frequency response monitored at 345 kV Jewett bus
Test: loss of two largest units (total loss of 2750 MW)
60.3
59.3
Frequency Hz
60.0
20% rrs rule
60.3
59.3
Frequency Hz
60.0
24% rrs rule
80%LR
70%LR
60%LR
50%LR
40%LR
30%LR
80%LR
70%LR
60%LR
50%LR
40%LR
30%LR

## Slide 8: Conclusion
For the outage of a single generating unit
(unit dispatched between 600 MW up to 1375 MW)
  There are no reliability concerns for integrating up to 70% LRs for 2800 MW total RRS.
For the outage of two largest units
(Total 2750 MW)
  For 2800 MW total RRS, there are no reliability concerns for integrating LRs up to 70% but additional RRS may be required based on operation condition (low load and low LRs participation)

## Slide 9: ERCOT Recommendations
ERCOT supports increasing the amount of LRs providing RRS up to 70%
ERCOT may procure additional RRS during certain times
  Still exploring multiple options

## Slide 10: Questions?