## Slide 1
Recommendations from 2011 Southwest Outage
Heather Polzin, FERC Office of Enforcement
Dave Nevius, Senior Vice President, NERC
Member Representatives Committee Meeting May 8, 2012

## Slide 2: September 8, 2011 Event
11 minute cascading outage in Pacific Southwest
2.7 million customers out in AZ, S.CA, MX (up to 12 hrs.)
Initiated when single 500 kV line tripped; not sole cause
Power redistributed, increasing flows, dropping voltages and overloading equipment in underlying systems
Led to tripping lines, generators, automatic load shedding, and operation of RAS and intertie separation scheme
Restoration process generally effective

## Slide 3: Customer Impacts
Entity | Load Lost (MW) | Customers
SDGE | 4,293 | 1.4 million
CFE | 2,150 | 1.1 million
IID | 929 | 146 thousand
APS | 389 | 70 thousand
WALC | 74 | Note
Note: 64 MWs of WALC’s load loss affected APS’s customers

## Slide 4: Simplified System Diagram

## Slide 5: 7 Phases of Event

## Slide 6: Phase 1 – Pre-Disturbance
Hot, shoulder season day; some generation and transmission outages
High loading on some key facilities: H-NG at 78% of normal rating; CV transformers at 83%
44 minutes before loss of H-NG, IID’s RTCA results showed loss of CV-1 transformer would load CV-2 transformer above its relay trip point
15:27:39: APS technician skipped a critical step in isolating the series capacitor bank at North Gila substation; H-NG trips

## Slide 7: Phase 2 – Trip of H-NG 500 kV
H-NG 500 kV trips at 15:27:39
APS tells WECC RC line expected to be restored quickly
SCE-SDGE flow (Path 44) increases by 84%; IID and WALC systems pick up 23% of H-NG flow
CV transformers immediately overloaded above relay settings
Path 44 at 5,900 amps; 8,000 amp limit on SONGS separation scheme
15:27:39 – 15:28:16

## Slide 8: Phase 3 – Trip of CV Xfmrs
15:28:16 – CV-2 and CV-1 230/92kV transformers trip on overload relays
Severe low voltage in WALC 161 kV system
Loading on Path 44 increases to 6,700 amps
15:28:16 – 15:32:10

## Slide 9: Phase 4 – Ramon Xfmr Trip
15:32:10 Ramon 230/92kV transformer trips on overload relay
15:32:13 – 15 Blythe-Niland and Niland – CV 161kV lines trip
IID undervoltage load shedding; loss of generation and 92 kV transmission lines
Severe low voltage in WALC 161 kV system
Loading on Path 44 increases to 7,800 amps; settles at 7,200 amps
15:32:10 – 15:35:40

## Slide 10: Phase 5 – Yuma Separates
15:35:40 – 15:37:55
Yuma AZ separates from IID and WALC when Gila and Yucca transformers trip
Yuma load pocket isolated on single tie to SDG&E
Loading on Path 44 increases to 7,400 amps after Gila transformer trip; to 7,800 amps after Yucca transformers and generator trip

## Slide 11: Phase 6 – High-Speed Cascade
El Centro – Pilot Knob 161kV line trips; all IID 92 kV system radial from SDG&E via S-Line
WALC 161 kV system voltage returns to normal
Path 44 exceeds 8,000 amp setting and timer starts
15:37:55

## Slide 12: Phase 6 – High-Speed Cascade
15:37:58 – 15:38:02.4
S-Line RAS trips IV generation and S-Line, isolating IID from SDG&E
Path 44 loading increases to as high as 9,500 amps and reduces to 8,700 amps after isolating IID

## Slide 13: Phase 6 – High-Speed Cascade
15:38:21.2
SONGS separation scheme operates; forms SDG&E, CFE, Yuma combined island
Combined island frequency begins to collapse

## Slide 14: Phase 7 – Yuma Separates
Yuma island separates from SDG&E when IV-NG 500 kV trips on underfrequency
Yuma load pocket begins to collapse
APS UFLS begins to operate, but insufficient to stabilize load pocket
15:38:23.12

## Slide 15: Phase 7 – CFE Separates
Underfrequency
15:38:23.13
APS, SDG&E and CFE UFLS continues
CFE separates from SDG&E

## Slide 16: Phase 7 – Complete Blackout
By 15:38:38
IID, Yuma, SDG&E, and CFE blacked out

## Slide 17: Joint FERC/NERC Inquiry
Inquiry announced September 9, 2011
Teams formed comprising over 30 senior technical staff of FERC and NERC
Multiple meetings/exchanges with affected entities
Team products combined into final report
Outreach sessions on draft findings and recommendations

## Slide 18: Inquiry Teams
Data Requests/Management
Sequence of Events
Modeling/Simulation
Cause Analysis/Human Performance
Operations Tools/ SCADA/EMS
Frequency Analysis
System Planning/Design
Equipment Performance/System Protection
Restoration

## Slide 19: Key Findings
Weaknesses in two broad areas:
Operations planning
Real-time situational awareness
Contributing factors:
Impact of sub-100 kV facilities operating in parallel with higher voltage systems
Failure to recognize IROLs
Not studying/coordinating effects of protection systems and RAS during contingency scenarios
Not providing effective operator tools and instructions for reclosing lines with large phase angle differences

## Slide 20: Operations Planning
Failure to consider in seasonal, next-day, and real-time studies:
Status of external generation and transmission facilities
Impact of external contingencies
Impacts on external systems
Impact on BPS reliability of sub-100 kV facilities operating in parallel with higher voltage systems

## Slide 21: Operations Planning
Recommended TOP/BA Improvements in WECC:
Obtain information on neighboring BAs and TOPs, including transmission outages, generation outages and schedules, load forecasts, and scheduled interchanges
Identify and plan for external contingencies that could impact their systems and internal contingencies that could impact neighbors’ systems
Consider sub-100 kV facilities operating in parallel with higher voltage systems that could impact BPS reliability
Coordinated review of planning studies to ensure operation of affected Rated Paths will not result in reliability problems

## Slide 22: Situational Awareness
Recommended Improvements in WECC:
Expand entities’ external visibility in models through more complete data sharing
Improve use of real-time tools to ensure constant monitoring of potential internal or external contingencies
Improve communications among entities to help maintain situational awareness
TOPs should review their real-time monitoring tools (State Estimator and RTCA) to ensure critical facilities are represented

## Slide 23: System Protection Issues
Recommendations:
IID and other TOs review transformer overload protection relay settings
TOPs plan to take proper pre-contingency mitigation measures considering emergency ratings and overload protection systems
All protection systems and separation schemes (Safety Nets, RAS, and SPS) studied and coordinated periodically to understand their impact on BPS reliability to ensure no unintended or undesirable effects

## Slide 24
Questions?