| NOGRR Number | 097 | NOGRR Title | New Section 8I, Black Start Resource Availability Test Form |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Recommended Approval |
| Date of Decision | June 13, 2012 |
| Proposed Effective Date | To be determined. |
| Priority and Rank Assigned | To be determined. |
| Nodal Operating Guide Section Requiring Revision | 8, Attachment I, Black Start Resource Availability Test Form (new) |
| Protocol Section(s) Requiring Revision | None. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds a Black Start Resource availability test form to the Nodal Operating Guides. |
| Reason for Revision | Paragraph (7) of Protocol Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing, requires Qualified Scheduling Entities (QSEs) who represent Black Start Resources to complete an ERCOT-provided report form for Black Start Resource availability tests. This NOGRR adds the form to the Nodal Operating Guides. |
| Procedural History | On 5/25/12 NOGRR097 and the associated Impact Analysis were posted. On 5/30/12, Luminant Energy Company, LLC comments were posted. On 6/13/12, the Operations Working Group (OWG) considered NOGRR097. |
| OWG Decision | On 6/13/12, the OWG was in consensus to recommend approval of NOGRR097 as amended by the 5/30/12 Luminant Energy Company, LLC comments and as revised by OWG. |
| Summary of OWG Discussion | On 6/13/12, ERCOT Staff stated that the that actual start time of the test should be included in the form. |

| Business Case |
| --- |
| Business Case | 1 | Provides a standard form for ERCOT and Market Participants to use during testing of Black Start Resources. |

| Sponsor |
| --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6531 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |
| --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |
| --- |
| Comment Author | Comment Summary |
| Luminant Energy Company, LLC 053012 | Proposed language changes to simplify the form. |

Proposed Guide Language Revision

ERCOT Nodal Operating Guides

Section 8

Attachment I

Black Start Availability Test Form

Month Day, Year

# Black Start Resource Availability Test Form

Name of Black Start Resource: ___________________________________________________________

Check method to satisfy quarterly Black Start Resource Availability Test:

Black Start Test – Complete Part A

Successful Start and Normal Operation – Complete Part B

PART A – Black Start Test

Date of Test: __________________________

Time ERCOT Notified the Qualified Scheduling Entity (QSE) of testing:__________________________

Actual Start Time: ___	______________________

Time Black Start Resource reached the Low Sustained Limit (LSL):_____________________________

Black Start Resource LSL per the Current Operating Plan (COP): ___________________________

Did the Black Start Resource operate at or above its LSL for at least four consecutive Settlement Intervals? ________

Time and Date test was completed (breaker open): ___________________________________________

PART B – Successful Start and Normal Operation

Date of Successful Start: _______________________________________

Time Black Start Resource reached the LSL: ________________________________________________

Black Start Resource LSL per the current COP: ___________________________

Did the Black Start Resource operate at or above its LSL for at least four consecutive Settlement Intervals? ________

Was this run time due to an Energy Emergency Alert (EEA) or Normal Operation? __________________

REQUIRED SIGNATURES

QSE Representative Name / Signature: _________________________ / __________________________

Date ___________________________

If a Black Start Availability Test was performed:

ERCOT Operator Name / Signature: ___________________________ / __________________________

Date ___________________________