ERCOT Operations Report

June 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 6/2/2012 13:23 | 59.789 | 216 | Unit trip with 890 MW net online. |
| 6/8/2012 11:46 | 59.889 | 32 | Unit trip with 640 MW net online. |
| 6/9/2012 1:22 | 59.899 | 4 | Unit trip with 450 MW net online. |
| 6/11/2012 13:57 | 59.883 | 88 | Unit trip with 706 MW net online. |
| 6/11/2012 15:57 | 59.894 | 16 | Unit trip with 403 MW net online. |
| 6/13/2012 0:37 | 60.113 | 368 | Expected Gen Deviation +900 MW in 7 min. |
| 6/16/2012 1:21 | 59.891 | 12 | Unit trip with 550 MW net online. |
| 6/17/2012 0:11 | 59.897 | 12 | Expected Gen Deviation -1700 MW in 5 min. |
| 6/20/2012 0:09 | 59.814 | 184 | Unit trip with 825 MW net online. |
| 6/22/2012 8:56 | 59.879 | 8 | Unit trip with 673 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

None

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 6/2/12 13:23:36 | 6/2/12 13:30:19 | 0:06:43 | 1097.7 |  |
| 6/8/12 11:46:56 | 6/8/12 11:50:51 | 0:03:55 | 52.66 |  |
| 6/9/12 1:22:07 | 6/9/12 1:24:11 | 0:02:04 | 8.79 |  |
| 6/11/12 13:57:45 | 6/11/12 14:01:47 | 0:04:02 | 277.67 |  |
| 6/11/12 15:57:26 | 6/11/12 16:00:54 | 0:03:28 | 443.16 |  |
| 6/16/12 1:21:32 | 6/16/12 1:21:48 | 0:00:16 | 342.46 |  |
| 6/17/12 0:10:20 | 6/17/12 0:17:20 | 0:07:00 | 455.26 |  |
| 6/20/12 0:09:32 | 6/20/12 0:15:12 | 0:05:40 | 1098.9 |  |
| 6/22/12 8:57:00 | 6/22/12 9:00:56 | 0:03:56 | 65.42 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North Axfmr1 138/69 kV | 25 |
| DCKT Marion - Zorn and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 20 |
| Fort Stockton Plant - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 16 |
| Lewisville Switch - Carrollton Northwest 345kV | Lewisville Switch - Jones Street Tnp 138kV | 14 |
| DCKT Fayette Plant 2 - Lytton Springs & Holman Aen 345 kV | Fayetteville 26At2 345/138 kV | 12 |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4L (3) 345/138 kV | 9 |
| Twin Buttes T1t (3) 345/138 kV | San Angelo Red Creek T2H (3) 345/138 kV | 9 |
| Paloduro Sub - Batesville Switching Station 138kV | Moore Switching Station - Downie Switching Station 138kV | 8 |
| Lobo - San Miguel 345_138 KV Switchyards 345 kV | San Diego - Freer 69 kV | 6 |
| Kyle - San Marcos 138 kV | Turnersville - Buda 138 kV | 6 |
| Bracketville - Asphalt Mines 138 kV | Hamilton Road - Maverick 138 kV | 6 |
| Midland East - Moss Switch 345 kV | Odessa - Odessa North 138 kV | 5 |
| Bosque Switch - Elm Mott 345 kV | Rogers Hill (Oncor) - Elm Mott 138 kV | 5 |
| Batesville Switching Station 138_69_1 138/69 kV | Moore Switching Station - Downie Switching Station 138kV | 5 |
| Lobo - San Miguel 345_138 KV Switchyards 345 kV | Laquinta - Lobo 138 kV | 4 |
| DCKT Austrop - Lost Pines 345 kV | Austrop (3) AU_At2h 345/138 kV | 4 |
| Meadow Sub - Ph Robinson 345 kV | North Alvin Tnp - Alvin Tnp 138 kV | 4 |
| DCKT Temple Elm Creek - Belton 138 kV | Temple Switch - Temple Southeast 138 kV | 4 |
| Hill Country Axfmr3L-H (3) 345/138 kV | Hill Country Axfmr4h-H (3) 345/138 kV | 4 |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 4 |
| Comanche Switch (Oncor) - Comanche Peak Ses 345 kV | Comanche Switch (Oncor) - Comanche Tap 138 kV | 4 |
| Lago Vista - Marshall Ford 138kV | Buttercup - Whitestone 138kV | 3 |
| Alazan - Barney Davis and Nelson Sharpe 138 kV | Airline Aep - Cabaniss 138 kV | 3 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu_Jack_Creek 345 KV | 3 |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345kV (260_A) | 3 |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North - North Cowden 69 kV | 2 |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North - Odessa Basin Switch 69 kV | 2 |
| DCKT Austrop - Lost Pines 345 kV | Fayetteville 345/138 KV XFMR 26At2 | 2 |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 2 |
| Aspermont Aep - Spur 138 kV | Spur - Girard Tap 69 kV | 2 |
| Aspermont Aep - Spur 138 kV | Spur 138_69_1 138/69 kV | 2 |
| DCKT Sandow Switch - Austrop 345kV | Seaton SEAAT1 138/69 kV | 2 |
| Aspermont Aep - Paint Creek 138kV | Aspermont AEP - Aspermont Continental 69kV | 2 |
| Rodd Field - Holly 138 kV | Airline Aep - Cabaniss 138 kV | 2 |
| Hiway 9 138_69A2 138/69 kV | Koch Up River 138_69A1 138/69 kV | 2 |
| DCKT Cagnon - Kendall 345kV and Cico - Helotes and Clear Springs - Freiheit 138 kV | Howard - Somerset 138 kV | 2 |
| DCKT Graham SES - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 2 |
| Bellville South 54at2 138/69 kV | Glidden Lcra 53At1 138/69 kV | 2 |
| Brownwood - Comanche Switch 138 kV | Brownwood Switch - Camp Bowie (Oncor) 138 kV | 2 |
| DCKT Hamilton Aen - Summit and Balcones Aen 138 kV | Summit - Williamson 138 kV | 2 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 2 |
| DCKT Garfield Aen - Stoney Ridge and Hicross Aen 138 kV | Austrop Au_At1h (3) 345/138 kV | 2 |
| Gabriel - Bell County and Hutto Switch 138 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 2 |
| Renner Switch Axfmr2h (3) 345/138 kV | Allen Switch Axfmr1h (3) 345/138 kV | 2 |
| DCKT Olinger - Firewheel and Elmgrove 138 kV | Olinger - Ben Davis 138 kV | 2 |
| Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 2 |
| Del Rio City - Buena Vista and Hamilton Road 138 kV | Hamilton Road - Maverick 138 kV | 2 |
| DCKT Allen Switch - Royse Switch and Monticello Ses 345 kV | Apollo - Richardson east 138 kV | 2 |
| Renner Switch - Allen Switch 345 kV | Allen Switch Axfmr1h (3) 345/138 kV | 2 |
| Lewisville Switch - Carrollton Northwest 345kV | Lakepointe Tnp - Jones Street Tnp 138 kV | 1 |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4L (3) 345/138 kV | 1 |
| Midland East - Moss Switch 345 kV | Odessa North Axfmr1 138/69 kV | 1 |
| Lobo 2_345_138_H 345/138 kV | North Laredo Switch Pst1 138 kV | 1 |
| Lobo 2_345_138_H 345/138 kV | Laquinta - Lobo 138 kV | 1 |
| DCKT Sandow Switch - Austrop 345kV | Taylor - Taylor West 138 kV | 1 |
| Aspermont Aep - Paint Creek 138kV | Aspermont Aep 138_69T1 138/69 kV | 1 |
| Crane Lclra - Midkiff Switch 138 kV | Rio Pecos - Woodward 1 Tap 138 kV | 1 |
| Crane Lclra - Midkiff Switch 138 kV | Hackberry Draw Tap - Country Road 101 Tap 138 kV | 1 |
| Uvalde Aep 138_69A1 138/69 kV | Tarpley - Utopia 69 kV | 1 |
| Big Lake - Twin Buttes 138 kV | San Angelo Concho - San Angelo Mathis Field 69 kV | 1 |
| Midkiff Switch Axfmr1 138/69 kV | Hackberry Draw Tap - Permian Basin SES 138 kV | 1 |
| Air Liquid Aep - Valero East and Hiway 9 69 kV | Koch Up River 138_69A1 138/69 kV | 1 |
| Allen Switch - Renner Switch and Plano Tennyson 345 kV | Allen Switch Axfmr1h (3) 345/138 kV | 1 |
| Yellow Jacket - Fort Mason 138 kV | Fort Mason - Mason Aep 69 KV | 1 |
| Illinois #4 - Fort Lancaster 138 kV | Sonora - Friess Ranch 69 kV | 1 |
| Crystal City - Turtle Creek Switching Station 69 kV | Asherton 138_69A1 138/69 kV | 1 |
| Gila - Hiway 9 138 kV (GILA_HIWAY_2) | Gila - Hiway 9 138 kV (GILA_HIWAY_1) | 1 |
| Fashing Sub - San Miguel 69 KV Switchyard 69 kV | Oaks Sub 138_69_1 138/69 kV | 1 |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney Tnp 138 kV | 1 |
| Olsen Tnp Olsenat1 138/69 KV | Lake Whitney Tnp - Olsen Tnp 69 kV | 1 |
| Bandera Lcra At3_H 138/69 KV | Bandera Lcra 65At2_L 138/69 KV | 1 |
| DCKT Decker Power Plant - Sprinkle and Dessau - Daffin Gin 138 kV | Decker Power Plant - McNeil Aen 138 kV | 1 |
| Duke / Hec - North Edinburg 138 kV | Aderhold Sub - Elsa 138 kV | 1 |
| San Diego - Alice 69 kV | Lobo - Freer 69 kV | 1 |
| Bluff Creek T2_H (3) 345/138 kV | Nicole - Orient 138 kV | 1 |
| DCKT Farmersville Switch - Monticello Ses 345 kV | Monticello Ses - Allen Switch 345 kV | 1 |
| San Miguel 345_138 KV Switchyards - Elmcreek 345 kV (SMG_ELMCRK2) | San Miguel 345_138 KV Switchyards Autb_L (3) 345/138 kV | 1 |
| Mesa View Switch - Fort Lancaster 138kV | Twin Buttes - Big Lake 138kV | 1 |
| West Levee Switch Axfmr1h (3) 345/138 KV | Industrial Blvd - Compton Street 138 KV | 1 |
| DCKT Cagnon-Kendall (345 KV) & Helotes-Cico (138 KV) | Howard - Somerset 138 kV | 1 |
| San Angelo Red Creek - Twin Buttes 345 kV | Nicole - Orient 138 kV | 1 |
| DCKT Norwood Switch - Liggett Switch and Cedar Hill Switch 345 KV | Mountain Creek Ses - Trinity River Authority 138 kV | 1 |
| Midkiff Switch - Spraberry Switch 138 kV | Garden City - Glasscock (Oncor) 69 kV | 1 |
| DCKT Long Creek - Graham Ses and Cook Field Road Switch 345 kV | Paint Creek - Murray Switch 138 kV | 1 |
| Ferguson - Wirtz and Coronado 138 kV | Ferguson - Sandy Creek Switchyard 138 kV | 1 |
| DCKT Zorn - Marion and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 1 |
| China Grove Switch - Morgan Creek SES 138 kV (6220) | China Grove Switch - Morgan Creek Ses 138 kV (6225) | 1 |
| Hiway 9 - Citgo N Oak Park 138 kV | Nueces Bay - Hiway 9 138 kV | 1 |
| Watermill Switch - Desoto Switch & Cedar Hill Switch 345kV | Amelia Street - Ut Southwest Medical Center 138 kV (3415_D) | 1 |
| DCKT Watermill Switch - West Levee Switch and Sargent Road 345 kV | Simpson Stuart - Buntin Drive 138 kV | 1 |
| Sun Switch - Snyder 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |
| Pancake Tnp - Pancake 69 kV | Seaton SEAAT1 138/69 kV | 1 |
| San Angelo Red Creek - Bluff Creek 345kV | Nicole - Orient 138 kV | 1 |
| Roanoke Switch - Parker Switch 345 kV | Parker Switch - Eagle Mountain Ses 345 kV | 1 |
| Alice - Kingsville 138kV | Falfurrias 138_69A1 138/69 kV | 1 |
| Fort Mason - Gillespie Lcra 138 kV | Ferguson - Sandy Creek Switchyard 138 kV | 1 |
| DCKT Ingleside Dupont Switch - Whitepoint 138 kV | Rincon - Whitepoint 138 kV | 1 |
| Granite Mountain - Ferguson 138 kV | Ferguson - Wirtz 138 kV (40T189) | 1 |
| Jonesboro Tnp - Pancake Tnp 69 kV | Sycamore Tnp - Coryell County Tnp 69 kV | 1 |
| Dilley Switch Aep - North Laredo Switch and San Miguel 69 KV Switchyard 138 kV | Pearsall Switching Station - Paloduro Sub 138 kV | 1 |
| Whitney Wht1T_H (3) 345/138 kV | Whitney Axfrm2L_H (3) 345/138 kV | 1 |
| DCKT Sandow Switch - Bell County East Switch 345kV | Seaton SEAAT1 138/69 kV | 1 |
| Big Wells - Asherton 138 kV | Turtle Creek Switching Station - Crystal City 69 kV | 1 |
| Lewisville Switch Axfmr22 345/138 KV | Lakepoint Tnp - Jones Street TNP 138kV | 1 |
| DCKT Cagnon - Medinabs and Tcc and Pinn_Rd and Wstside 138 kV | Five_Pts - Wstside 138 kV | 1 |
| Cedar Hill Switch Axfmr2L (3) 345/138 KV | Sherry Switch - Park Row 138KV (6325_C) | 1 |
| Wink Sub - Cheyenne and No Trees Switch 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 13 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 06/01/2012 | Transmission and Security Desk V1 Rev17 | 599 |
| 06/01/2012 | Shift Supervisor Desk V1 Rev15 | 598 |
| 06/01/2012 | Resource Desk V1 Rev17 | 597 |
| 06/01/2012 | Real Time Desk V1 Rev18 | 596 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

06/26 17:00 66,583 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | NA |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.94 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 6/26/2012 | 14:07 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

06/10 15:44 	ERCOT issued a transmission watch for Uvalde area due to low voltages. The Eagle Pass DC-Tie export was curtailed to zero.  There were outages in the area.

06/25 14:06 	ERCOT issued a transmission watch for the loss of Batesville Station to Paloduro 138 kV overloads Moore to Downies 138kV.  Watch was issued until a Mitigation Plan could be developed.

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None