## Slide 1
July 12, 2012
OPSTF
<number>
OPSTF – Issue 5
Load Levels to Consider in Planning Studies

## Slide 2: OPSTF Issue 5:
Many on OPSTF are concerned that 1) in recent years SSWG Base Case load levels have fallen relative to the ERCOT CDR and
2) after 2009 the load level in the SSWG cases dropped such that the transmission system being planned for 2013 and later does not have the reliability margin built in that previously existed.
July 12, 2012
OPSTF
<number>

## Slide 3: OPSTF Issue 5:
SSWG Loads have decreased relative to the ERCOT CDR
2009 Base Cases 2010 Base Cases
Model Year % Increase* Model Year %Increase*
2011 10.2% 2013 3.1%
2012 9.9% 2014 3.6%
2013 9.0% 2015 3.6%
*SSWG Load Level vs. ERCOT CDR
July 12, 2012
OPSTF
<number>

## Slide 4: Data
July 12, 2012
OPSTF
<number>
 | 2010 | Model | 
 | SSWG DSB | CDR | Difference
2007 | 72207 | 67955 | 6.3%
2008 | 72917 | 67481 | 8.1%
 | 2011 | Model | 
 | SSWG DSB | CDR | Difference
2007 | 73840 | 69456 | 6.3%
2008 | 74897 | 68804 | 8.9%
2009 | 71920 | 65252 | 10.2%
 | 2012 | Model | 
 | SSWG DSB | CDR | Difference
2007 | 75720 | 70733 | 7.1%
2008 | 76688 | 69892 | 9.7%
2009 | 73776 | 67152 | 9.9%
2010 | 68973 | 66416 | 3.8%
 | 2013 | Model | 
 | SSWG DSB | CDR | Difference
2008 | 78400 | 71294 | 10.0%
2009 | 75401 | 69157 | 9.0%
2010 | 70155 | 68023 | 3.1%
2011 | 71632 | 67362 | 6.3%
 | 2014 | Model | 
 | SSWG DSB | CDR | Difference
2009 | 77123 | 70595 | 9.2%
2010 | 71667 | 69209 | 3.6%
2011 | 73128 | 70004 | 4.5%
 | 2015 | Model | 
 | SSWG DSB | CDR | Difference
2010 | 72789 | 70275 | 3.6%
2011 | 74251 | 71910 | 3.3%
* SSWG DSB year represents year cases were released

## Slide 5: OPSTF Issue 5:
Proposal: Change Planning Guide 6.1 “Steady State Model Development”
6.1(3)(a) Each TSP, or its Designated Agent shall provide its respective transmission network steady-state model data, including load data. The load data shall correspond to the 90th percentile weather forecast for each TSP area.
And
Add new provision 6.1(4) ERCOT shall develop and post on the MIS Public Area a Weather Zone peak load forecast for the next six years that corresponds to the 90th percentile weather forecast for each Weather Zone by December 31 each year.
July 12, 2012
OPSTF
<number>

## Slide 6: OPSTF Issue 5:
QUESTIONS ?
July 12, 2012
OPSTF
<number>