| NPRR Number | 460 | NPRR Title | WGR Ramp Rate Limitations |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | July 19, 2012 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Nodal Protocol Section Requiring Revision |  | 6.5.7.10, WGR Ramp Rate Limitations |  |  |
| Market Guide Section(s) Requiring Revision |  | None. |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) increases the Wind-powered Generation Resource (WGR) ramp rate limitation from 10% per minute of nameplate rating to 20% per minute of nameplate rating. |  |  |
| Reason for Revision |  | This revision allows WGRs to be fully Dispatched on or fully curtailed off in one Security-Constrained Economic Dispatch (SCED) interval. This would allow for a more efficient Dispatch of Resources and more precise curtailment instructions to WGRs. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 5/2/12, NPRR460 was posted. - On 5/15/12, WMS comments were posted. - On 5/15/12, ERCOT comments were posted. - On 5/17/12, PRS considered NPRR460. - On 6/18/12, ROS comments were posted. - On 7/3/12, Performance Disturbance Compliance Working Group (PDCWG) comments were posted. - On 7/12/12, a second set of WMS comments were posted. - On 7/13/12, a second set of ROS comments were posted. - On 7/19/12, PRS again considered NPRR460. |  |  |
| PRS Decision |  | On 5/17/12, PRS unanimously voted to table NPRR460 and to refer the issue to ROS. All Market Segments were present for the vote. On 7/19/12, PRS unanimously voted to recommend approval of NPRR460 as revised by PRS. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 5/17/12, there was no discussion. On 7/19/12, ERCOT Staff stated that because of how compliance is determined under paragraph (9) of Section 6.5.7.10, revising the ramp rate limitation to 20% effectively removes the ramp rate limitation for WGRs and therefore proposed to delete Section 6.5.7.10 entirely. Participants countered that the 20% ramp rate limitation would still be effective and that it is anticipated that the Texas Reliability Entity (Texas RE) will require Resource Entities with WGRs to have the necessary controls in place to comply with the limitation, and that therefore Section 6.5.7.10 should remain. Participants also discussed ERCOT Staff’s request to delay implementation until December 2012, noting that NPRR460, which is on a normal timeline, would not be considered by the ERCOT Board any earlier than the November 2012 ERCOT Board meeting. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | Qualitative benefits: - Provides for a more efficient dispatch of Resources by not artificially restricting the response of a Resource. - Provides additional ramping capability for SCED to use when resolving congestion as well as responding to net Load changes. - Reduces sequential WGR dispatches, which cause price and Base Point oscillations - the sequential generator dispatches for WGRs occur when a constraint is activated (e.g. West to North) requiring multiple WGRs to respond but ramp rate limits cause the “most expensive” Resources to be partially deployed the first SCED interval with cheaper WGRs also being deployed and then for the next SCED interval the expensive Resource is completely deployed and the cheaper Resource is no longer curtailed. These sequential WGR dispatches have been over 100 MW and add to the oscillations seen in West Zone Base Points. |
|  | 2 | Quantifiable benefits: - WGRs would not be forced to generate at a price that is below their Energy Offer Curve. - Generator Operations and Maintenance (O&M) costs will be reduced due to less wear and tear when responding to curtailments one interval and then being released the next interval. All Resources will have more stable price signals more reflective of actual Resource capabilities. |
|  | 3 | Comment on impacts to Market Segments: - Improves SCED Dispatch results and reduced artificial, single-SCED-interval negative prices for all Resources. - Reduces Base Point oscillations that affect all Resources. - No effect on Loads operationally and a small increase in prices due to fewer artificial negative prices and a small reduction in prices due to more efficient Dispatch. |

| Sponsor |  |
| --- | --- |
| Name | Brad Schwarz |
| E-mail Address | Bradley.schwarz@eon.com |
| Company | E.ON Climate & Renewables |
| Phone Number | 512-482-4003 |
| Cell Number | 512-289-7425 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| WMS 051512 | Endorsed NPRR460 as submitted. |
| ERCOT 051512 | Reiterated concerns that the proposed changes could impact frequency control and subsequently grid reliability and requested that PRS refer NPRR460 to ROS/PDCWG for additional review. |
| ROS 061812 | Referred NPRR460 to PDCWG. |
| PDCWG 070312 | Stated support for the proposal to change the ramp rate restriction from 10% to 20% and agreed to review the ERCOT proposal to remove the ramp rate restriction entirely. |
| WMS 071212 | Endorsed the 5/15/12 WMS comments. |
| ROS 071312 | Endorsed NPRR460 as submitted. |

Proposed Protocol Language Revision

- 6.5.7.10	WGR Ramp Rate Limitations

(1)	Each WGR that is part of a Standard Generation Interconnection Agreement (SGIA) signed on or after January 1, 2009 shall limit its ramp rate to 20% per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

(2)	The requirement of paragraph (1) above does not apply during a Force Majeure Event or during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available WGR.

(3)	Each WGR that is part of an SGIA signed on or before December 31, 2008 and that controls power output by means other than turbine stoppage shall limit its ramp rate to 20% per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

(4)	The requirement of paragraph (3) above does not apply during a Force Majeure Event, during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available WGR, or during unit start up and shut down mode.

(5)	The ramp rate requirement of paragraph (3) above shall not apply to a WGR during a limited compliance transition period if the WGR:

(a)	Meets the technical specifications of paragraph (3) above but does not comply with the ramp rate requirement; and

(b)	Submitted a compliance plan to ERCOT on or before June 1, 2009 that details the technical limitations leading to non-compliance, a work plan to achieve compliance by a reasonable date, and a ramp rate mitigation plan describing the WGR’s best efforts to adhere to the WGR ramp rate limitation during the applicable compliance transition period.

(6)	The ramp rate requirement of paragraph (3) above shall not apply to a WGR that:

(a)	Does not meet the technical specifications of paragraph (3) above; and

(b)	Submitted an operations plan to ERCOT on or before June 1, 2009 describing the WGR’s best efforts to adhere to the WGR ramp rate limitation.

(7)	WGRs subject to the ramp rate limitations of paragraphs (1) and (3) above are exempt from the requirements of the applicable paragraph upon receipt of a valid Dispatch Instruction from ERCOT to exceed the applicable ramp rate limitation when necessary to protect ERCOT System reliability.

(8)	WGRs that operate under an SPS are exempt from the ramp rate limitations of paragraphs (1) and (3) above when decreasing unit output to avoid SPS activation.

(9)	WGRs that meet the requirements of paragraphs (1) and (3) above are compliant with ramp rate limitation requirements when the number of five-minute averages of eligible intervals meeting 20% of nameplate capacity per minute ramp rate limit is equal to or greater than 90% of eligible intervals per month.  Intervals where paragraphs (2), (4), (7) or (8) above apply shall be excluded as eligible intervals for this performance metric.  ERCOT shall initiate a review process with the WGR where the WGR’s score is less than 90%.  Scores that remain below 90% for three consecutive months shall be considered to have failed the ramp rate limitation performance measure.