August 1, 2012

David R. Nevius

Senior Vice President

North American Electric Reliability Corporation

3353 Peachtree Road NE

Suite 600, North Tower

Atlanta, GA 30326

RE:  Texas RE Final Report on the Follow-Up Actions for the September 8, 2011 Southwestern Blackout Regarding Group A Recommendations

Dear Dave:

Texas RE is responding to NERC’s “Follow-Up Actions for September, 8, 2011 Southwestern Blackout” sent to Texas RE on June 5, 2012 requesting that Texas RE provide a final report to NERC within 60 days of receipt.

Below is Texas RE’s Final Report which provides the status on actions by Registered Entities, technical committees, or other work groups within the ERCOT Interconnection to address the applicable findings and recommendations in Group A from the NERC/FERC Joint Staff Inquiry report on the Arizona – Southern California Outages on September 8, 2011.  While many of the recommendations are specific to WECC and the companies involved in the event, Texas RE initiated discussions among stakeholders to seek broader application or confirm practices in place to evaluate or minimize the possibility of similar occurrences within the ERCOT Interconnection.  Texas RE attended and or conducted several meetings with stakeholders and Regional technical working groups further developing the initial responses and identifying possible improvements to Regional operations and planning.

All but one of the Transmission Operators (TOPs) in the ERCOT Interconnection is registered pursuant to a Coordinated Functional Registration (CFR) agreement for TOP functions.  The CFR agreements are executed by and assign specific responsibilities for TOP functions to (1) ERCOT ISO and (2) certain transmission-owning entities that each operates a control center for a discrete portion of the bulk-power system within the ERCOT Interconnection.  These transmission entities are defined in the CFR as Local Control Centers (LCCs).  ERCOT ISO is the only Reliability Coordinator (RC) and Balancing Authority (BA) for the ERCOT Interconnection and is party to all of the TOP CFRs.  One additional transmission-owning entity elected to be registered as a TOP without a CFR.  The NERC questions have been answered based on the assignment of responsibilities within the TOP CFR agreements.

Sincerely,

W. Lane Lanford, President and CEO

Lane.Lanford@texasre.org

(512) 583-4940

Texas RE Response to NERC Follow Up Request

Group A: Next-Day Planning and Real-Time Operating Issues

Recommendations 1 – 4 address the responsibilities of RCs, TOPs, and BAs in the next-day planning timeframe.  They stress the importance of accuracy in next-day planning models, including sharing, across the entire RC footprint, generation and transmission outages and transactions that could impact the reliability of the bulk power system (BPS); comprehensiveness of studies with respect to facilities that can impact bulk power system reliability, including sub-100 kV facilities; and the free and unrestricted exchange of next-day operations data and studies between and among operating reliability entities.

Response to Recommendations 1 – 4:

- How do the TOPs in the ERCOT Interconnection conduct next-day studies and freely share with each other and the RC, the status of planned outages of generation and transmission, expected transactions, and study results?

ERCOT ISO updates next-day studies to reflect planned outages of generation and transmission. ERCOT ISO, as a TOP and the only RC and BA for the ERCOT Interconnection, is the sole entity with complete visibility of the entire Interconnection.  ERCOT ISO is also the only recipient of generation Current Operating Plan (COP) data.  Since ERCOT acts as the single BA for the region, there are no inter-BA transactions other than through Direct Current ties.  As such, ERCOT ISO is the only entity that can conduct next-day studies of the entire Region.  The ERCOT Interconnection has local rules in place that reinforce the responsibilities associated with next-day planning and support the requirements in the TOP CFR.

All LCCs have the entire Network Model Management System (NMMS) Common Information Model (CIM)/XML Network Model   of the ERCOT transmission system available to them through the Market Information System (“MIS”); however, having the CIM/XML model available for downloading is different from having the model file available to be used in study applications.  Currently, only ERCOT ISO uses the CIM/XML model as direct input for its Energy Management System used in Real-time and Day-Ahead activities.  Due to the technical aspects of the ERCOT CIM/XML model structure considerable time and cost would be necessary for other entities to use the ERCOT CIM/XML model in their own study applications.

Transmission and generation outage information for next-day studies is available to all LCCs from the ERCOT outage scheduling tools and processes; however, the format provided is not directly importable into the LCCs applications.  Generator Current-Operating-Plans (COPs) for the next seven days are not available to LCCs for next-day planning, but ERCOT ISO has this information for conducting next-day security analysis.  Single contingencies are developed through internal ERCOT ISO (RC, BA, and TOP) processes based on data provided by LCCs.  Special contingencies, such as double-circuit contingencies, are developed by ERCOT ISO or can be suggested by LCCs to ERCOT ISO for inclusion in models.  The sharing of study results is primarily accomplished with ERCOT ISO receiving transmission and generation outages requests and performing multi-day-ahead and day-ahead operational review of those outages and the setting of system limits.  Some neighboring LCCs model portions of each other’s systems to a certain extent that may reflect contingency-based issues within their neighbor’s borders; however, none of these limited models have the complete information to fully analyze the effect of contingencies.  ERCOT ISO processes are the key in coordinating contingency implications among neighboring LCCs.  Some LCCs also pre-screen outage requests prior to submitting to ERCOT ISO.  ERCOT ISO conducts next-day contingency analysis through the Day-Ahead Reliability Unit Commitment (DRUC) process for the entire Interconnection.

The LCCs could benefit from having visibility into planned generation dispatch, for instance through the sharing of the COPs.  This visibility would not impose an obligation on the LCCs to run studies in parallel with ERCOT ISO.  A significant amount of additional data (i.e. generator ramp rates and limitations, explicit EMS modeling of Remedial Action Schemes, significant amounts of additional external SCADA points, LCC EMS modifications, external modeling enhancements, etc.) and resources would be required by LCCs to perform extensive studies for next-day planning purposes that are currently the responsibility and obligation of the ERCOT ISO.  The studies that are run by the Local Control Centers support the ERCOT ISO obligations but would not replace those obligations.

Texas RE will continue to seek feedback and monitor any progress on the following

- Effectiveness of LCC to LCC and ERCOT to LCC sharing of next-day study information.

- Provision of additional information (i.e. COPs, SPSs, Mitigation Plans, etc.) to the LCCs by ERCOT ISO.

- Discussions regarding ERCOT ISO possible enhancements to the System Operations Test Environment (SOTE) currently accessible by LCCs.

- Discussions between ERCOT ISO and LCCs regarding additional Private Use Network (PUN) modeling and information possibly needed for inclusion in both planning and operational studies for increased situational awareness for ERCOT ISO and LCCs.

- Confirmation with ERCOT ISO on how the ERCOT ISO’s next day study results are acknowledged by LCCs and how the disagreements, if any, are resolved among them.

- Which TOPs have completed studies identifying the sub-100 kV facilities that can have significant impacts on BPS reliability and model those facilities in their next-day studies?  How often are studies performed to evaluate the effect on sub-100 kV facilities when new transmission or generation facilities are added to the system?

ERCOT ISO and LCCs include the sub-100kV networks in their models and next-day studies for the Region; therefore, effects of system changes on these facilities are included in the studies.  Facility owners submit model data for all facilities 60 kV and above to ERCOT ISO prior to the facilities being placed in service. Studies are performed that include all transmission facilities regardless of voltage level.  ERCOT ISO includes all 69 kV contingencies in all EMS studies (real-time, outage coordination, day-ahead SOL studies, etc.).  ERCOT ISO includes select 69 kV contingencies for inclusion in Market Management System studies which includes Reliability Unit Commitment (RUC) studies.  ERCOT ISO incorporates the study results into its security constrained economic dispatch of generation and its direction to the Local Control Centers.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Further review to determine if 69 kV issues are given different treatment in studies and action plans and/or if impacts of certain private networks (which may be above or below 100 kV) are thoroughly considered.

- When and how are TOPs alerted to contingencies on neighboring systems that could impact their internal system and the need to plan for such contingencies?  When do TOPs include contingencies in next-day studies on neighboring systems that could impact their internal system?

See response to Question#1.  ERCOT ISO has complete visibility across the Region’s entire transmission system, including 69 kV, and provides notifications through outage coordination and operational communications. ERCOT ISO develops contingency plans based on system conditions.  ERCOT ISO communicates these contingency plans in several different ways, ranging from a formal procedure to an email.

ERCOT ISO alerts Local Control Centers of contingencies on neighboring LCC systems that could impact another LCC’s internal system and the need to plan for such contingencies.  Some neighboring LCCs have chosen to model portions of each other’s systems due to system topology that may indicate contingency based issues within their neighbors’ borders; however, ERCOT ISO processes are the key in coordinating contingency implications among neighboring LCCs.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Standardization of ERCOT ISO regarding all contingency plans through posting contingency plans on the ERCOT Market Information System (MIS).

Group B: Longer-Term and Seasonal Planning Issues

Seasonal Planning  NOTE- TO BE DISCUSSED WITH PLWG

Recommendations 5 – 8 address the responsibilities of TOPs/TPs for seasonal planning, especially in terms expanding the scope of their seasonal planning studies to include external facilities and the impact of sub-100 kV facilities, both internal and external to the TOP/TP’s system, on bulk power system reliability.  The recommendations also stress the importance of sharing information with neighboring TOPs and the RC regarding overload relay trip settings that fall below or near the emergency ratings of their facilities.

Response to Recommendations 5-8

- How are TOP operators alerted to and prepared to respond to first contingency conditions on their own and their neighbors’ systems?

ERCOT ISO has total visibility of the entire ERCOT footprint and performs the seasonal analysis of the entire ERCOT Interconnection.  During the current seasonal planning process, a full contingency analysis of the entire ERCOT Interconnection is conducted. ERCOT ISO alerts Local Control Centers of contingencies on neighboring LCC systems that could impact another LCC’s internal system and the need to plan for such contingencies.  Several neighboring LCCs model each other’s systems to a certain extent that may indicate contingency based issues within their neighbors’ borders, but ERCOT ISO processes are the key in coordinating contingency implications among neighboring LCCs and TPs.

- How do seasonal studies evaluate the entire region whereby TOPs can see the effect on one area from a contingency occurring in another area?  How does the seasonal planning process ensure there are no study gaps/seams between parts of the region?

ERCOT ISO and its LCCs act as a single Region with ERCOT ISO in the lead for the operational seasonal studies.  ERCOT ISO uses its 90-day Outage study as a seasonal study.  It provides a continuously updated look ahead that establishes that the temporal model (representing the expected physical system) with known outages is adequate to reliably serve the expected load.  The study is a steady-state analysis that uses a full contingency set.  If voltage problems are suspected, the steady-state analysis may be supplemented with dynamic voltage stability studies.

- In the seasonal study process, which elements, including those below 100 kV that can affect the reliability of the BPS, are deemed appropriate for study in contingency analysis (i.e. included as contingencies and the impacts of contingencies)?

ERCOT ISO has total visibility of the entire ERCOT Interconnection footprint and performs the seasonal analysis of the entire ERCOT Interconnection which includes the entire transmission network above 60 kV.  During the seasonal planning process, a full contingency analysis of the entire ERCOT Interconnection is conducted.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Consideration and evaluation of Private Use Networks in studies.

- Grid management regarding 69 kV elements

- Under what conditions are seasonal studies performed by TOPs for shoulder periods such as Spring and Fall when load can still be high but transmission elements and generators may be scheduled out of service for maintenance?  What load levels are considered?

ERCOT ISO runs some different studies and considers 90/10 conditions in the load forecast.  The continuously rolling 90-day outage study is performed and loads in the cases are continually changing to match the expected seasonal conditions.  ERCOT ISO will also study off-peak loads and additional load variations when required.  The study of multiple load levels has been and continues to be a discussion point for ERCOT ISO and the LCCs.  The overall forecast methodology by ERCOT ISO has changed to include the extreme weather events of 2011 (both in the winter and summer).  Internally, LCCs study several different load levels.  Load variation is somewhat LCC dependent as geography has to be considered (e.g. Dallas load variation versus western Texas load variation are quite different).  Load variation is required to provide a load forecast to ERCOT ISO.  Working Groups in the ERCOT Interconnection, like the Steady State Working Group, have processes in place to study load variations within the system.

- What is the process to share overload trip settings on transformers and transmission lines between neighboring TOPs, the RC, neighboring TPs, and the PC to ensure that the settings are incorporated into the next-day and seasonal planning process?

Texas RE has been made aware that overload trip settings are not directly shared or modeled in planning cases, except perhaps in ratings for some equipment types (where relay settings are found to be the most limiting element when calculating the ratings).  The Steady State Working Group Procedure Manual states that: “Facility ratings shall not exceed the most limiting applicable equipment rating of the individual equipment that comprises the facility. If the continuous or two (2) hour ratings of any series elements at the station terminals is less than the associated transmission line’s continuous or two (2) hour rating, then the most limiting elements’ rating data will be used as the Rate A and/or Rate B rating for the transmission line.  The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices.”

Overload trip settings are primarily shared among neighboring entities to verify protective relay coordination (e.g. PRC-001 requirements).  PRC-023 is used as the basis in evaluating relay loadability settings for any system elements subject to PRC-023.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Processes used to notify identified most limiting elements, with emphasis on relays, in a facility rating and the value of such notification.

- Processes for recognition of relay overload settings that exceed or are equal to ratings in operational tools (such as RTCA) within ERCOT ISO systems.

- How does the ERCOT Interconnection ensure that seasonal planning studies address the interaction of various Protection Systems, especially Special Protection Systems and UVLS systems that are designed to operate post-contingency?

Coordination of protective systems with SPS, UVLS, and post-contingent mitigation plans need a thorough review with emphasis on relay settings overlap and coordination.    In general, there is significant effort regarding coordination of protections systems but there may be isolated cases indicative of a process review.

Group B: Longer-Term and Seasonal Planning Issues

Near- and Long-Term Planning NOTE- TO BE DISCUSSED WITH PLWG

Recommendations 9 – 10 focus on the importance of addressing gaps in the planning processes of TPs, and PCs, especially where these gaps result in a lack of consideration for critical system conditions, impact of sub-100 kV facilities, interaction of Protection Systems, and failure to benchmark models against actual system conditions that occur during unusual system events.

Response to Recommendations 9-10

- How do the near- and long-term planning studies conducted by TPs and PCs evaluate the impacts of major transmission outages under heavy transfer conditions?

Cases are prepared for peak conditions and special studies also accompany planned outage requests.   During the planning process, a full contingency analysis of the entire ERCOT Interconnection is conducted.  Impacts are reviewed by TPs and PCs as a case of normal business.  The planning process dictates evaluation criteria used to determine the need for new facilities.  The Regional Planning Group provides a primary forum for discussion, input and comment on issues related to planning the ERCOT system for reliable and efficient operation.  The Planning Working Group identifies any needed improvements to planning criteria, processes, and data provision requirements as well as assisting in the review and analysis of unusual or emergency type events having a significant impact on the ERCOT Interconnection transmission system.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Evaluation by PC and TPs to determine if similar conditions (such as the result of the single contingency loss in WECC) are possible in the ERCOT Interconnection.

- How do these studies evaluate the impact of such outages on sub-100 kV facilities, especially those operated in parallel with the BES, to determine whether any potential exists for system cascading?

ERCOT ISO has total visibility of the entire ERCOT Interconnection footprint and performs the planning analysis of the ERCOT Interconnection which includes the entire transmission network above 60 kV.  During the planning process, a full contingency analysis of the entire ERCOT Interconnection is conducted.   The impact evaluation is completed at all voltage levels above 60 kV and there has been no differentiation noted in actions based on the voltage levels.

- How does the ERCOT Interconnection ensure that near- and long-term planning studies address the interaction of various Protection Systems, especially Special Protection Systems and UVLS systems that are designed to operate post-contingency?

Coordination of protective systems with SPS, UVLS, and post contingent mitigation plans need a thorough review with emphasis on relay overload limitations.  In general, there is significant effort regarding coordination of protections systems but there may be isolated cases indicative of a process review.

- What does the Region do to benchmark its planning models against real system conditions, especially severe and unusual system conditions? When does the Region benchmark its planning models?

The overall forecast methodology by ERCOT ISO has changed to include the extreme weather events of 2011 (both in the winter and summer). ERCOT ISO specifically publishes two seasonal assessments each year in Summer and Winter that aim to include impacts of more severe conditions.  Models are updated to correct discrepancies discovered during operational studies and conditions, faults, and disturbances.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Overall approach to benchmarking of ERCOT ISO and TPs planning models against real system conditions.

- How do system dynamic studies take into account protective relay (PRC-023), UVLS, and UFLS schemes?

ERCOT ISO adds existing UVLS and UFLS relay data to dynamic studies as needed.  Load Resources relay data that trigger at 59.7 Hz are also added to studies as needed.  Coordination and impact of transmission line relaying in particular needs to be reviewed in these dynamics analyses.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Consideration of protection coordination in dynamics case building with appropriate working groups.

Group A: Next-Day Planning and Real-Time Operating Issues

Situational Awareness

Recommendations 11 – 16 cover a broad range of situational awareness issues, including: real-time visibility of external systems; adequacy of real-time tools; reliance on post-contingency mitigation measures; communicating the need for backup when RTCA capabilities are lost or impaired; and inconsistencies between real-time and planning models.

Response to Recommendations 11-16

- Which TOPs in the ERCOT Interconnection have RTCA or State Estimator (SE) tools and visibility of external systems, and what potential gaps are left?  How many TOPs have real-time tools versus having other entities that perform real time analysis for them?

ERCOT ISO as a TOP and the only RC in the Interconnection has total visibility of the entire ERCOT Interconnection with backup capability and performs real-time analysis of the entire ERCOT Interconnection.  ERCOT ISO implements reliable real-time tools that provide situational awareness to identify and plan for contingencies.  ERCOT ISO uses a significant amount of tools and applications such as STNET, STCA, RTNET, RTCA, VSAT, TSAT, and TCM to manage the ERCOT Interconnection system.  ERCOT ISO maintains the real-time tools and off-line study tools necessary to provide N-1 visibility for the entire ERCOT Interconnection.   LCCs have access to a System Operations Test Environment (SOTE) through which ERCOT ISO provides State Estimator case results every five minutes.  The SOTE does not provide real time visibility to the LCCs.  Some LCCs may use the SOTE studies and data to validate internal studies.

LCC capabilities for real-time visibility and situational awareness vary across the ERCOT Interconnection.  Some Local Control Centers have real time tools, but these are operated for the benefit of the individual Local Control Center and not explicitly for ERCOT ISO purposes.  Some LCCs model facilities operated by another LCC (total and partial- the practice varies) and have utilized options to retrieve some real-time data from ERCOT ISO.  There is limited data sharing from LCCs to other LCCs via ICCP links.  All LCCs have access to the ERCOT ISO model which includes all LCC facilities and have the option to retrieve real-time data from ERCOT ISO via ICCP links; however, as noted before, this data is sometimes not in a format that can be readily incorporated into LCC applications.  LCCs work extensively with ERCOT ISO and neighboring LCCs on issues that cross boundaries.

ERCOT ISO determines System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs).  Multi-element SOLs and IROLs may not be necessarily modeled in ERCOT's Real-Time Contingency Analysis (RTCA) (i.e., each contingency analysis output shows result on individual element, not on the multi-element SOLs/IROLs as a whole).  Multi-element SOLs and IROLs are modeled in other tools (e.g., VSAT) used by ERCOT ISO to manage the ERCOT Interconnection system.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Procedure for each LCC’s communication efforts with other LCCs, other than ERCOT ISO, regarding their tools or the solutions from the tools.

- Study processes regarding SPS interactions within real-time applications.

- LCCs real time visibility outside of their system (and including Private Use Networks) for operator situational awareness.

- Possible SOTE enhancements to provide increased situational awareness from a broader perspective for the LCCs.

- PUN modeling and information included in both planning and operational studies to increase situational awareness for the ERCOT ISO and LCCs.

- LCC RTCA capabilities, internal RTCA processes, and process for sharing with ERCOT ISO and other LCCs.

- ERCOT ISO review of plans regarding loss of its SE/RTCA functionality, SE/RTCA application failure, RTCA contingencies failure to converge, and associated notification process for these conditions where applicable.

- Post-contingency mitigation measures:

  - To what extent do TOPs and the RC rely on post-contingency mitigation measures?  If so, how are these measures evaluated to ensure they do not lead to cascading outages under severe or unusual system conditions?

Post-contingency mitigation measures are used in the ERCOT Interconnection.  The development of post-contingency mitigation measures is coordinated between ERCOT ISO and LCCs, with communication and impact of the measures representing a significant part of the effort.  Upon request of ERCOT ISO, LCCs may provide additional information or assist in developing post-contingency mitigation plans. The development includes the study of conditions and outcomes, which may be based on temporary abnormal conditions such as equipment outages.   ERCOT ISO has ultimate approval authority for all mitigation plans.  The procedures for development of post-contingency mitigation plans have been developed by ERCOT ISO.  Past ERCOT events have provided examples regarding to what extent LCCs and the ERCOT ISO rely on post-contingency mitigation measures and how those measures are evaluated to avoid cascading outages under severe or unusual system conditions.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Further verification that the analysis leading to the mitigation plan adequately identifies the concerns raised by NERC, looking at recent system events here as well as the WECC event.  The recognition of relay overload settings will play a part in developing any new processes associated with this recommendation.

- Further investigation of ERCOT ISO’s management of the ERCOT Interconnection system utilizing ratings provided by LCCs.

  - How are affected neighboring TOPs notified of possible ramifications of these post-contingency measures?

The development of post-contingency mitigation measures is coordinated between ERCOT ISO and LCCs, with communication and impact of the measures representing a significant part of the effort.  ERCOT ISO has ultimate approval authority for all mitigation plans.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Further verification that the analysis leading to the mitigation plan adequately identifies the concerns raised by NERC, looking at recent system events here as well as the WECC event.

  - How do post-contingency mitigation measures take into consideration the effects of protective relay actions (e.g. PRC-023 settings, UVLS system response, etc.)?

In general, it is unclear how protection system settings are considered by ERCOT ISO during the development of post contingency mitigation plans.  There may be cases indicative of a need for a process review when viability of post-contingency mitigation plans is impacted by protection system settings.   Based on review of the WECC event, LCCs have proposed to ERCOT ISO, a process to confirm protective relay overload settings when developing post-contingency mitigation measures.   System Operators need to have time to take actions or be aware of automatic protection system operations that may be encountered.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Process being considered by ERCOT ISO and LCCs regarding the consideration of relay overload settings in the development of post-contingency mitigation plans.

  - How can the post-contingency mitigation plans be implemented by System Operators in a time-frame necessary to take the mitigating actions, considering the effects of these relay actions?

This requires careful analysis and planning in the development of the post-contingency mitigation plan, as the San Diego event shows that certain protection system actions will occur before System Operators are likely able to act.  As part of the proposed LCC process to confirm protective relay settings when developing post-contingency mitigation measures, an analysis of the time-frame necessary to take the mitigating actions, considering the effects of these relay actions, as well as the time required for LCCs to implement ERCOT ISO directives needs to be reviewed.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Process being considered by ERCOT ISO and LCCs regarding the consideration of relay overload settings in the development of post-contingency mitigation plans.

- What steps are taken to ensure consistency between real-time and planning models?

ERCOT ISO has a process in place to ensure consistency between operations and planning models based on local rules (ERCOT Protocols) in place.  The ERCOT ISO processes, which involve Registered Entities, are unique in the industry and help ensure consistency between planning and operational model data.  Model data is submitted by Registered Entities to ERCOT ISO, which is responsible for maintaining an accurate computer model for the ERCOT Interconnection utilized for analyzing and planning system operations.  The data is incorporated directly into a time-based modeling system that serves as the base platform for model data used in real-time and in future planning models (referred to as the Network Model Management System in the Region).  ERCOT ISO manages the modeling process which includes several data validation and feedback milestones with the Registered Entities.  Topology processing is coordinated and approved with the ERCOT LCCs.  ERCOT’s Operations & Planning Synchronization Task Force was created in the Spring of 2012 to help address enhancements to the planning and operations processes regarding the utilization of models and modeling data within the ERCOT Interconnection.  The ERCOT Interconnection had made considerable progress in this area even prior to the WECC event.

- To what extent have the TOPs in your region incorporated the recommendations of the NERC Real-Time Tools Best Practices Task Force?

ERCOT ISO is the RC for the ERCOT Interconnection, is also the only TOP required to operate the State Estimator and RTCA tools for the entire ERCOT Interconnection. ERCOT ISO was the only TOP operating in the ERCOT Interconnection at the time the referenced best practices were developed.  ERCOT ISO provided experts to the Task Force for the development of the recommendations.  Some LCCs have evaluated the report and enhanced their practices where applicable.

Consideration of BES Equipment

Recommendation 17 addresses the need for consideration, both in advanced studies and in real-time operations, of sub-100 kV facilities operated in parallel with the BES that can have an impact on bulk power system reliability.

Response to Recommendation 17:

- What steps are taken to ensure that sub-100 kV facilities that could impact bulk power system reliability are considered in both real-time and advanced studies, especially during severe or unusual system conditions?

ERCOT ISO and LCCs include the sub-100kV networks in their models and next-day studies for the Region; therefore, effects of system changes on these facilities are included in studies.  Facility owners submit model data for all facilities 60 kV and above to ERCOT ISO prior to the facilities being placed in service. Studies are performed that include all transmission facilities regardless of voltage level.  ERCOT ISO includes all 69 kV contingencies in all EMS studies (real-time, outage coordination, day-ahead SOL studies, etc.).  ERCOT ISO includes select 69 kV contingencies for inclusion in Market Management System studies which includes Reliability Unit Commitment (RUC) studies.  ERCOT ISO incorporates the study results into its security constrained economic dispatch of generation and its direction to the Local Control Centers.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Further review to determine if 69 kV issues are given different treatment in studies and action plans and/or if impacts of certain private use networks (which may be above or below 100 kV) are thoroughly considered.

Interconnection Reliability Operating Limits

Recommendation 18 refers to the identification and recognition of Interconnection Reliability Operating Limits (IROLs), both in day-ahead studies and in real-time operations.

Response to Recommendation 18:

- What is the procedure for identifying IROLs within ERCOT and how are these limits shared and coordinated with TOPs within the Region?

ERCOT ISO is responsible for identifying IROLs as the RC and PA within the ERCOT Interconnection.  ERCOT ISO maintains several procedures managing the identification, monitoring, publication, and coordination of IROLs and SOLs within the Region (e.g.,”ERCOT System Operating Limit Methodology for the Operations Horizon” procedure).   ERCOT ISO reviews these processes regularly and incorporates necessary improvements considering comments from the LCCs with the ERCOT Interconnection.  ERCOT ISO processes identify SOLs that are potential IROLs (not confirmed IROLs) and addresses the SOLs in the real-time.   The LCCs submit the necessary data, including facility ratings per ERCOT SOL Methodology, to ERCOT ISO to facilitate identification of IROLs and SOLs.   Identified IROLs are posted daily for review by LCCs.  ERCOT ISO has indicated that the procedures involving identification of SOLs and potential IROLs were under review by ERCOT ISO before this NERC request was provided.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Technical justification for IROLs, as currently defined by the ERCOT ISO procedure to consider other conditions that may result in IROL-related consequences (loss of load not meeting the current threshold level required to be identified as an IROL).

- What is the process to consider whether any System Operating Limits (SOLs) constitute an IROL in real-time, day-ahead, and seasonal studies?

ERCOT ISO evaluates all IROLs on an annual basis. ERCOT ISO also reviews SOL exceedances to determine if they qualify as potential IROLs based on the following criteria defined in the document “ERCOT System Operating Limit Methodology For The Operations Horizon”:

    - “Potential IROLs will be investigated when the Real-Time Contingency Analysis application indicates a thermal rating exceedance in excess of 125% of the SOL of the monitored facility rating (Emergency Rating).

    - Potential IROLs will also be investigated for base case exceedance greater than 100% of the normal facility ratings.

    - Potential IROLs will also be investigated when the Real-Time Contingency Analysis application indicates an under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities or an over-voltage condition greater than 110% across three or more related BES facilities.

    - An unsolved or divergent contingency is present in RTCA.”

- What is the process to validate existing SOLs and ensure that they take into account all transmission and generation facilities that impact BPS reliability?

The LCCs submit model data to ERCOT ISO that includes the facility ratings as one of the components used by ERCOT ISO to identify IROLs and SOLs.  The LCCs work extensively with ERCOT ISO on the provision of ratings that may constitute SOLs/IROLs and SOLs, in general, are well known because of the basis for determining SOLs are the ratings provided.  A review of the Facility Rating Methodology, sharing of relay overload settings, and the general management of facilities based on the ratings provided will be topics for further discussion among Texas RE stakeholders.

- What are the limitations to tools necessary to identify and monitor all SOLs (including IROLs) in real-time, day-ahead, and seasonal studies?  Examples may be multi-element SOL’s in RTCA or SPS modeling in RTCA.

Multi-element SOLs and IROLs may not be necessarily modeled in ERCOT's Real-Time Contingency Analysis (RTCA) (i.e. each contingency analysis output shows result on individual element, not on the multi-element SOLs/IROLs as a whole).  Multi-element SOLs and IROLs are modeled in other tools (e.g. VSAT and TSAT) which provide real-time monitoring but may lack post-contingency analysis. More review of SPS interaction with real-time applications will also be considered.

Protection Systems

Recommendations 19 – 26 address multiple issues related to Protection Systems, including: regular review, analysis, and coordination of Special Protection Systems with and among interconnected systems, especially under adverse system conditions; sensitivity of turbine control systems during extreme events; communicating to neighboring systems and RCs equipment when overload relay settings are below or only marginally above applicable ratings; reflecting overload relay settings in the determination of System Operating Limits (SOLs) (including IROLs).

Response to Recommendations 19-26:

- How do TOPs share with the RC and neighboring TOPs overload relay trip settings on transformers and transmission lines that could impact the reliability of the BPS?

Each LCC coordinates protective systems on major transmission lines and interconnections with other LCCs and Generator Operators that are impacted by the protection system.  Each affected LCC coordinates protective systems on major transmission lines and interconnections that impact transmission facility capacity with ERCOT ISO.  LCCs share all facility ratings with ERCOT ISO including those that are limited by relay trip settings.  There has not been an explicit requirement for the LCC to share additional rating related data above and beyond the most limiting series element based rating set.  However, based on the questions regarding the relay overload settings, LCCs and ERCOT ISO are reviewing possible changes to the procedures for the development of post-contingency mitigation plans used in the ERCOT Interconnection.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Consideration of relay settings by LCCs in providing ratings to ERCOT ISO and in coordinating such information to other LCCs, particularly in consideration of post-contingency mitigation plan development.

- Recognition of overload settings exceeding ratings in operational tools (such as RTCA) within ERCOT ISO systems

- How do TOPs share with neighboring TOPs, overload trip settings below 150% of the normal rating or below 115% of the highest emergency rating, whichever of these two values is greater?  If these conditions exist, do TOPs share their operating procedures for mitigating the problem?  Are these operating procedures pre- or post-contingency?  For post-contingency procedures, how is it established that there is enough time for operators to initiate the procedures based on the time delays associated with the relay settings?

Each LCC coordinates protective systems on major transmission lines and interconnections with LCCs and Generator Operators that are impacted by the protection system.  Each affected LCC coordinates protective systems on major transmission lines and interconnections that impact transmission facility capacity with ERCOT ISO.  Such coordination includes sharing overload relay trip settings that could impact the reliability of the BPS, if applicable.  If the applicable facility is rated above 200 kV or has been identified as operationally significant to BPS reliability by ERCOT ISO, then PRC-023 requires that the overload relay trip setting be 150% of the two hour emergency rating in the ERCOT Interconnection.   Therefore, if the applicable facility is operationally significant to the reliability of the BPS, the overload settings would not be below 150% of the normal rating or 115% of the highest emergency rating.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Consideration of relay settings by LCCs in providing ratings to ERCOT ISO and in coordinating such information to other LCCs, particularly regarding post-contingency mitigation plan development.

- Recognition of overload settings exceeding ratings in operational tools (such as RTCA) within ERCOT ISO systems.

- How frequently do the TOPs review Special Protection Systems for their continued necessity and their coordination with other similar systems and within the Interconnection?

As indicated in ERCOT Nodal Operating Guide 6.2.2 (14)(a), ERCOT ISO and the affected LCC each conduct a review of each existing SPS at least every five years as required by changes in system conditions.  The SPS review includes demonstration of performance requirements for inadvertent operation of an SPS.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Processes to ensure SPS coordination efforts with other SPSs as well as the interaction with other Protection Systems within the ERCOT Interconnection.

- What efforts are underway to evaluate the performance of generators under severe or unusual system conditions, especially with regard to the behavior of turbine control systems and underfrequency relay coordination?

A review by Texas RE utilizing the technical working group expertise within the ERCOT Interconnection was conducted to determine the evaluation efforts regarding the performance of generators under severe or unusual system conditions, especially with regard to the sensitivity of turbine control systems during extreme events.  Speed sensors are an existing part of the plant distributed control system (DCS) and could trigger an overspeed trip to protect generator equipment. Control coordination is typically done during commissioning, and subsequently on an as-needed basis. Current efforts of ERCOT working groups to provide feedback to GO/GOPs have resulted in a reduction of sympathetic unit trips.

Angular Separation

Recommendation 27 addresses the need for tools to determine, in advance of contingencies, the angular separation following line trips under a wide range of system conditions, as well as the need for plans for reclosing lines with large phase angle differences.

Response to Recommendation 27:

- Which TOPs or the RC have identified or can identify, from seasonal and operational planning studies and in real time, the standing angles that would result following major transmission line outages?

The ERCOT ISO State Estimator shows the calculated phase angle for every bus in the system.  ERCOT ISO knows phase angle differences between buses at all times.   SOTE information contains phase angle information and is available to LCCs in the ERCOT Interconnection; however, SOTE does not provide real time visibility to the LCCs.  Some LCCs may use the SOTE data to validate internal studies.

Texas RE will continue to seek feedback and monitor any progress on the following;

- Process for studies that may indicate concerns with the standing angles that would result following major transmission line outages.

- Where are there PMUs or PMU-capable digital relays located and streaming data such that post-contingency angles can be seen directly in SCADA/EMS systems of the TOPs or RC?

ERCOT ISO and Registered Entities have participated in discussion of PMU applications in the ERCOT Interconnection.  Some LCC’s have pilot usage of PMUs, but additional information from ERCOT ISO and Registered Entities will be requested to evaluate PMU utilization for this purpose for on-line or off-line applications.  Ref:  https://www.naspi.org/File.aspx?fileID=987

- Where does the RC have predetermined plans for reducing angles to within synchro-check relay settings to allow prompt reclosing of lines?

Any post-contingency voltage angle limit impacts are addressed as part of a post-contingency mitigation plan, similar to thermal limits exceeded post-contingency.

Texas RE will continue to seek feedback and monitor any progress on the following:

- Process for plans where studies may indicate concerns with the standing angles that would result following major transmission line outages.

The Common Information Model (“CIM”) is defined as follows:  A standard way to communicate information about a transmission system.  The CIM is used to describe the ERCOT transmission system topology consisting of Transmission Elements, including all the parameters needed to describe the Transmission Elements and how they interrelate to one another.  The CIM that ERCOT uses must conform to the Electric Power Research Institute (EPRI) standards for CIMs.

The Network Operations Model is defined as follows:  A representation of the ERCOT System providing the complete physical network definition, characteristics, ratings, and operational limits of all elements of the ERCOT Transmission Grid and other information from Transmission Service Providers, Resource Entities, and Qualified Scheduling Entities.