ERCOT Planning Guide Section 4: Transmission Planning Criteria September 1, 2011

4	tRANSMISSION pLANNING CRITERIA	1

4.1	Introduction	1

4.1.1	Reliability Criteria	2

4.1.1.1	Planning Assumptions	2

4.1.1.2	Performance Requirements for Credible Single Contingencies for Transmission Planning	2

4.1.1.3	Voltage Stability Margin	2

4.1.2	ERCOT Application of NERC Standards for System Assessments	3

4.1.2.1	Category C	3

4.1.2.2	Category D	4

# 4	tRANSMISSION pLANNING CRITERIA

4.1	Introduction

(1)	ERCOT employs both reliability criteria and economic criteria in evaluating the need for transmission system improvements.  The economic criteria are included in Protocol Section 3.11.2, Planning Criteria.  This Planning Guide provides the reliability criteria.

(2)	The ERCOT System consists of those generation and Transmission Facilities (60 kV and higher voltages) that are controlled by individual Market Participants and that function as part of an integrated and coordinated system.

(3)	To maintain reliable operation of the ERCOT System, it is necessary that all stakeholders observe and subscribe to certain minimum planning criteria.  The criteria set forth herein, combined with the applicable North American Electric Reliability Corporation (NERC) Reliability Standards, constitute the aforementioned minimum planning criteria.  Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, ERCOT recognizes that events more severe than those outlined in these criteria could cause grid separation and other tests may also be performed.

(4)	The complexity and uncertainty inherent in the planning and operation of the ERCOT System make exhaustive studies impracticable; therefore, to gain maximum benefit from the limited number of tests performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

(5)	ERCOT and each Transmission Service Provider (TSP) will perform steady-state, and dynamic analysis and each TSP will perform short circuit analysis appropriate to ensure the reliability of the ERCOT System and implement appropriate solutions.

(6)	ERCOT in coordination with the TSPs shall determine and demonstrate the need for any static and/or dynamic Reactive Power capability in excess of the explicit requirements of the Protocols and Operating Guides that is necessary to ensure compliance with the planning criteria.  ERCOT shall establish specific TSP responsibility for any associated facility additions.

(7)	The base cases created by the Steady-State Working Group (SSWG), System Protection Working Group (SPWG), and ERCOT are available for use by Market Participants.

(8)	If a TSP has its own planning criteria in addition to those defined in this Planning Guide, the TSP shall provide documentation of those criteria to ERCOT.  ERCOT shall post the documentation on the Planning and Operations Information website.  The TSP shall notify ERCOT of any changes to their planning criteria and provide revised documentation within 30 days of such change.

4.1.1	Reliability Criteria

4.1.1.1	Planning Assumptions

The following assumptions may be used in planning studies:

(a)

Reasonable variations of load forecast.

(b)	Reasonable variations of generation commitment and dispatch applicable to transmission planning analyses on a case-by-case basis may include, but are not limited to, the following methods:

(i)	Production cost model simulation, security constrained optimal power flow, or similar modeling tools that analyze the ERCOT System using hourly generation dispatch assumptions;

(ii)	Modeling of high wind generation conditions, where applicable; or

(iii)	Modeling of low or no wind generation conditions, where applicable.

4.1.1.2	Reliability Performance Criteria

The following performance criteria shall be adhered to in planning analyses.  ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  In the case where a Transmission Facility improvement is required to meet these criteria, but the improvement cannot be implemented in time to resolve the performance deficiency, a Remedial Action Plan (RAP) or Special Protection System (SPS) may be used to temporarily resolve the deficiency until the improvement has been implemented.

- With all facilities in their normal state (no contingency), all facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding and there shall be no non-consequential load loss;

- With all other facilities in their normal state, the loss of a single generator, transmission line circuit, transformer, shunt device, FACTS device, or double circuit transmission line (two circuits sharing a tower for 0.5 miles or greater) with or without a three-phase fault with normal clearing, all facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss;

- With all other facilities in their normal state, the loss of a bus section due to a single-line-to-ground fault or an internal breaker fault, all facilities shall be within their applicable ratings and the system shall be stable with no cascading or uncontrolled islanding. A Mitigation Plan (MP), RAP or SPS may be planned on a permanent basis to resolve a performance deficiency under this condition;

- With any single generating unit unavailable, including an entire combined cycle train if no part of the train cannot operate with one of the units offline per the Resource Asset Registration Form, the loss of a single generator, transmission line circuit, transformer, shunt device, FACTS device, or double circuit transmission line (two circuits sharing a tower for 0.5 miles or greater) with or without a three-phase fault with normal clearing, all facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss. A RAP or SPS may be planned on a permanent basis to resolve a performance deficiency under this condition;

- With all other facilities in their normal state, the loss of elements as a consequence of a stuck breaker attempting to clear a fault on single generator, transmission line circuit, transformer, shunt device, FACTS device, internal breaker, or bus section, all facilities shall be within their applicable ratings and the system shall be stable with no cascading or uncontrolled islanding. A MP, RAP or SPS may be planned on a permanent basis to resolve a performance deficiency under this condition;

4.1.1.3	Voltage Stability Margin

Voltage stability margin shall be sufficient to maintain post-transient voltage stability under the following study conditions for each ERCOT or TSP-defined areas:

(a)	A 5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas; and NERC Category A or B operating conditions; and

(b)	A 2.5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas and NERC Category C operating conditions.

4.1.2	ERCOT Application of NERC Standards for System Assessments

4.1.2.1	Category C

(1)	Bus Section Definition - "Bus Section" shall be interpreted to mean any section of bus work, which would be isolated by normal relay/breaker operation when faulted.

(2)	Manual System Adjustments Definition - "Manual System Adjustments" shall be interpreted to include only operator actions that:

(a)	Would be made no later than one hour after clearing of the first fault;

(b)	Are made using remote control capability or communications with other operators having such capability;

(c)	Include circuit switching, changes in the schedules of Generation Resources operating at clearing of the first fault, and changes in the schedules of other Generation Resources that can contribute within one hour; and

(d)	Exclude the physical repair or replacement of damaged equipment and the starting of any Generation Resource that cannot contribute within one hour.

(3)	Planned Loss of Demand or Curtailed Firm Transfer Definition - All Load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged with associated written operating procedures.  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

(4)	Cascading Outage Definition - Cascading Outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

(5)	Implementation Guidelines - Evaluation of all the possible combination of facility Outages under Category C is not required.  Each TSP with bulk Transmission Facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events.  In either case, the selected contingencies must indicate more severe results or impacts based on the engineering judgment of the facility owner, ERCOT or any TSP.  An explanation of why any remaining contingencies would produce less severe system results shall be available as supporting information.

4.1.2.2	Category D

(1)	For the purpose of evaluating the consequences resulting from a Category D event, a Large Load or Major Load Center is an electrical demand of between 50 and 500 MW.  This may be a large single Load or a group of electrically close Loads.  The loss of this demand will not include any other system elements other than those directly connected.

(2)	Evaluations of Category D contingencies are not required to be performed annually.  Evaluations should be performed for the following:

(a)	Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study; and

(b)	Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, ERCOT or any TSP, have unacceptable consequences.