ERCOT Operations Report

July 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 7/7/2012 7:48 | 59.829 | 51 | Unit trip with 624 MW net online. |
| 7/8/2012 20:57 | 59.803 | 128 | Unit trip with 780 MW net online. |
| 7/9/2012 9:28 | 59.888 | 13 | Multiple unit trips with 716 MW net online. |
| 7/10/2012 20:46 | 59.714 | 127 | Multiple unit trips with 1120 MW net online. |
| 7/16/2012 19:03 | 59.872 | 64 | Unit trip with 598 MW net online. |
| 7/23/2012 14:41 | 59.885 | 76 | Unit trip with 521 MW net online. |
| 7/30/2012 15:51 | 59.817 | 152 | Unit trip with 654 MW net online. |
| 7/30/2012 16:03 | 59.709 | 216 | Multiple unit trips with 1295 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration (s) | Summary |
| --- | --- | --- | --- |
| 07/10/2012 20:46:34 | DCS event | 20 | The event was caused by the loss of two units. The units were generating a total of 1122 MW before trip. The frequency dropped to 59.71 Hz. The oscillating frequency of 0.57 Hz and 10.92% damping ratio was observed during the event. |
| 07/30/2012 16:03:44 | DCS event | 28 | The event was caused by the loss of two units. The units were generating a total of 1298 MW before trip. The frequency dropped to 59.706 Hz. The oscillating frequency of 0.65 Hz and 5.31% damping ratio was observed during the event. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 7/7/12 7:48:06 | 7/7/12 7:53:32 | 0:05:26 | 416.92 |  |
| 7/8/12 20:57:32 | 7/8/12 21:02:04 | 0:04:32 | 1138.5 |  |
| 7/9/12 9:28:28 | 7/9/12 9:30:24 | 0:01:56 | 257.5 |  |
| 7/10/12 20:46:34 | 7/10/12 20:50:46 | 0:04:12 | 1115.1 |  |
| 7/16/12 19:03:36 | 7/16/12 19:06:14 | 0:02:38 | 97.872 |  |
| 7/23/12 14:41:39 | 7/23/12 14:44:30 | 0:02:51 | 66.719 |  |
| 7/30/12 15:51:02 | 7/30/12 15:55:42 | 0:04:40 | 654.82 |  |
| 7/30/12 16:03:46 | 7/30/12 16:09:58 | 0:06:12 | 1367 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Moss Switch - Holt Switch & Amoco North Cowden 138 kV | Odessa North Axfmr1 138/69 kV | 31 |
| Lobo - San Miguel 345_138 KV Switchyards 345 V | Laquinta - Lobo 138 kV | 12 |
| Paloduro Sub - Batesville Switching Station 138 kV | Moore Switching Station - Downie Switching Station 138 kV | 12 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 12 |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4L (3) 345/138 kV | 5 |
| Fort Stockton Plant - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 5 |
| DCKT Allen Switch - Royse Switch and Monticello SES 345 kV | Centerville Road Switch Axfmr1l (3) 345/138 kV | 5 |
| Midland East - Moss Switch 345 kV | Odessa - Odessa North 138 kV | 5 |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | San Diego - Freer 69 kV | 4 |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 4 |
| Sacroc - Snyder 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 4 |
| West Batesville - Batesville Switching Station 138 kV | Moore Switching Station - Downie Switching Station 138kV | 4 |
| China Grove Switch - Morgan Creek SES 138 kV | China Grove Switch - Morgan Creek SES 138 kV | 3 |
| DCKT Skyline - Calaveras 345 kV | Cagnon Axfmr3L (3) 345/138 kV | 3 |
| Kyle - San Marcos 138 kV | Turnersville - Buda 138 kV | 3 |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 3 |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Seagoville - Kleberg Tap 138 kV | 2 |
| Mountain Creek SES - Cedar Crest Switch 138 kV | Mountain Creek SES - Trinity River Authority 138 kV | 2 |
| Forney Switch Axfmr3t (3) 345/138 kV | Balch Springs Tap - Mesquite 138 kV | 2 |
| Hiway 9 138_69A2 138/69 kV | Koch Up River 138_69A1 138/69 kV | 2 |
| Snyder Axfmr1 138/69 kV | Ennis Creek Switch Axfmr1 138/69 kV | 2 |
| Greens Bayou At1_H (3) 345/138 kV | Greens Bayou At2L (3) 345/138 kV | 2 |
| Power Plant Substation - Price Road Substation 138 kV | Power Plant Substation T1 138/69 kV | 2 |
| DCKT Olinger - Firewheel and Elmgrove 138 kV | Olinger - Ben Davis 138 kV | 2 |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North - North Cowden 69 kV | 1 |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Alice 138_69A1 138/69 kV | 1 |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4h (3) 345/138 KV | 1 |
| Golden Switch - Sun Switch 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 1 |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Prairie Creek - Parkdale Switch 138 kV | 1 |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Prairie Creek Switch - Prairie Creek 138 kV | 1 |
| Basecase | Bowie - Johnson Switch 69 kV | 1 |
| DCKT Paris Switch - Valley SES And Valley South 345 kV | Brookstone Tap - Bonham Lake Poi 138 kV | 1 |
| DCKT Paris Switch - Valley SES And Valley South 345 kV | Bonham Lake Poi - Valley SES 138 kV | 1 |
| Ena Snyder Wind - Wkn_Bkr 69 kV | Ennis Creek Switch Axfmr1 138/69 kV | 1 |
| Garfield AEN Gf_At_1 345/138 kV | Garfield AEN Gf_At_2 345/138 kV | 1 |
| DCKT Centerville Road Switch - Lake Hubbard SES - Centerville Road 138 kV | Prairie Creek Switch - Prairie Creek 138 kV | 1 |
| Asherton 138_69a1 138/69 kV | Turtle Creek Switching Station - Crystal City 69 kV | 1 |
| DCKT Austrop - Garfield LCRA & Zorn 345 kV and Austrop - Decker Power Plant 138 kV | Austrop Au_At1h (3) 345/138 kV | 1 |
| Austrop Au_At1l (3) 345/138 kV | Austrop Au_At2h (3) 345/138 kV | 1 |
| DCKT Eagle Mountain SES - Alliance - Roanoke Switch - Parker Switch 345 kV | Eagle Mountain SES - Wagley Robertson 138 kV | 1 |
| DCKT Navarro - Big Brown SES And Venus Switch 345 kV | Richland Chambers - Trinidad SES 345 kV | 1 |
| Alazan - Barney Davis and Nelson Sharpe 138 kV | Airline AEP - Cabaniss 138 kV | 1 |
| Westover (ONCOR) - Amoco South Foster 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |
| Laquinta - Lobo 138 kV | San Diego - Freer 69 kV | 1 |
| DCKT Farmersville Switch - Monticello SES 345 kV | Monticello SES - Allen Switch 345 kV | 1 |
| Andrews North Axfmr1 and Axfmr2 138/69 kV | Holt Switch - Emma Tap 69 kV | 1 |
| Pawnee Switching Station - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 1 |
| Paducah Clare Street 138_69T1 138/69 kV | Paducah Clare Street - Paducah City 69 kV | 1 |
| Rodd Field - Holly 138 kV | Airline AEP - Cabaniss 138 kV | 1 |
| DCKT Long Creek - Graham SES and Cook Field Road Switch 345 kV | Paint Creek - Murray Switch 138 kV | 1 |
| Gaf TNP - Greenbelt TNP 138 kV | Greenbelt TNP - Tejas TNP 138 kV | 1 |
| Big Lake - Twin Buttes 138 kV | Santiago - Live Oak AEP 138 kV | 1 |
| Alice - Kingsville 138 kV | Falfurrias 138_69A1 138/69 kV | 1 |
| DCKT South Texas # 1& # 2 | Lolita - Blessing 138kV | 1 |
| Morgan Creek SES - Bitter Creek & Champion Creek Switch 345KV | Tonkawa Switch - Morgan Creek SES 345 kV | 1 |
| DCKT Centerville Road Switch - Parkdale Switch 138 kV | Prairie Creek Switch - Prairie Creek 138 kV | 1 |
| Cabaniss - Airline AEP and Westside AEP 138 kV | Barney Davis - Rodd Field 138 kV | 1 |
| DCKT Navarro - Limestone Plant And Watermill Switch 345 kV | Richland Chambers - Trinidad SES 345 kV | 1 |
| Trumbull - Desoto Switch And Ennis Switch 138 kV | Ennis West Switch - Waxahachie 138 kV | 1 |
| North Alvin TNP - Meadow Sub 138 kV | PH Robinson AT1L (3) 345/138 kV | 1 |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 1 |
| Meadow Sub - PH Robinson 345 kV | North Alvin TNP - Alvin TNP 138 kV | 1 |
| Lewisville Switch Axfmr22 345/138 KV | Carrollton Northwest - Lakepointe TNP 138 kV | 1 |
| La Palma - Rio Hondo 345 kV (La_Pal_Riohon1) | Raymondville 2 - Raymondville 1 69 kV | 1 |
| DCKT Austrop - Lost Pines 345 kV | Salem At3 345/138 kV | 1 |
| Salem LCRA At3 345/138 kV | Fayetteville 26At2 345/138 kV | 1 |
| DCKT Norwood Switch - Liggett Switch and Cedar Hill Switch 345 KV | Mountain Creek SES - Trinity River Authority 138 kV | 1 |
| Lake Hubbard SES - Centerville Road Switch 138 kV | Lake Hubbard SES - Centerville Road 138 kV | 1 |
| Odessa Basin Switch - Odessa North 69 kV | Odessa North - North Cowden 69 kV | 1 |
| Lewisville Switch - Carrollton Northwest 345kV | Euless - Grapevine Highway 360 138 kV | 1 |
| Renner Switch Axfmr2h (3) 345/138 kV | Allen Switch Axfmr1h (3) 345/138 kV | 1 |
| Roanoke Switch - Parker Switch 345 kV | Parker Switch - Eagle Mountain SES 345 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 2 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 07/16/2012 | Transmission and Security Desk V1 Rev18 | 605 |
| 07/16/2012 | Shift Supervisor Desk V1 Rev16 | 604 |
| 07/16/2012 | Resource Desk V1 Rev18 | 603 |
| 07/16/2012 | Reliability Unit Commitment Desk V1 Rev16 | 602 |
| 07/16/2012 | Real Time Desk Vi Rev19 | 601 |
| 07/16/2012 | DC Tie Desk V1 Rev15 | 600 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

07/31 17:00 65,787 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | 2.85 |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.93 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 7/14/2012 | 07:58 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 14:00 - 21:00 |
| 7/30/2012 | 16:08 | ERCOT issued a Watch for PRC below 2500 MW. |

Transmission Watch

None

Emergency Notice

None

Texas RE Event Analysis

7/10 20:46	ERCOT experienced a loss of two units totaling 1130 MW of net output due to a malfunction of a control system communication switch.

7/30 16:03 	ERCOT experienced a loss of two units totaling 1298 MW of net output. Investigation is ongoing.