## Slide 1: PDCWG Report to ROS
David Kee
CPS Energy
Sydney Niemeyer
NRG Energy

## Slide 2: August 8th meeting
22 attendees representing 15 companies, ERCOT, TRE, & PUC
San Diego event
BAL-001-TRE Field trial results
Regulation deployment analysis
RRS on LRs
DR response to disturbances
Control performance metrics & GREDP
FRRS pilot
Event analysis – 3 events
Next meeting Sept. 5

## Slide 3: BAL-001-TRE Field trial results
Measurement issue found
Retooled evaluation spreadsheet
Field Trial will be re-evaluated using the modified performance measures.
Results to come in August

## Slide 4: DR Response to Disturbances
Issue around DR frequency response
Risk: counting on DR that does not perform
Recommendations:
  Review the impact of growing DR on systems (load forecast, planning, AS procurement methodologies, etc)
  Study, characterize and quantify reliability impact

## Slide 5: FRRS Pilot
Concerns over signal coordination
Question on impact of procurement of A/S quantities
Recommendation: Shrink FRRS deployment deadband to 0.010Hz

## Slide 6: Event Analysis
7-10-12@2046 – DCS event
  Passed DCS standard
  Failed ERCOT response metric
    Delivered 357MW/0.1Hz from ERCOT system
    Metric is minimum of 420MW/0.1Hz PFR
  2 Resources identified with issues
    ERCOT is engaged
  Responsive was carried on nonresponsive power augmentation
  Power Augmentation which did deploy showed delays in deployment
High Risk Scenario: IF the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard

## Slide 7: Event Analysis cont.
7-8-12@2057
  System passed ERCOT response metric
  RRS was carried on nonresponsive Resources
  One Resource seemed oversold
    ERCOT is engaged
6-2-12@13:23
  System passed initial response, failed sustained response
    Out of regulation in this event
  RRS was carried on nonresponsive Resources

## Slide 8: Event Analysis Recommendation
Growing trend of carrying RRS on nonresponsive generators
Members note protocols need clarification
PDCWG will begin task to “Clarify protocols as they relate to the primary frequency obligation of RRS providers”

## Slide 16
July 30th DCS Event

## Slide 22
Questions?