## Slide 1: RRS Supplied by Load Resources – Study Review
Reviewed study scenarios and results
Discussed study assumptions
  Effects of Hydro
  Benchmarking of models
  Model validation & verification

## Slide 2: RRS Supplied by Load Resources – Study Review
Concerns
  Question of model appropriateness and accuracy
    The PDCWG scope does not include modeling, however the experience that some members have with generator models indicates that older generators may have outdated or inaccurate models.
  Study period is up to 20 seconds
    Concern over control instability (generator swing) caused by rapid changes outside of study period (see next slide for example)
    While this concern has not been raised by past market participants, the group feels this is a valid issue.
  Study does not reveal outcomes over the long term
    Reduction in PFR is expected
      Long term impact of reducing frequency responsive capacity
      Introducing a daily risk to address a 1 in 10 year risk
      Impact to annual frequency response when evaluating to BAAL-003
  Will reduce proportional PFR from RRS providers and remove available PFR capacity from the grid.
    Less frequency responsive generation will be online providing RRS when replaced by LRs.

## Slide 3: RRS Supplied by Load Resources – Study Review
Example of generator instability risk & potential for loss of generator
Frequency decays to 59.7Hz
600MW generator adds 60MW worth of fuel to boiler to provide up governor response (+20MW/.1Hz *.3Hz)
LRs (on UFR) deploy
Frequency increases to 60.4 Hz
Generator removes 140MW worth of fuel (-20MW/.1Hz*.7Hz) to withdraw up governor response and provide down governor response
This phenomenon may increase chances of sympathetic trips causing further system degredation

## Slide 4: RRS Supplied by Load Resources – Study Review
Recommendation - Retain at least 1150 MW of proportional response that is immediately "reset" after a trip and that provides routine frequency control.
LRs are critically important to frequency recovery but too much LR response at the same time can be a serious issue. Perhaps if the LAAR had different trip points it would work.
1150 MW of frequency responsive generation is a tried a true minimum for frequency support