Karnes Electric Cooperative (KEC) and Medina Electric Cooperative (MEC) Load Addtion Project

Version 1.0

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |

| 08/30/2012 | 1.0 | Final | Ehsan Ur Rehman |
| --- | --- | --- | --- |

Table of Contents

1.	Introduction	1

2.	Reliability Analysis	4

3.	Project Options	4

4.	G-1 and N-1 Analysis	10

5.	Load Growth Scenario	11

6.	Conclusion	11

7.	Designated Providers of Transmission Facilities	11

8.	Appendices	12

# Introduction

Eagle Ford Shale oil and natural gas exploration, located in multiple counties in South Texas, stretches from the Laredo area, bounded by Maverick and Webb Counties, northeast to Gonzalez and DeWitt counties, and beyond. Electric load related to oil and gas exploration is developing in and around this area. South Texas Electric Cooperative (STEC) projects a load increase in the Dimmit, La Salle and McMullen Counties area of approximately 247 MW which will be served through the ERCOT Region transmission system by the year 2017.

Either there is no transmission in the area to serve the growing load or the existing 69 kV transmission system in the area is composed of 4/0 ACSR conductor having a rating (circuit Rate B) of 40 MVA. Most of the system has almost reached its capacity limit and thus cannot support the proposed load additions without transmission system improvements.

As a part of its Regional Planning Group (RPG) submittal, STEC proposed the following transmission improvements as their preferred option to support the Karnes and Medina Electric Cooperatives Load Addition:

Construct an approximately 47 mile 138 kV circuit on double circuit capable structures from Tilden to Reveille.

Construct a 138 kV substation with a 69/138 kV auto transformer at STEC’s 69 kV Cotulla substation. AEP’s line from Cotulla to Jardin will be looped into the new 138 kV station.

Construct a 69/138 kV autotransformer station near where STEC’s Carrizo Springs to West Crystal City 69 kV circuit crosses LCRA’s Asherton to Conoco Chittam Tap138 kV circuit. This station is referred to as BEVO in this report.

Rebuild the 3.3 mile AEP Turtle Creek to Crystal City 69 kV line. This line rebuild is in ERCOT’s 2011 5 year plan so the costs were not included in this regional project submittal.

Add a 14.4 MVAR capacitor at the STEC Carrizo Springs substation.

The above project option was submitted as a Tier 2 project with an estimated cost of approximately $ 48.4 million.

Figure I below shows the map of the areas surrounding Dimmit, La Salle and McMullen Counties.

Figure I:  Map of the area of concern

The analysis of the system needs primarily focused on steady-state thermal and voltage reliability of the ERCOT transmission system upon interconnecting the new load.

The 2011 Five-Year Transmission Plan model for the year 2016 served as the start case for the analysis since a 2017 (n-1 secure) case was not available.  The following changes were made to the 2016 case based on the most recent information received by ERCOT to create a 2017 and a 2021 loading case:

Load Changes:

Load, based on STEC’s forecast, was updated in and around the area of study (Dimmit, La Salle and McMullen Counties). A total of approximately 190 MW was modeled on the existing 69 kV transmission system. The following Table A shows the individual substation loads modeled at the KEC and MEC system:

| Substation | Current 2017 load forecast (MW) |
| --- | --- |
| Cotulla | 21.5 |
| Dilley | 6.8 |
| Big Wells | 2.8 |
| Brundage | 15.6 |
| Carrizo | 12.5 |
| West Crystal | 6.3 |
| Jardin | 29 |
| Reveille | 41 |
| Fowlerton | 44 |
| Artesia Wells | 18 |
| Tilden | 50 |
| Total | 247 |

Table A: STEC’s Load Forecast

Load, based on AEP’s forecast, was also updated in and around the area of study (specifically in Dimmit, La Salle and McMullen Counties, TX). Approximately 120 MW of additional load was modeled on AEP’s transmission system

The 2017 load forecast for STEC and AEP TCC load was approximately 1,686 MW and 6,364 MW; respectively

The 2021 load forecast for STEC and AEP TCC load was approximately 1,929 MW and 6,375 MW; respectively

Generation Updates and Changes:

Rayburn 3 (24 MW) was turned off because the unit was recently retired

Transmission Changes:

Rio Bravo – Lobo 138 kV line (Rate B: 776 MVA, approx. 26 miles) was modeled

The model contained all existing generation plus generation with signed interconnection agreements at the start of the analysis.

# Reliability Analysis

The n-1 reliability analysis was performed using TARA on the 2017 and 2021 cases. The highest overloads in the area are shown in Table I. The full AC Contingency results are presented in Appendices A and B.

| Highest Loaded Element | Contingencies | Loading in 2017 (%) | Loading in 2021 (%) |
| --- | --- | --- | --- |
| Turtle Creek – West Crystal City 69 kV line | Big Wells – Cotulla 69 kV line | 112 | 121 |
| Batesville – Crystal City 69 kV line | Carrizo – Asherton 69 kV line | 102 | 112 |

Table I: Loading on the existing 69 kV system with 2017 and 2021 loads

The results show that the existing 69 kV transmission system is heavily constrained and cannot support the new load addition without additional transmission improvements. The addition of new loads also caused under-voltage conditions on the 69 kV transmission system.

It should be noted that the analysis revealed other post-contingency overloaded elements in the region. These elements were discarded from the analysis since these are either not related to the new load addition, are very far from the area under study, or will be addressed by other projects. These elements are shaded gray in the attached spreadsheets in the Appendices A and B.

# Project Options

ERCOT studied five different alternatives (Options A through E) to identify the most reliable solution to serve the KEC and MEC load addition. The following transmission upgrades were common to all five alternatives (Option A through Option E) considered in this study:

Common Upgrades for all five alternatives studied:

Construct a new Tilden – Fowlerton – Reveille 138 kV double circuit line (approx. 47 miles on a new R.O.W.) so that each circuit Rate B is at least 240 MVA

Construct a new 138 kV substation near the STEC 69 kV Cotulla substation and loop the AEP Dilley – Cotulla 138 kV line into it

Add a (69/138 kV) autotransformer (with reverse power relays) at the Cotulla substation so that the Rate B is at least 150 MVA

Add reverse power relays at the George West autotransformer

Add a 9.6 MVAR capacitor bank at George West 69 kV substation

Add 19.2 MVAR capacitor banks at Tilden, Fowlerton and Jardin 138 kV substations

The additional upgrades required (in addition to the above listed common upgrades) for the Five Options (A-E) will be discussed in the rest of the report.

Option A (69 kV HUB):

Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it

Upgrade the autotransformer at Asherton so that the Rate B is at least 150 MVA

Upgrade the Asherton – Carrizo 69 kV line (approx. 8.3 miles) so that the circuit Rate B is at least 120 MVA

Upgrade the Dilley – Cotulla 69 kV line (approx.15.8 miles) so that the circuit Rate B is at least 120 MVA

Add 9.6 MVAR capacitor banks at Crystal City, Big Wells, and Freer 69 kV substations

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation

The total cost estimate for Option A including common upgrades is approximately $64 million.

Figure II below shows the transmission topology related to Option A upgrades:

Figure II: Option A Upgrades

The n-1 (AC contingency) analysis showed no overloads with Option A. Full AC Contingency results are provided in the Appendices C and D for the 2017 and 2021 loading cases, respectively.

Option B (BEVO 69/138 kV substation):

Construct a 138/69 kV BEVO substation near where the LCRA (TSC) Asherton – Conoco Chittam Tap 138 kV line crosses the STEC Carrizo Springs – West Crystal 69 kV line. Add a (69/138 kV) 150 MVA autotransformer at BEVO.

Upgrade the autotransformer at Asherton so that the Rate B is at least 150 MVA.

Upgrade the Asherton – Carrizo 69 kV line (approx. 8.3 miles) so that the circuit Rate B is at least 120 MVA.

Upgrade the Dilley – Cotulla 69 kV line (approx.15.8 miles) so that the circuit Rate B is at least 120 MVA.

Add 9.6 MVAR capacitor banks at Big Wells and Freer 69 kV substations.

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation.

The total cost estimate for Option B including common upgrades is approximately $66 million.

Figure III below shows the transmission topology related to Option B upgrades:

Figure III: Option B Upgrades

The n-1 (AC contingency) analysis showed no overloads with Option B. Full AC Contingency results are provided in the Appendices E and F for the 2017 and 2021 loading cases, respectively.

Option C (69kV HUB and Union substation):

Construct a 138/69 kV Union substation near where the AEP West Bates – Asherton 138 kV line crosses the STEC Carrizo Springs – Brundage 69 kV line. Add a (69/138 kV) 150 MVA auto at UNION substation.

Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it.

Install reverse power relays on the 69/138 kV Asherton autotransformer.

Add 9.6 MVAR capacitor banks at Big Wells and Freer 69 kV substations.

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation.

Add a 4.6 MVAR capacitor bank at Brundage 69 kV substation.

The total cost estimate for Option C including common upgrades is approximately $59.8 million.

Figure IV below shows the transmission topology related to Option C upgrades:

Figure IV: Option C Upgrades

The n-1 (AC contingency) analysis showed no overloads with Option C. Full AC Contingency results are provided in the Appendices G and H for the 2017 and 2021 loading cases, respectively.

Option D (69kV HUB and Big Wells autotransformer):

Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it.

Add a 69/138 kV autotransformer (with reverse power relays) at Big Wells so the Rate B is at least 150 MVA.

Install reverse power relays on the 69/138 kV autotransformer at Asherton.

Upgrade the Big Wells – Brundage 69 kV line (approx. 11.10 miles) so that the circuit Rate B is 120 MVA.

Add a 9.6 MVAR capacitor bank at Freer 69 kV substation.

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation.

Add a 4.6 MVAR capacitor bank at Brundage 69 kV substation.

The total cost estimate for Option D including common upgrades is approximately $60.8 million.

Figure V below shows the transmission topology related to Option D upgrades:

Figure V: Option D Upgrades

The n-1 (AC contingency) analysis showed no overloads with Option D. Full AC Contingency results are provided in the Appendices I and J for the 2017 and 2021 loading cases, respectively.

Option E (69kV HUB and BEVO):

Construct a 138/69 kV BEVO substation near where the LCRA (TSC) Asherton – Conoco Chittam Tap 138 kV line crosses the STEC Carrizo Springs – West Crystal 69 kV line. Loop these lines into the 138/69 kV substation and add a (69/138 kV) 150 MVA auto at BEVO.

Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it.

Add a 9.6 MVAR capacitor bank Freer 69 kV substation.

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation.

Add a 4.6 MVAR capacitor bank at Brundage 69 kV substation.

The total cost estimate for Option E including common upgrades is approximately $57 million.

Figure VI below shows the transmission topology related to Option E upgrades:

Figure VI: Option E Upgrades

The n-1 (AC contingency) analysis showed no overloads with Option E. Full AC Contingency results are provided in the Appendices K and L for the 2017 and 2021 loading cases, respectively.

It should also be noted that all five upgrade alternatives met the reliability criteria and that the upgrades discussed under Option E were the most economical. Thus, upgrades discussed under Option E were studied for additional sensitivities.

# G-1 and N-1 Analysis

In accordance with the ERCOT Planning Criteria, a G-1 + N-1 analysis was also performed by turning off nearby generation units in the study area and performing AC contingency analysis.  A sensitivity analysis (with 2021 loading case) was performed by turning off six units at Pearsall. It was found that the outage of these units did not cause any transmission violations. Full AC Contingency results, with the six Pearsall units out may be found in Appendix M.

# Load Growth Scenario

A sensitivity analysis was performed to study the impact of additional load growth in the area beyond 2021. STEC load in the area of concern was increased by 15% beyond 2021 loading. The AC contingency analysis revealed no violations.

Full AC Contingency results may be found in Appendix N.

# Conclusion

Based on the reliability analysis as described, it was determined that the following transmission upgrades studied as Option E constitute the most cost-effective solution to serve the projected load addition:

Construct a new Tilden – Fowlerton – Reveille 138 kV double circuit line (approx. 47 miles on new R.O.W.) so that each circuit Rate B is at least 240 MVA.

Construct a new 138 kV substation near the STEC 69 kV Cotulla substation and loop the AEP Dilley – Cotulla 138 kV line into it.

Add a (69/138 kV) autotransformer (with reverse power relays) at Cotulla so that the Rate B is at least 150 MVA.

Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it.

Construct a new 69/138 kV BEVO substation near where the LCRA (TSC) Asherton – Conoco Chittam Tap 138 kV line crosses the STEC Carrizo Springs – West Crystal 69 kV line. Loop these lines into BEVO and add a (69/138 kV) 150 MVA autotransformer.

Add reverse power relays on the George West autotransformer.

Add a 9.6 MVAR capacitor bank at George West 69 kV substation.

Add 19.2 MVAR capacitor banks at Tilden, Fowlerton and Jardin 138 kV substations.

Add a 9.6 MVAR capacitor bank at Freer 69 kV substation.

Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation.

Add a 4.6 MVAR capacitor bank at Brundage 69 kV substation.

# Designated Providers of Transmission Facilities

In accordance with the ERCOT Protocols, ERCOT is to designate transmission providers for projects reviewed by the RPG. These providers can agree to provide or delegate the new facilities or inform ERCOT if they do not elect to provide them. For the project scope recommended in this report STEC, AEP TCC, and LCRA (TSC) are the designated provider of all transmission facilities.

# Appendices

| Appendix A |  |
| --- | --- |
| Appendix B |  |
| Appendix C |  |
| Appendix D |  |
| Appendix E |  |
| Appendix F |  |
| Appendix G |  |
| Appendix H |  |
| Appendix I |  |
| Appendix J |  |
| Appendix K |  |
| Appendix L |  |
| Appendix M |  |
| Appendix N |  |