## Slide 1: STEC KEC-MEC Load Addition Project Regional Planning Group (RPG) Review; ERCOT Independent Review
Jeff Billo
Manager, Transmission Planning
TAC
ERCOT
September 7, 2012
1

## Slide 2: Background
Eagle Ford Shale exploration and production is rapidly increasing in South Texas
  Oil reserves estimated at 3 billion barrels and trillions of cubic feet of natural gas
  May be sixth largest oil field discovery in U.S.
  Projected 247 MW load increase on Karnes Electric Cooperative (KEC) and Medina Electric Cooperative (MEC) systems in Dimmit, La Salle and McMullen Counties
    Total existing load = 28 MW
    Multiple RPG projects addressing needs in other counties
ERCOT Public

## Slide 3: RPG Review
South Texas Electric Cooperative submitted project for RPG Review in April 2012
Transmission system in area of load additions either does not exist or is mainly made up of 4/0 conductor 69 kV lines (40 MVA)
  New transmission lines needed along with significant upgrades to existing system
ERCOT Independent Review analyzed five options
  Performed 2017 analysis with 2021 sensitivity
  AC steady-state contingency thermal and voltage analysis
  Additional sensitivity for load growth 15% above 2021 levels
  Also performed generator outage analysis
  Recommended most cost effective solution
ERCOT Public

## Slide 4: Endorsement
ERCOT will request the ERCOT BOD endorse the following improvements:
  Construct a new Tilden – Fowlerton – Reveille 138 kV double circuit line (approx. 47 miles on new R.O.W.) so that each circuit Rate B is at least 240 MVA
  Construct a new 138 kV substation near the STEC 69 kV Cotulla substation and loop the AEP Dilley – Cotulla 138 kV line into it
  Add a (69/138 kV) autotransformer (with reverse power relays) at Cotulla so that the Rate B is at least 150 MVA
  Construct a 69 kV substation on the AEP Carrizo – Crystal City 69 kV line and loop the STEC Brundage – Carrizo Springs 69 kV line into it
  Construct a new 69/138 kV BEVO substation near where the LCRA Asherton – Conoco Chittam Tap 138 kV line crosses the STEC Carrizo Springs – West Crystal 69 kV line. Loop these lines into BEVO and add a (69/138 kV) 150 MVA autotransformer
  Add reverse power relays on the George West autotransformer
  Add a 9.6 MVAR capacitor bank at George West 69 kV substation
  Add 19.2 MVAR capacitor banks at Tilden, Fowlerton and Jardin 138 kV substations
  Add a 9.6 MVAR capacitor bank at Freer 69 kV substation
  Add a 14.4 MVAR capacitor bank at Carrizo Springs 69 kV substation
  Add a 4.6 MVAR capacitor bank at Brundage 69 kV substation
The cost estimate for these improvements is ~ $57 million
ERCOT Public

## Slide 5: Questions?
ERCOT Public

## Slide 6: Appendix – Map of Study Area
ERCOT Public