## Slide 1: ERCOT Pilot Project for Fast Responding Regulation Service (FRRS)
September 7, 2012 TAC

## Slide 2: Agenda
What is Fast Responding Regulation Service (FRRS)?
Purpose of the FRRS Pilot Program
FRRS Qualification and Performance Criteria
How Will FRRS be Procured (Priced and Paid For) in the Pilot?
Proposed Implementation Schedule for the Pilot
Potential Benefits of FRRS
Questions
Appendix

## Slide 3: What is Fast Responding Regulation Service (FRRS)?
FRRS is intended to complement current regulation service.
FRRS can be ramped to its full output within 60 cycles.
FRRS is intended to respond first and help slow down the frequency decay while other resources start to respond.
FRRS is intended to respond to large frequency drops to promptly help arrest the frequency decay.
California ISO, New York ISO, PJM, ISO New England and MISO will have or already have fast responding regulation.

## Slide 4: Purpose of the FRRS pilot program
Gather and analyze data to assist in determining the potential improvements in ERCOTs ability to arrest frequency decay during unit trips due to the presence of FRRS.
Gather and analyze data to assist in determining the potential reductions of current regulation that would be appropriate due to the presence of FRRS.
Assess the operational benefit and challenges of procuring and deploying FRRS.
Gather and analyze data to assist ERCOT in developing settlement methodologies for FRRS and current regulation that use a pay for performance approach similar to what is specified in FERC Order 755.

## Slide 5: FRRS-pilot Qualification Criteria
Resources providing FRRS must be able to follow FRRS signal.
Resources requesting FRRS-up qualification
  Must be able to respond to large frequency decay triggered by loss of generation.
  Resources providing FRRS-up must provide full MW response within 60 cycles after frequency hits 59.91 Hz trigger.
Resources requesting FRRS-down qualification
  Must be able to respond to high frequency.
  Resources providing FRRS-down must provide full MW response within 60 cycles after frequency hits 60.09 Hz trigger.

## Slide 6: Pilot FRRS Qualification Criteria (continued)
Resources providing FRRS (Up and Down) must be able to continuously remain deployed for up to 8 minutes with 95% or more of the requested MW for successful qualification.
Resources that successfully demonstrate the requirement above will be qualified as FRRS capable Resources for the capacity that was requested for qualification.

## Slide 7: FRRS Performance Criteria
Resources providing Fast Responding Regulation Service shall meet the following performance criteria
MW response provided by Resources carrying FRRS in response to ERCOT FRRS signal shall be at least 95% and less than 110 % of the ERCOT deployment instruction for that Resource.
Failure of the above performance criterion during any deployment for 30% or more of the deployments during any hour shall be deemed failure of the Resource’s obligation for that hour.
When FRRS-up is not fully deployed, for sudden frequency decay where frequency declines lower than 59.91 Hz, Resources providing FRRS-up shall within 60 cycles appropriately respond to the declining frequency.
When FRRS-down is not fully deployed, for sudden frequency deviation that may cause frequency to exceed 60.09 Hz, Resources providing FRRS-down shall within 60 cycles appropriately respond to frequency.
FRRS Resource must provide high speed data with resolution no less than 32 samples per second to demonstrate their performance for (3) and (4) above. ERCOT will also review randomly selected deployments during deviations of lower magnitude to verify compliance.
Failure to meet the deployment obligations during any hour as required in paragraph (2) will lead to claw-back of capacity payment for that hour.

## Slide 8: How is FRRS Procured during the Pilot?
FRRS-up and FRRS-down amounts are specified in advance for each hour. For the pilot, ERCOT will procure up to 65 MW per hour for FRRS-up and will procure up to 35 MW per hour for FRRS-down. No changes are made to the existing REGUP and REGDN requirements.
ERCOT has a list of “Qualified” FRRS Pilot Resources. Each Tuesday QSEs inform ERCOT of the amounts available for Saturday through Friday.
ERCOT prorates amounts to Pilot Resources as necessary. Final quantities sent to QSEs (for the upcoming week).
COPs for Pilot Resources shall reflect the final schedule as REGUP and REGDN.

## Slide 9: How is FRRS is Priced and Paid for during the Pilot?
ERCOT Settlements performs settlement by creating appropriate SASM data cuts. Current REGUP and REGDN bill determinants are used. A SASM is NOT executed by the operators.
DAM clearing prices shall be used to price the FRRS awards.
The cost for pilot MWs procured are paid for similar to other AS.
Adjustments can be made depending on actual availability and performance.

## Slide 10: Background Information and Pilot Schedule
Presented and discussed the FRRS Pilot Proposal with Market Participants in June, July and August. (ETWG, WMS, ROS, and PDCWG) [Written questions received and answered.] (Adjustments made to proposed Pilot approach and Governing Document)
ERCOT presents FRRS Pilot Project to TAC at 9/7/12 TAC meeting.
Request approval for FRRS Pilot at the 9/18/12 BOD meeting.
Qualify Pilot Resources 10/18/12 through (end of pilot). [6 month Pilot starting with the first Operating Day with FRRS deployments]
ERCOT to receive the first set of offers 1-15-13. First Operating Day with FRRS deployments is 1-19-13. Continue Pilot for 6 months (7-19-13) unless stopped early by ERCOT. Extensions of pilot may be considered during the first 6 months and would need ERCOT BOD approval.

## Slide 11: Other Info
Regular updates to be provided to ETWG and PDCWG during the Pilot Project.
It is expected that ERCOT will need to engage a contractor equivalent to .5 to 1 FTE for the duration of the Pilot Project.
The average cost for REGUP over the last 6 months has been about $9/MW and for REGDN has been about $6/MW. The estimated cost for 6 months of FRRS procurement from pilot resources is estimated to be about $3.4 Million.

## Slide 12: Potential benefits of FRRS
Promptly arrest frequency decay during unit trips.
Reduce the use of traditional regulation.
Reduce the quantity of Regulation capacity required to be procured.
Provide better frequency control at a lower overall cost.

## Slide 13: Questions?

## Slide 14: Appendix Additional Slides Presented Previously at WMS/ROS/ETWG/PDCWG

## Slide 15: Declining Inertial Frequency Response in ERCOT
http://www.ercot.com/content/gridinfo/etts/keydocs/System_Inertial_Frequency_Response_Estimation_and_Impact_of_.pdf

## Slide 16: ERCOT Frequency Profile Jan 2011 through Feb-2012

## Slide 18: Frequency Decay Slope

## Slide 19: FRRS-Up and FRRS-Down Deployment Logic
Deadband for FRRS trigger (±0.03 Hz)
Deployment period
Deployment period when frequency degrades further
Recalling
Maximum continuous deployment duration
Apply similar logic for Down-Regulation for high frequency
ERCOT may make additional parameter changes during pilot as needed
FRRS deployment signal logic will be shared with the pilot Resources

## Slide 20: FRRS Deployment logic and Parameters
During the FRRS pilot, some of the FRRS deployment parameters listed below are subject to change within the defined range
Initial trigger limit may be changed to ± 15 mHz
Initial FRRS MW deployment may be changed
Duration of FRRS deployment may be lowered from current 2 minutes duration for any single band deployment
FRRS deployments may be done proportionally over increments of 0.01 Hz or 0.005 Hz between 59.985 Hz and 59.95 Hz.

## Slide 21
Example: FRRS and PFR

## Slide 22
Example: FRRS Deployment Logic and Expected Impact
Deploy current Reg-Down
Recall Reg-Down and Deploy Reg-Up
Deploy FRRS-Up

## Slide 23
Simulation: Effect of FRRS on sudden large Frequency decay
FRRS-Up Full Deployment with 1 second delay after 59.91 Hz

## Slide 25: Scenario 1: Frequency below 59.97 Hz

## Slide 26: Scenario 2: Frequency below 59.95 Hz

## Slide 27: Scenario 3: Frequency below 59.91 Hz (on slow decline)

## Slide 28: Scenario 4: Frequency below 59.91 Hz (Unit trip)

## Slide 29
FRRS-Up Recall (Always based on duration or frequency)