## Slide 1: ERCOT Load Resources (LR)/ Responsive Reserve Service (RRS) Assessment
Jeff Billo
Manager, Transmission Planning
TAC
ERCOT
September 7, 2012
1

## Slide 2: Background
Frequency event in November 2010
  1436 MW tripped at two different generation plants
  LaaRs deployed and frequency recovered in approximately 5 minutes 10 seconds
The ERCOT BOD requested ERCOT perform an assessment of the Load Resources (LR) and Responsive Reserve Service (RRS)
  Currently amount of RRS provided by LRs capped at 50%
Several changes during the course of the study (requiring additional analysis):
  RRS increased from 2300 MW to 2800 MW
    Concurrent change to allow units to carry up to 24% of their capability for RRS (previously capped at 20%)
  Draft NERC BAL-003 standard may impose new frequency performance criteria
    Second ballot on new standard expected later this year
    FERC has imposed May 2013 deadline for completion of standard
ERCOT Public

## Slide 3: ERCOT Study
Primarily focused on worst-case scenario
  High wind, low load conditions (low system inertia)
Tested for two worst-case conditions:
  Frequency overshoot due to deploying of LRs for relatively small generation trip
  Low frequency for loss of two largest units (STP units 1 and 2)
Results:
  No reliability concerns with LRs providing up to 70% of RRS
  If not enough LRs procured, could lead to under frequency issue during times of low system inertia
ERCOT Public

## Slide 4: ERCOT Study Results (Indicative Sample)
ERCOT Public
60.5
59.5
60.0
70%LR
50%LR
30%LR
Overshoot test – loss of a single unit
Under frequency test – loss of a largest two units

## Slide 5: Stakeholder Comments
Results presented to ROS in June 2012
  ROS asked DWG and PDCWG to comment
DWG comments resulted in additional sensitivity analysis performed by ERCOT
PDCWG comments focused on limitations of existing stability models
  Mechanical characteristics of boiler system not fully represented in stability models
ROS took no action at August 2012 meeting
ERCOT Public

## Slide 6: Next Steps
Study supports increasing the amount of RRS provided by LRs (currently capped at 50%)
  Would require NPRR
ERCOT investigating solutions if low LR participation during times of low system inertia
ERCOT Public

## Slide 7: Questions?
ERCOT Public