| NOGRR Number | 097 | NOGRR Title | New Section 8I, Black Start Resource Availability Test Form |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Approved |
| Date of Decision | September 7, 2012 |
| Effective Date | October 1, 2012 |
| Priority and Rank Assigned | Not applicable |
| Nodal Operating Guide Section Requiring Revision | 8, Attachment I, Black Start Resource Availability Test Form (new) |
| Protocol Section(s) Requiring Revision | None. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds a Black Start Resource availability test form to the Nodal Operating Guides. |
| Reason for Revision | Paragraph (7) of Protocol Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing, requires Qualified Scheduling Entities (QSEs) who represent Black Start Resources to complete an ERCOT-provided report form for Black Start Resource availability tests. This NOGRR adds the form to the Nodal Operating Guides. |
| Procedural History | On 5/25/12 NOGRR097 and the associated Impact Analysis were posted. On 5/30/12, Luminant Energy Company, LLC comments were posted. On 6/13/12, the Operations Working Group (OWG) considered NOGRR097. On 7/18/12, the OWG considered the 6/13/12 OWG Report and Impact Analysis for NOGRR097. On 8/16/12, ROS considered NOGRR097. On 9/7/12, TAC considered NOGRR097. |
| OWG Decision | On 6/13/12, the OWG was in consensus to recommend approval of NOGRR097 as amended by the 5/30/12 Luminant Energy Company, LLC comments and as revised by OWG. On 7/18/12, the OWG was in consensus to endorse and forward the 6/13/12 OWG Report as revised by OWG and the Impact Analysis for NOGRR097 to ROS. |
| Summary of OWG Discussion | On 6/13/12, ERCOT Staff stated that the actual start time of the test should be included in the form. On 7/18/12, language changes were proposed to clarify that the form should be provided to ERCOT on a quarterly basis in accordance with Protocol Section 8.1.1.2.1.5. |
| ROS Decision | On 8/16/12, ROS unanimously voted to recommend approval of NOGRR097 as recommended by OWG in the 7/18/12 OWG Report. All Market Segments were present for the vote. |
| Summary of ROS Discussion | On 8/16/12, there was no discussion. |
| TAC Decision | On 9/7/12, TAC unanimously voted to approve NOGRR097 as recommended by ROS in the 8/16/12 ROS Report and as revised by TAC. All Market Segments were present for the vote. |
| Summary of TAC Discussion | On 9/7/12, administrative changes were proposed. |

| Business Case |
| --- |
| Business Case | 1 | Provides a standard form for ERCOT and Market Participants to use during testing of Black Start Resources. |

| Sponsor |
| --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6531 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |
| --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |
| --- |
| Comment Author | Comment Summary |
| Luminant Energy Company, LLC 053012 | Proposed language changes to simplify the form. |

Proposed Guide Language Revision

ERCOT Nodal Operating Guides

Section 8

Attachment I

Black Start Resource Availability Test Form

Month Day, Year

# Black Start Resource Availability Test Form

As required by Protocol Section 8.1.1.2.1.5, System Black Start Capability and Testing, Black Start Resources shall complete and provide this form to ERCOT on a quarterly basis.

Name of Black Start Resource: ___________________________________________________________

Check method to satisfy quarterly Black Start Resource Availability Test:

Black Start Test – Complete Part A

Successful Start and Normal Operation – Complete Part B

PART A – Black Start Test

Date of Test: __________________________

Time ERCOT Notified the Qualified Scheduling Entity (QSE) of testing:__________________________

Actual Start Time: ___	______________________

Time Black Start Resource reached the Low Sustained Limit (LSL):_____________________________

Black Start Resource LSL per the Current Operating Plan (COP): ___________________________

Did the Black Start Resource operate at or above its LSL for at least four consecutive Settlement Intervals? ________

Time and Date test was completed (breaker open): ___________________________________________

PART B – Successful Start and Normal Operation

Date of Successful Start: _______________________________________

Time Black Start Resource reached the LSL: ________________________________________________

Black Start Resource LSL per the current COP: ___________________________

Did the Black Start Resource operate at or above its LSL for at least four consecutive Settlement Intervals? ________

Was this run time due to an Energy Emergency Alert (EEA) or Normal Operation? __________________

REQUIRED SIGNATURES

QSE Representative Name / Signature: _________________________ / __________________________

Date ___________________________

If a Black Start Availability Test was performed:

ERCOT Operator Name / Signature: ___________________________ / __________________________

Date ___________________________