## Slide 1: DCS Events & Analysis
PDCWG
David Kee, Chair
Sydney Niemeyer, Vice Chair
9-13-2012

## Slide 2: Event Analysis
7-10-12@2046 – DCS event
  Passed DCS standard
  LRs deployed
  Failed ERCOT response metric (squelched)
    Delivered 357MW/0.1Hz from ERCOT system
    Metric is minimum of 420MW/0.1Hz PFR
  2 Resources identified with issues
    ERCOT is engaged
  Responsive was carried on nonresponsive power augmentation
  Power Augmentation which did deploy showed delays in deployment
High Risk Scenario: IF the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard

## Slide 3: Event Analysis
7-30-12@1603 – DCS event
  Passed DCS standard
  Load Resources deployed
  Failed ERCOT response metric (squelch)
    Delivered 500MW/0.1Hz from ERCOT system at B-point
    Delivered 387MW/0.1Hz from ERCOT system at B+30
    Metric is minimum of 420MW/0.1Hz PFR
  LR deployment contributed to the initial frequency response
  No Resources identified with issues
  Top reason for poor performance
    36 of 70 No spinning (at HSL and possibly on duct burners)
    12 of 70 Capacity (including Responsive Reserve) on Non-frequency responsive equipment
  Responsive was carried on nonresponsive power augmentation
LR response provided initial PFR.
High Risk Scenario: IF the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard

## Slide 4: Event Analysis Recommendation
Issue: HSL inaccuracies can cause regulation deployment bias resulting in less available regulation for frequency deviations
Recommendation: ERCOT can add a regulation bias to the generation to be dispatched value. This will result in SCED actively dispatching units to reclaim regulation deployed.
Issue: Growing trend of carrying RRS on nonresponsive generators
Recommendation: ERCOT compliance to continue to follow up with generation resources that continually (2 events or more) carry Responsive Reserves on capacity that is not frequency responsive

## Slide 5: Event Analysis Recommendations
Issue: Members note protocols need clarification
Recommendations (did not reach a consensus):
  Modify protocols to require:
  Telemetry describing frequency responsive capacity. Intent is to allow more visibility into what capacity the resource has that will respond to frequency deviations.
  Responsive reserve capacity shall be frequency responsive for the entire RRS obligation. Intent is to have the RRS capacity be able to respond to frequency deviations via PFR.
  Separate the obligation methodology from the performance requirement by qualifying the 10 minute requirement. Intention is to remove the excuse of RRS having a 10 minute requirement.
All need more review.