## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: September 5th meeting
18 attendees representing 11 companies, ERCOT & TRE
BAL-001-TRE Field trial results
Regulation deployment analysis
RRS on Combined Cycle Steam Turbines and Power Augmentation
Impact of HSL errors
Draft NOGRR for PFR testing
Control performance metrics & GREDP
Event analysis – DCS 07-30-12
Next meeting Oct. 3

## Slide 3: BAL-001-TRE Field trial results
Results communicated to participants via conference call
Retooled evaluation spreadsheet and delivered (will deliver) to participants
Next steps to update all documentation and possibly resubmit for ballot.

## Slide 4: RRS on Steam Turbines & Duct Burners
Issue: Can Steam Turbines from Combined Cycles carry RRS capacity?
Group agreed that if Combined Cycles set the droop on the Combustion Turbines associated with a single Steam Turbine in a combined cycle train to 4%, the corresponding frequency response of the combined cycle train will meet all requirements. This allows RRS to be carried on Steam Turbines associated with combined cycles.
Recommendation: No market rule changes are needed. QSE/RE will need to update control system settings. ERCOT compliance & PDCWG will evaluate performance of Combined Cycles to events.
It should be noted that the group did agree that RRS capacity should not be carried on power augmentation that is not frequency responsive.

## Slide 5: Impact of HSL errors
Issue: HSL not being achieved on resources causing regulation to be biased high on peak and low off peak.
  Review of issue shows that overall deviation values are near 2% (some outliers).
  Reliability impact if regulation is consistently deployed over peak, effective regulation available is less than AS methodology requires.
  It was noted that in under Zonal market, this issue was corrected by QSE control systems.
  ERCOT control system should account for real time errors similarly.
Recommendations:
  Add regulation bias to Generation To Be Dispatched (GTBD) value.
  Create SCE-like (Zonal) control methodology for issuing basepoints.

## Slide 6: System Oscillations
PDCWG member noted oscillations on 8/13/12 near 1130.
  Opinion that this may be a sign of import limit for Houston.
PDCWG member noted oscillations on 8/23 & 8/24.
  Wind dispatch (SCED) oscillation was noted and effected generation in other zones.
  ERCOT operations will research.

## Slide 7: NOGRRs
NOGRR096 has potential to reduce PFR from online generation below 1150MW.
ERCOT to evaluate AS methodology to find what safeguards exist to keep minimum PFR at 1150MW from online generation.
Draft NOGRR for PFR testing
Reviewed and completed conventional forms.
Need to work on CLR & ACLR requirements.

## Slide 8: Metrics Review CPS1, CPS2, RMS, etc.
Performance is still good.
Periods of load ramping improved
  Attributed to the STARTUP/SHUTDOWN status changes
  Status changes are not perfect but a step in the right direction

## Slide 9: Event Analysis
7-10-12@2046 – DCS event
  Passed DCS standard
  LRs deployed
  Failed ERCOT response metric (squelched)
    Delivered 357MW/0.1Hz from ERCOT system
    Metric is minimum of 420MW/0.1Hz PFR
  2 Resources identified with issues
    ERCOT is engaged
  Responsive was carried on nonresponsive power augmentation
  Power Augmentation which did deploy showed delays in deployment
High Risk Scenario: IF the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard

## Slide 10: Event Analysis
7-30-12@1603 – DCS event
  Passed DCS standard
  Load Resources deployed
  Failed ERCOT response metric (squelch)
    Delivered 500MW/0.1Hz from ERCOT system at B-point
    Delivered 387MW/0.1Hz from ERCOT system at B+30
    Metric is minimum of 420MW/0.1Hz PFR
  LR deployment contributed to the initial frequency response
  No Resources identified with issues
  Top reason for poor performance
    36 of 70 No spinning (at HSL and possibly on duct burners)
    12 of 70 Capacity (including Responsive Reserve) on Non-frequency responsive equipment
  Responsive was carried on nonresponsive power augmentation
LR response provided initial PFR.
High Risk Scenario: IF the ERCOT system has exhausted all available capacity and depended only on PFR and the subsequent energy deployed from RRS providers, ERCOT would fail the DCS standard

## Slide 11: Event Analysis Recommendation
Issue: HSL inaccuracies can cause regulation deployment bias resulting in less available regulation for frequency deviations
Recommendation: ERCOT can add a regulation bias to the generation to be dispatched value. This will result in SCED actively dispatching units to reclaim regulation deployed.
Issue: Growing trend of carrying RRS on nonresponsive generators
Recommendation: ERCOT compliance to continue to follow up with generation resources that continually (2 events or more) carry Responsive Reserves on capacity that is not frequency responsive

## Slide 12: Event Analysis Recommendations
Issue: Members note protocols need clarification
Recommendations (did not reach a consensus):
  Modify protocols to require:
  Telemetry describing frequency responsive capacity. Intent is to allow more visibility into what capacity the resource has that will respond to frequency deviations.
  Responsive reserve capacity shall be frequency responsive for the entire RRS obligation. Intent is to have the RRS capacity be able to respond to frequency deviations via PFR.
  Separate the obligation methodology from the performance requirement by qualifying the 10 minute requirement. Intention is to remove the excuse of RRS having a 10 minute requirement.
All need more review.

## Slide 13
Questions?