ERCOT Operations Report

August 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 8/1/2012 11:24 | 59.833 | 120 | Unit trip with 775 MW net online. |
| 8/7/2012 20:30 | 59.832 | 41 | Unit trip with 739 MW net online. |
| 8/18/2012 22:54 | 59.898 | 4 | Unit trip with 478 MW net online. |
| 8/24/2012 15:30 | 59.812 | 96 | Unit trip with 805 MW net online. |
| 8/24/2012 16:04 | 59.853 | 100 | Multiple unit trips with 473 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration (s) | Summary |
| --- | --- | --- | --- |
| 8/13/2012 22:30:00 | Local oscillation | Approx. 3 min | The oscillation was observed in the Houston area but it was only detected in PI data as there is no PMU installed in that area. The cause of the oscillation has not been determined yet. The RFI has been sent to the TSP for more information. |
| 08/15/2012 11:50:00 | Local oscillation | Approx. 1 hr. | The oscillating frequency of approx. 1.8 Hz was observed at one station in the West Texas. ERCOT was informed that the oscillation was due to some control circuit with calibration variances issue. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 8/1/12 11:24:48 | 8/1/12 11:28:31 | 0:03:43 | 289.95 |  |
| 8/7/12 20:30:06 | 8/7/12 20:33:46 | 0:03:40 | 515.09 |  |
| 8/24/12 15:30:42 | 8/24/12 15:33:18 | 0:02:36 | 484.71 |  |
| 8/26/12 6:29:42 | 8/26/12 6:31:14 | 0:01:32 | 40.41 | Unit Trip with 403 MW net online. |

RUC Commitments

None

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Moss Switch - Holt Switch & Amoco North Cowden 138 kV | Odessa North Axfmr1 138/69 kV | 29 | Y |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 14 | N |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 12 | N |
| Moss Switch - Holt Switch & Amoco North Cowden 138 kV | Odessa North - Odessa Basin Switch 69 kV | 10 | Y |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - BTU_Jack_Creek 345 kV | 8 | N |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4L (3) 345/138 kV | 8 | N |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 7 | N |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | San Diego - Freer 69 kV | 6 | N |
| DCKT Allen Switch - Royse Switch and Monticello SES 345 kV | Centerville Road Switch Axfmr1l (3) 345/138 kV | 6 | N |
| Paloduro Sub - Batesville Switching Station 138 kV | Moore Switching Station - Downie Switching Station 138 kV | 6 | N |
| DCKT Centerville Road Switch - Lake Hubbard SES - Centerville Road 138 kV | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 5 | N |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 5 | N |
| Midland East - Moss Switch 345 kV | Odessa - Odessa North 138 kV | 4 | N |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 4 | N |
| Kyle - San Marcos 138 kV | Turnersville - Buda 138 kV | 4 | N |
| Midland East - Moss Switch 345 kV | Edwards Tap - Judkins 138 kV | 3 | N |
| Dilley Switch AEP - North Laredo Switch and San Miguel 69 kV Switchyard 138 kV | Pearsall Switching Station - Paloduro Sub 138 kV | 3 | N |
| DCKT STP Units 1 & 2 | Columbia - Stafford 69 kV | 3 | N |
| Bracketville - Asphalt Mines 138 kV | Hamilton Road - Maverick 138 kV | 3 | N |
| Lewisville Switch - Carrollton Northwest 345 kV (105_A) | Highlands TNP - West TNP 138 kV | 3 | N |
| DCKT Skyline - Calaveras 345 kV | Cagnon Axfmr3L (3) 345/138 kV | 3 | N |
| Mountain Creek SES - Cedar Crest Switch 138kV | Mountain Creek SES - Trinity River Authority 138 kV | 3 | N |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 3 | N |
| DCKT Marion - Zorn and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 3 | N |
| Salem Lcra At3 345/138 kV | Fayetteville 26At2 345/138 kV | 3 | N |
| DCKT Centerville Road Switch - Parkdale Switch 138 kV | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 2 |  |
| Bosque Switch - Elm Mott 345 kV | Bosque Switch - Rogers Hill BEPC 138 kV | 2 |  |
| DCKT Salado Switch - Hutto Switch 345kV | Sandow Switch - Bell County East Switch 345 kV (431) | 2 |  |
| West Batesville - Uvalde AEP 138 kV | Moore Switching Station - Downie Switching Station 138 kV | 2 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Kennedy Switch 138kV | 2 |  |
| DCKT Olinger - Firewheel and Elmgrove 138 kV | Olinger - Ben Davis 138 kV | 2 |  |
| Lewisville Switch - Carrollton Northwest 345 kV | Euless - Grapevine Highway 360 138 kV | 2 |  |
| Big Wells - Dilley Switch AEP 138 kV | West Batesville - Asherton 138kV | 2 |  |
| Bracketville - Odlaw Switchyard & Hamilton Road 138 kV | Hamilton Maverick 138kV | 2 |  |
| DCKT Cagnon - Medinabs and Tcc and Pinn_Rd and Westside 138 kV | Five_Pts - Westside 138 kV | 2 |  |
| Midland East - Moss Switch 345 kV | Odessa EHV Switch - Big Three Odessa Tap 138 kV | 1 |  |
| Midland East - Moss Switch 345 kV | General Tire Switch - Southwestern Portland Tap 138 kV | 1 |  |
| DCKT Allen Switch - Royse Switch and Monticello SES 345 kV | Ben Davis - Parker Maxwell Creek 138 kV | 1 |  |
| Dilley Switch AEP - North Laredo Switch and San Miguel 69 kV Switchyard 138 kV | Pleasanton - Jourdanton 69 kV | 1 |  |
| DCKT STP Units 1 & 2 | Lolita - Blessing 138kV | 1 |  |
| DCKT Centerville Road Switch - Parkdale Switch 138 kV | Prairie Creek - Parkdale Switch 138 kV | 1 |  |
| Bosque Switch - Elm Mott 345 kV | Rogers Hill BEPC - Elm Mott 138 kV | 1 |  |
| DCKT Eagle Mountain SES - Alliance - Roanoke Switch - Parker Switch 345 kV | Morris Dido - Rosen Heights Tap 2 138 kV | 1 |  |
| DCKT Eagle Mountain SES - Alliance - Roanoke Switch - Parker Switch 345 kV | Eagle Mountain SES - Eagle Mountain Poi 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | North Laredo Switch Pst1 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 1 |  |
| DCKT Navarro - Big Brown SES And Venus Switch 345 kV | Richland Chambers - Trinidad SES 345 kV (31) | 1 |  |
| DCKT Navarro - Big Brown SES And Venus Switch 345 kV | Richland Chambers - Trinidad SES 345 kV (21) | 1 |  |
| Power Plant Substation - Price Road Substation 138 kV | Power Plant Substation T1 138/69 kV | 1 |  |
| Gonzales - Luling 138 kV | Flatonia - Hallettsville GVEC 138kV | 1 |  |
| Manchaca - Buda 138 kV | Buda - Rutherford 138 kV | 1 |  |
| Trinidad SES - Watermill Switch And Tri Corner 345 kV | Trinidad SES Axfmr6 (3) 345/138 kV | 1 |  |
| DCKT Everman Switch - Handley SES 138 kV | Handley SES - Ayers 138 kV | 1 |  |
| DCKT Lytton Spring - Zorn and Austrop 345 kV | Turnersville - Buda 138 kV | 1 |  |
| DCKT Calmont Switch - Benbrook Switch 138 kV | Saginaw Switch - American Mfg Tap 138 kV | 1 |  |
| DCKT Navarro - Limestone Plant And Watermill Switch 345 kV | Richland Chambers - Trinidad SES 345 kV (31) | 1 |  |
| Waco Lasalle - Waco East And Lake Creek SES 138kV | Lake Creek SES - Robinson 138kV | 1 |  |
| Caney Creek - Wharton & East Bernard & Dyann 138kV | Pledger - West Columbia 138 kV | 1 |  |
| San Angelo Paulann - San Angelo Red Creek & San Angelo North 138kV | San Angelo Red Creek - San Angelo Coke Street 138kV | 1 |  |
| Salt Creek BEPC - Spur And Scurry Switch 138kV | Spur 138_69_1 138/69 kV | 1 |  |
| Kiamichi Energy Facility - Kiowa Switch 345 kV (Kmchi_Kwass1) | Kiamichi Energy Facility - Kiowa Switch 345kV (Kmchi_Kwass2) | 1 |  |
| Midkiff Switch Axfmr1 138/69 kV | Hackberry Draw Tap - Permian Basin SES 138 kV | 1 |  |
| Ajo - Rio Hondo 345 kV | North Edinburg Nedin_Xc2 345 kV | 1 |  |
| Midkiff Switch - Spraberry Switch 138 kV | Garden City - Glasscock (ONCOR) 69 kV | 1 |  |
| Cisco - Putnam 138kV & Leon Switch 138kV | Putnam 138kV - Leon Switch 138 kV | 1 |  |
| DCKT Gabriel - Bell County and Hutto Switch 138 kV | Hutto Switch - Round Rock Northeast 138 kV (1661_B) | 1 |  |
| Forest Hill Switch Axfmr1 138/69 kV | Handley SES - Duval 69 kV | 1 |  |
| Bellville South 54at2 138/69 kV | Glidden Lcra 53At1 138/69 kV | 1 |  |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Fayetteville 26At2 345/138 kV | 1 |  |
| Comanche Switch (ONCOR) - Comanche Peak SES 345kV | Comanche Switch (ONCOR) - Comanche Tap 138 kV | 1 |  |
| Zorn - Hays Energy 345 kV | Kendall 4LH 345/138 kV | 1 |  |
| Oxychem Ingleside - Ingleside Cogen Switch 138 kV (Inglco_Oxy_In1) | Dupont Switch Ingleside - Dupont PP1 Ingleside 138 kV (I_Dupp_I_Dups1) | 1 |  |
| La Palma - Rio Hondo 138 kV | Harlingen Switch - Oleander 138kV | 1 |  |
| Moss Switch Axfmr1h_H (3) 345/138kV | Odessa - Odessa North 138 kV | 1 |  |
| Kiamichi Energy Facility - Kiowa Switch 345 kV (Kmchi_Kwass2) | Kiamichi Energy Facility - Kiowa Switch 345 kV (Kmchi_Kwass1) | 1 |  |
| Westover (ONCOR) - Amoco South Foster 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which made our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 3 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

08/09 DCKT Centerville Road Switch– Lake Hubbard SES 138kV RAP

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 08/29/2012 | Transmission and Security Desk V1 Rev19 | 610 |
| 08/29/2012 | Shift Supervisor Desk V1 Rev17 | 609 |
| 08/29/2012 | Resource Desk V1 Rev19 | 608 |
| 08/29/2012 | Real Time Desk V1 Rev20 | 607 |
| 08/29/2012 | DC Tie Desk V1 Rev16 | 606 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

08/01 17:00 66,489 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | 2.85 |
| August | 3.07 | 2.29 | 2.28 | 2.96 |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.93 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 8/1/2012 | 12:45 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 15:00 - 19:00 |

Transmission Watch

8/27 14:00	ERCOT issued a Transmission Watch for the Rio Grande Valley area due to forced outages.  The Stewart Road to Weslaco 138kV and Rio Hondo to La Palma 345kV lines were forced out.  An export schedule of 150 MW across the Railroad DC-Tie was curtailed.

8/30 17:05 	ERCOT issued a Transmission Watch for the Laredo area due to the post- contingency loss of Lobo to San Miguel 345kV.  An export schedule across the Laredo VFT of 40 MW was curtailed.

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None