## Slide 1: Operating Guide and Planning Guide Revision Requests
Blake Williams, ROS Chair
September 13, 2012

## Slide 2: Agenda
Credible Single Contingency
Operations Studies/Analyses
Operations Contingencies
Operations Reliability Criteria
Redundant Security Criteria
Outage Coordination Requirements
TSP Provision of Contingencies
Directives

## Slide 3: “Credible Single Contingency”
Credible Single Contingency for Transmission Planning
(1) A single facility, comprised of transmission line, auto transformer, or other associated pieces of equipment. This includes multiple equipment Outaged or interrupted during a single fault (SFME).
Credible Single Contingency for Operations Planning
(1) A single facility, comprised of transmission line, auto transformer, or other associated pieces of equipment. This includes multiple equipment Outaged or interrupted during a single fault (single fault multiple element (SFME)).

## Slide 4: “Credible Single Contingency”
Credible Single Contingency for Transmission Planning
(2) The Forced Outage of a DCKT in excess of 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal.
Credible Single Contingency for Operations Planning
(2) The Forced Outage of a double-circuit transmission line (DCKT) in excess of 0.5 miles in length will always be considered a credible single contingency for all security constrained unit commitment decisions. The Forced Outage of a DCKT in excess of 0.5 miles in length will only be considered a credible single contingency for energy deployment decisions for any of the following operating conditions characterized by high DCKT Outage probability or consequence:
  High Outage Probability:
  High Outage Consequence:

## Slide 5: “Credible Single Contingency”
Credible Single Contingency for Transmission Planning
(3) Any Generation Resource:
  (a) A combined-cycle facility shall be considered a single Generation Resource; or
  (b) Each unit of a combined-cycle facility will be considered a single Generation Resource if the combustion turbine and the steam turbine can operate separately, as stated in the Resource registration on the Market Information System (MIS) Public Area.
Credible Single Contingency for Operations Planning
(3) Any Generation Resource:
  (a) A combined-cycle facility shall be considered a single Generation Resource; or
  (b) Each unit of a combined-cycle facility will be considered a single Generation Resource if the combustion turbine and the steam turbine can operate separately, as stated in the Resource registration on the Market Information System (MIS) Public Area.

## Slide 6: “Credible Single Contingency”
Credible Single Contingency for Transmission Planning
(4) With any single Generation Resource unavailable, and with any other generation preemptively redispatched, the contingency loss of a single Transmission Facility (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal.
Credible Single Contingency for Operations Planning
(4) With any single Generation Resource unavailable, and with any other generation preemptively redispatched, the contingency loss of a single Transmission Facility (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause the following:
  (a) Cascading or uncontrolled Outages;
  (b) Instability of Generation Resources at multiple plant locations; or
  (c) Interruption of service to firm demand or generation other than that isolated by the transmission facility, following the execution of all automatic operating actions such as relaying and Special Protection Systems (SPSs).
Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., RAPs) such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

## Slide 7: “Credible Single Contingency”
Transmission Facilities
(1) Power lines, substations, and associated facilities, operated at 60 kV or above, including radial lines operated at or above 60 kV;
(2) Substation facilities on the high voltage side of the transformer, in a substation where power is transformed from a voltage higher than 60 kV to a voltage lower than 60 kV (DISTRIBUTION SUBSTATION) or is transformed from a voltage lower than 60 kV to a voltage higher than 60 Kv (GENERATION SWITCHYARD); and
(3) The direct current interconnections between ERCOT and the Southwest Power Pool or Comision Federal de Electricidad (CFE).

## Slide 8: “Credible Single Contingency”
Credible Single Contingency for Transmission Planning
(5) Single contingency conditions defined in North American Electric Reliability Corporation (NERC) Reliability Standards and any subsequent revisions.

## Slide 9: Operations Studies/Analyses
operational ERCOT Transmission Grid reliability studies
load flows and security analyses
reliability planning
contingency analyses
planning and engineering studies
Day-Ahead studies
Real-Time security analyses
sound engineering studies
Real-Time and short term planning

## Slide 10: Operations Contingencies
Credible Single Contingency
first contingency conditions
“Contingency” (N-1) conditions

## Slide 11: Operations Reliability Criteria
as needed to maintain reliability
credible N-1 criteria
N-1 criteria
maintain reliable operations
post-contingency voltages within post contingency limits
“First Contingency” (N-1) transfer limits
severely overloaded
significant impact on the reliability
“First Contingency” (N-1) Criteria
security criteria established in the Protocols and these Operating Guides

## Slide 12: Redundant Security Criteria
2.2.2 Security Criteria
(1) Technical limits established for the operation of transmission equipment shall be applied consistently in planning and engineering studies, Congestion Revenue Rights (CRRs), Day-Ahead studies, Real-Time security analyses, and operator actions.
(2) Unless an Emergency Condition has been declared by ERCOT, the ERCOT System shall be operated in such a manner that the occurrence of a Credible Single Contingency will not cause any of the following conditions:
  (a) Uncontrolled breakup of the ERCOT Transmission Grid;
  (b) Loading of Transmission Facilities above defined Emergency Ratings that cannot be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;
  (c) Transmission voltage levels outside system design limits that cannot be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or
  Customer Outages, except for high set interruptible and radially served loads.
4.3 Operation to Maintain Transmission System Security
(1) ERCOT Operators are responsible for operating the ERCOT System within “First Contingency” (N-1) transfer limits so that there is no overload of any significant Transmission Element whose loss could jeopardize the reliability of the ERCOT System. Whenever the ERCOT System is not engaged in emergency operation, it will be operated in such a manner that the occurrence of a Credible Single Contingency will not cause any of the following:
  (a) Uncontrolled breakup of the transmission system;
  (b) Loading of Transmission Facilities above defined Emergency Ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;
  (c) Transmission voltage levels outside system design limits which can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or
  (d) Customer Outages, except for high set interruptible and radially served loads.

## Slide 13: Outage Coordination Requirements
2.4 Outage Coordination
For Outage coordination details, reference Protocol Section 3.1, Outage Coordination and the ERCOT Market Information System (MIS) Secure Area.

## Slide 14: TSP Provision of Contingencies
5 Network Operations Modeling Requirements
5.1 System Modeling Information
Information on existing and future ERCOT System components and topology is necessary for ERCOT to create databases and perform tests as outlined in these criteria. To ensure that such information is made available to ERCOT, the following actions by Market Participants are required:

## Slide 15: ROS Chair Directive to PLWG
Continue efforts to reformat the Transmission Planning Criteria in Section 4 of the Planning Guide:
Credible Single Contingency
  Eliminate the use of Credible Single Contingency for Transmission Planning by explicitly stating system conditions, contingencies and performance requirements in the Planning Guide; or
  Modify the definition to accurately state the contingencies. Consider renaming the defined term from Credible Single Contingency… to Planning Contingencies.
Structure the criteria such that it is clearly understood and can easily be modified to incorporate ROS-directed OPSTF Issues.
Only substantive changes to reflect current practices should be included.

## Slide 16: ROS Chair Directive to NDSWG
Work with ERCOT and OWG to revise the Nodal Operating Guides:
Modify the definition of Credible Single Contingency for Operations Planning to accurately state the contingencies. Consider changing the defined term from Credible Single Contingency… to Credible Contingencies… or Operations Contingencies.
Explicitly state applicable operations studies or analyses. Consider use of defined terms. Also consider revising applicable sections of the Nodal Protocols for consistency.
Explicitly state applicable operations contingencies or use newly defined Credible Single Contingency term. Also consider revising applicable sections of the Nodal Protocols for consistency.
Explicitly state applicable reliability criteria or reference Section 2.2.2 – Security Criteria. Also consider revising applicable sections of the Nodal Protocols for consistency.
Consider removing the redundantly stated security criteria in Section 4.3 – Operation to Maintain Transmission System Security.
Consider expansion of Section 2.4 – Outage Coordination to provide guidance/requirements for outage studies.
Consider addition of requirements for TSP provision of contingencies in Section 5.1 – System Modeling Information.
Only substantive changes to reflect current practices should be included.