| PGRR Number |  | PGRR Title | Clarify Planning Assumptions and Performance Criteria |
| --- | --- | --- | --- |
| Date Posted |  |  |  |

| Requested Resolution (Normal or Urgent, and justification for Urgent status) | Normal |
| --- | --- |
| Planning Guide Section(s) Requiring Revision (Include Section No. and Title) | 2.1 Definitions 4.1 Introduction 4.1.1.1 Planning Assumptions 4.1.1.2 Reliability Performance Criteria |
| Protocol Section(s) Requiring Revision (If applicable) | None. |
| Revision Description | This Planning Guide Revision Request (PGRR) clarifies assumptions allowed for planning studies and planning performance criteria. The revised language will also better reflect current planning practices. |
| Reason for Revision | The current planning criteria in the Planning Guide are unclear and, in some cases, in conflict with the intention of the performance objective. |

Business Case

Business Case instructions:  To allow for comprehensive PGRR consideration, please fill out the Business Case section below and provide as much detailed information as possible.  Wherever possible, please include reasons, explanations, and cost benefit calculation pertaining to the PGRR.  Insert additional rows as needed.

| Business Case | 1 | This PGRR will add clarity for ERCOT and TSP planners. |
| --- | --- | --- |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
|  | 5 |  |

| Sponsor |  |
| --- | --- |
| Name | Jeff Billo on behalf of the PLWG |
| E-mail Address | jbillo@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248- 6334 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Guide Language Revision

## DEFINITIONS

Relevant terms and definitions used in the Planning Guide can be found in Protocol Section 2, Definitions and Acronyms.  The terms within this Section 2.1 contains terms not defined in Protocols.

C

[Back to Top]

4.1	Introduction

(1)	ERCOT employs both reliability criteria and economic criteria in evaluating the need for transmission system improvements.  The economic criteria are included in Protocol Section 3.11.2, Planning Criteria.  This Planning Guide provides the reliability criteria.

(2)	The ERCOT System consists of those generation and Transmission Facilities (60 kV and higher voltages) that are controlled by individual Market Participants and that function as part of an integrated and coordinated system.

(3)	To maintain reliable operation of the ERCOT System, stakeholders are required to observe and subscribe to certain minimum planning criteria.  The criteria set forth herein, combined with the applicable North American Electric Reliability Corporation (NERC) Reliability Standards, constitute the aforementioned minimum planning criteria.  Planning studies outlined herein shall be performed to determine conformance to these minimum criteria; however, ERCOT recognizes that events more severe than those outlined in these criteria could cause grid separation and other tests may also be performed.

(4)	The complexity and uncertainty inherent in the planning and operation of the ERCOT System make exhaustive studies impracticable; therefore, to gain maximum benefit from the limited number of tests performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

(5)	ERCOT will perform steady-state and dynamic analysis appropriate to ensure the reliability of the ERCOT System and implement appropriate solutions.

(6)	Each Transmission Service Provider (TSP) will perform steady-state, short circuit, and dynamic analysis appropriate to ensure the reliability of their portion of the ERCOT System and implement appropriate solutions.

(7)	The base cases created by the Steady-State Working Group (SSWG), System Protection Working Group (SPWG), Dynamics Working Group (DWG), and ERCOT are available for use by Market Participants.

(8)	If a TSP has its own planning criteria in addition to those defined in this Planning Guide, the TSP shall provide documentation of those criteria to ERCOT.  ERCOT shall post the documentation on the Planning and Operations Information website.  The TSP shall notify ERCOT of any changes to their planning criteria and provide revised documentation within 30 days of such change.

4.1.1.1	Planning Assumptions

The following assumptions may be used in planning studies:

(a)	Reasonable variations of load forecast.

(b)	Reasonable variations of generation commitment and dispatch applicable to transmission planning analyses on a case-by-case basis may include, but are not limited to, the following methods:

(i)	Production cost model simulation, security constrained optimal power flow, or similar modeling tools that analyze the ERCOT System using hourly generation dispatch assumptions;

(ii)	Modeling of high intermittent generation conditions; or

(iii)	Modeling of low or no intermittent generation conditions.

4.1.1.2	Reliability Performance Requirements

The following performance criteria shall be applicable to planning studies.  ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this section, but the improvement cannot be implemented in time to resolve the performance deficiency, a Remedial Action Plan (RAP) or Special Protection System (SPS) may be used to temporarily resolve the deficiency until the improvement has been implemented.

- With all facilities in their normal state (no contingency), facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding and there shall be no non-consequential load loss;

- With all other facilities in their normal state, after the loss (with or without a three-phase fault with normal clearing) of a single generator, transmission line circuit, transformer, shunt device, FACTS device, or double circuit transmission line (two circuits sharing a tower for 0.5 miles or greater), all facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss;

- With all other facilities in their normal state, after the loss of a bus section due to a single-line-to-ground fault or an internal breaker fault, all facilities shall be within their applicable ratings and the system shall be stable with no cascading or uncontrolled islanding. A Mitigation Plan with non-consequential load loss (MP) or RAP may be planned on a permanent basis to resolve a performance deficiency under this condition;

- With any single generating unit unavailable, including an entire combined cycle train if no part of the train cannot operate with one of the units offline per the Resource Asset Registration Form, followed by Manual System Adjustments, after the loss (with or without a three-phase fault with normal clearing) of a single generator, transmission line circuit, transformer, shunt device, FACTS device, or double circuit transmission line (two circuits sharing a tower for 0.5 miles or greater) all facilities shall be within their applicable ratings, the system shall be stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss. A RAP may be planned on a permanent basis to resolve a performance deficiency under this condition;

- With all other facilities in their normal state, the loss of elements as a consequence of a stuck breaker attempting to clear a fault on single generator, transmission line circuit, transformer, shunt device, FACTS device, internal breaker, or bus section, all facilities shall be within their applicable ratings and the system shall be stable with no cascading or uncontrolled islanding. A MP or RAP may be planned on a permanent basis to resolve a performance deficiency under this condition;

- With any single transformer, transmission line circuit, shunt device or FACTS device unavailable, the loss (with or without a three-phase fault with normal clearing) of a single generator, transmission line circuit, transformer, shunt device, or FACTS device, all facilities shall be within their applicable ratings and the system shall be stable with no cascading or uncontrolled islanding. A MP or RAP may be planned on a permanent basis to resolve a performance deficiency under this condition.

Table 1 summarizes the above criteria.

| Initial Condition | Event | Fault Type | Facilities within Applicable Ratings and System Stable with No Cascading or Uncontrolled Outages | Planned RAP Allowed | Planned MP Allowed |
| --- | --- | --- | --- | --- | --- |
| Normal System | None | N/A | Yes | No | No |
| Normal System | Loss of one of the following: - Generator - Transmission Circuit - Transformer - Shunt Device - FACTS Device - Double Circuit Transmission Line (two circuits sharing a tower for 0.5 miles or greater) | 3Ø | Yes | No | No |
| Normal System | Bus Section Fault or Internal Breaker Fault | SLG | Yes | Yes | Yes |
| Loss of a generator unit followed by Manual System Adjustments | Loss of one of the following: - Generator - Transmission Circuit - Transformer - Shunt Device - FACTS Device - Double Circuit Transmission Line (two circuits sharing a tower for 0.5 miles or greater) | 3Ø | Yes | Yes | No |
| Normal System | Loss of elements as a consequence of a stuck breaker attempting to clear a fault on one of the following: - Generator - Transmission Circuit - Transformer - Shunt Device - FACTS Device - Internal breaker - Bus section | SLG | Yes | Yes | Yes |
| Loss of one of the following followed by Manual System Adjustments: - Transmission Circuit - Transformer - Shunt Device - FACTS Device | Loss of one of the following: - Generator - Transmission Circuit - Transformer - Shunt Device - FACTS Device | 3Ø | Yes | Yes | Yes |

Table 1: ERCOT Planning Reliability Performance Criteria