ERCOT Operations Report

September 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 9/4/2012 11:28 | 59.882 | 68 | Unit Trip with 676 MW net online. |
| 9/8/2012 23:12 | 59.895 | 16 | Gen Deviation of - 2000 MW in 10 min. |
| 9/11/2012 16:13 | 59.866 | 52 | Unit Trip with 555 MW net online. |
| 9/12/2012 23:11 | 59.899 | 16 | Gen Deviation of - 1000 MW in 3 min. |
| 9/14/2012 13:31 | 59.844 | 76 | Unit Trip with 785 MW net online. |
| 9/17/2012 10:29 | 59.815 | 48 | Unit Trip with 785 MW net online. |
| 9/21/2012 18:21 | 59.876 | 24 | Unit Trip with 584 MW net online. |
| 9/23/2012 19:26 | 59.872 | 125 | Unit Trip with 516 MW net online. |
| 9/27/2012 11:43 | 59.813 | 176 | Multiple Unit Trips with 484 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 09/26/2012 22:07 | Local oscillation | Approx. 30 min | The oscillating frequency of approx. 1.8 Hz was observed at one station in West Texas. It is still under investigation and is suspected that the oscillation might be due to similar control circuit issue which occurred in August. |
| 9/27/2012 07:35 | Local oscillation | Approx. 1.6 min | The oscillation was observed in the Houston area but it was only detected in PI data as there is no PMU installed in that area. The cause of the oscillation has not been determined yet. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 9/4/12 11:28:06 | 9/4/12 11:33:26 | 0:05:20 | 501.37 |  |
| 9/8/12 23:11:02 | 9/8/12 23:17:14 | 0:06:12 | 442.53 |  |
| 9/11/12 16:13:48 | 9/11/12 16:18:44 | 0:04:56 | 296.76 |  |
| 9/12/12 23:11:28 | 9/12/12 23:16:12 | 0:04:44 | 428.14 |  |
| 9/14/12 13:31:44 | 9/14/12 13:34:44 | 0:03:00 | 333.33 |  |
| 9/17/12 10:29:28 | 9/17/12 10:32:44 | 0:03:16 | 629.38 |  |
| 9/18/12 14:05:44 | 9/18/12 14:09:32 | 0:03:48 | 166.63 | Multiple Unit trips with 354 MW net online. |
| 9/21/12 18:21:16 | 9/21/12 18:25:08 | 0:03:52 | 353.25 |  |
| 9/23/12 19:26:08 | 9/23/12 19:31:08 | 0:05:00 | 249.16 |  |
| 9/27/12 7:38:36 | 9/27/12 7:42:20 | 0:03:44 | 403.83 | Multiple Unit trips with 511 MW net online. |
| 9/27/12 11:43:43 | 9/27/12 11:48:00 | 0:04:17 | 1032.7 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North Axfmr1 138/69 kV | 15 | N |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 11 | N |
| Meadow Sub - PH Robinson 345 kV | North Alvin TNP - Alvin TNP 138 kV | 10 | N |
| Salt Creek BEPC - Spur And Scurry Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 9 | N |
| Midland East - Moss Switch 345 kV | General Tire Switch - Southwestern Portland Tap 138kV | 8 | N |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 8 | N |
| Midland East - Moss Switch 345 kV | Edwards Tap - Judkins 138 kV | 6 | N |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Jones Street TNP - Lakepointe TNP 138kV | 6 | N |
| Cisco - Putnam 138kV & Leon Switch 138 kV | Putnam 138 kV - Leon Switch 138 kV | 6 | N |
| DCKT Centerville Road Switch - Parkdale Switch 138 kV | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 5 | N |
| Paloduro Sub - Batesville Switching Station 138kV | Moore Switching Station - Downie Switching Station 138kV | 5 | N |
| Caney Creek - Wharton & East Bernard & Dyann 138 kV | Pledger - West Columbia 138 kV | 5 | N |
| DCKT South Texas # 1& # 2 | Hamilton Road - Maverick 138 kV | 5 | N |
| Moss Switch - Holt Switch & Amoco North Cowden 138 kV | Odessa North - Odessa Basin Switch 69 kV | 4 | N |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 4 | N |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barrilla 69 kV | 4 | N |
| Bracketville - Asphalt Mines 138 kV | Hamilton Road - Maverick 138 kV | 4 | N |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 4 | N |
| Midland East - Moss Switch 345 kV | Odessa - Odessa North 138 kV | 3 | N |
| Salt Creek BEPC - Spur And Scurry Switch 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 3 | N |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Euless - Grapevine Highway 360 138 kV (1065_L) | 3 | N |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - BTU_Jack_Creek 345 kV | 3 | N |
| Comanche Switch (ONCOR) - Comanche Peak Ses 345 kV | Comanche Switch (ONCOR) - Comanche Tap 138 kV | 3 | N |
| Del Rio City - Buena Vista & Hamilton Road 138kV | Hamilton Road - Maverick 138 kV | 3 | N |
| Pawnee Switching Station - San Miguel 345_138 KV Switchyards 345 kV | Pawnee Switching Station Xf1 345/138 kV | 3 | N |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69 kV | 3 | N |
| Bracketville - Odlaw Switchyard & Hamilton Road 138kV | Hamilton Road - Maverick 138kV | 3 | N |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Lewisville Switch - Jones Street TNP 138kV | 2 |  |
| Sun Switch - Morgan Creek SES 138 kV | Snyder - Sacroc 138kV | 2 |  |
| Sun Switch - Morgan Creek SES 138 kV | Aspermont AEP 138_69T1 138/69 KV | 2 |  |
| DCKT Allen Switch - Royse Switch and Monticello Ses 345 KV | Apollo - Richardson east 138 kV | 2 |  |
| DCKT Allen Switch - Royse Switch and Monticello Ses 345 KV | Ben Davis - Parker Maxwell Creek 138kV | 2 |  |
| Lewisville Switch - Carrollton Northwest 345kV (105_A) | Jones Street TNP - Lakepointe TNP 138kV | 2 |  |
| North Alvin TNP - Meadow Sub 138 kV | PH Robinson AT1L (3) 345/138 kV | 2 |  |
| China Grove Switch - Morgan Creek SES 138 kV (6220) | China Grove Switch - Morgan Creek SES 138kV (6225) | 2 |  |
| Rule - Aspermont AEP 69 kV | Aspermont AEP - Aspermont Continental 69 kV | 2 |  |
| Camp Springs Energy Center - Golden Switch 138 kV | Morgan Creek SES- Sun Switch 138 kV | 2 |  |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Hamilton Road - Maverick 138 kV | 2 |  |
| Bosque Switch - Elm Mott 345 kV | Rogers Hill BEPC - Elm Mott 138 kV | 2 |  |
| Ph Robinson At2_H 345/138 kV | PH Robinson AT1L (3) 345/138 kV | 2 |  |
| Kyle - San Marcos 138 kV | Turnersville - Buda 138 kV | 2 |  |
| Scurry Switch - Sun Switch 138 kV | Spur - Girard Tap 69 kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Longworth - Roby 69 kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 1 |  |
| Sun Switch - Morgan Creek SES 138 kV | Longworth - Roby 69 kV | 1 |  |
| Sun Switch - Morgan Creek SES 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| Sun Switch - Morgan Creek SES 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| DCKT Allen Switch - Royse Switch and Monticello Ses 345 KV | Apollo - Richardson east 138 kV | 1 |  |
| DCKT Jewett - Singleton 345 kV | Gibbons Creek - Singleton 345kV (SNGXGC_75) | 1 |  |
| DCKT Jewett - Singleton 345 kV | Gibbons Creek - Singleton 345 kV (SNGXGC_99) | 1 |  |
| Golden Switch - Sun Switch 138 kV | Willow Valley Switch - Gail Sub 138 kV | 1 |  |
| Lewisville Switch - Carrollton Northwest 345 kV (105_A) | Lewisville Switch - Jones Street TNP 138 kV | 1 |  |
| Lewisville Switch - Carrollton Northwest 345 kV (105_A) | Highlands TNP - West TNP 138 kV | 1 |  |
| North Alvin TNP - Meadow Sub 138 kV | PH Robinson AT1L (3) 345/138 kV | 1 |  |
| China Grove Switch - Morgan Creek Ses 138 kV (6220) | Morgan Creek Ses Axfmr3h 138/69 kV | 1 |  |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 1 |  |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | San Diego - Freer 69 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | Asherton - North Laredo Switch 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | Hamilton Road - Maverick 138 kV | 1 |  |
| DCKT Elmcreek - San Miguel 345_138 kV Switchyards 345 kV | Coleto Creek - Kenedy Swtich 138 kV | 1 |  |
| Norwood Switch Axfmr1h 345/138 kV | Amelia Street - UT Southwest Medical Center 138 kV (3415_D) | 1 |  |
| Green Mountain Energy Wind Farm At Brazos - Sun Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | 1 |  |
| DCKT Calmont Switch - Benbrook Switch 138 kV | Saginaw Switch - American Mfg Tap 138 kV | 1 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 1 |  |
| Aspermont AEP - Paint Creek 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 1 |  |
| Forest Hill Switch Axfmr1 138/69kV | Handley SES - Duval 69 kV | 1 |  |
| Oxychem Ingleside - Ingleside Cogen Switch 138 kV (Inglco_Oxy_In1) | Dupont Switch Ingleside - Dupont PP1 Ingleside 138 kV (I_Dupp_I_Dups1) | 1 |  |
| Paducah - Matador & Paducah Clare Street 69 kV | Aspermont AEP - Aspermont Continental 69 kV | 1 |  |
| DCKT Garfield LCRA - Lytton Springs & Austrop - Zorn 345 kV | Garfield AEN Gf_At_2 345/138 kV | 1 |  |
| Spur 138_69_1 138/69 kV | Aspermont AEP 138_69T1 138/69 kV | 1 |  |
| Desoto Switch - Red Oak - Ennis Switch 138 kV | Ennis West Switch - Waxahachie 138 kV | 1 |  |
| Snyder Axfmr1 138/69 kV | Ector Switch Axfmr1 138/69 kV | 1 |  |
| DCKT Centerville Road - Centerville Road Switch - Lake Hubbard Ses 138 kV (3260_A, 3260_B, & 3671) | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 1 |  |
| Manchaca - Buda 138 kV | Buda - Rutherford 138 kV | 1 |  |
| Odessa North Axfmr1 138/69 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4L (3) 345/138 kV | 1 |  |
| Comanche Switch (ONCOR) - Brown Switch 345 kV | Hamilton Road - Maverick 138 kV | 1 |  |
| Los Fresnos - Loma Alta Substation & La Palma 138 kV | La Palma - Villa Cavazos 138 kV | 1 |  |
| Eagle Pass Hydro - Maverick 138 kV | Friess Ranch - Rock Springs 69 kV | 1 |  |
| DCKT Navarro - Big Brown SES And Venus Switch 345 kV | Richland Chambers - Trinidad SES 345 kV (21) | 1 |  |
| DCKT Singleton - Zenith 345 kV | Singleton - Tomball 345 kV | 1 |  |
| Ph Robinson At2_H 345/138 kV | PH Robinson AT1L (3) 345/138 kV | 1 |  |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Prairie Creek Switch - Prairie Creek 138 kV (3655_B) | 1 |  |
| Kiamichi Energy Facility - Kiowa Switch 345 kV (Kmchi_Kwass1) | Kiamichi Energy Facility - Kiowa Switch 345 kV (Kmchi_Kwass2) | 1 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Kenedy Swtich 138 kV | 1 |  |
| DCKT Twin Oak Switch - BTU_Jack_Creek & Gibbons Creek 345 kV | Jewet - Singleton 345 kV (240) | 1 |  |
| Alazan - Barney Davis and Nelson Sharpe 138 kV | Airline AEP - Cabaniss 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which made our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 4 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 09/12/2012 | Transmission and Security Desk V1 Rev20 | 611 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

09/05 17:00 64,862 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | 2.85 |
| August | 3.07 | 2.29 | 2.28 | 2.96 |
| September | 3.68 | 3.14 | 2.70 | 3.43 |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.99 |

OCN, Advisory, Watch & Emergency Notices

Capacity

None

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None