| PGRR Number | 02X | PGRR Title | Clarify Planning Assumptions and Performance Criteria |
| --- | --- | --- | --- |
| Date Posted |  |  |  |

| Requested Resolution (Normal or Urgent, and justification for Urgent status) | Normal |
| --- | --- |
| Planning Guide Section(s) Requiring Revision (Include Section No. and Title) | 2.1 Definitions 4.1 Introduction 4.1.1.1 Planning Assumptions 4.1.1.2 Reliability Performance Criteria |
| Protocol Section(s) Requiring Revision (If applicable) | None. |
| Revision Description | This Planning Guide Revision Request (PGRR) clarifies assumptions allowed for planning studies and planning performance criteria. The revised language will also better reflect current planning practices. |
| Reason for Revision | The current planning criteria in the Planning Guide are unclear and, in some cases, in conflict with the intention of the performance objective. |

Business Case

Business Case instructions:  To allow for comprehensive PGRR consideration, please fill out the Business Case section below and provide as much detailed information as possible.  Wherever possible, please include reasons, explanations, and cost benefit calculation pertaining to the PGRR.  Insert additional rows as needed.

| Business Case | 1 | This PGRR will add clarity for ERCOT and TSP planners. |
| --- | --- | --- |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
|  | 5 |  |

| Sponsor |  |
| --- | --- |
| Name | Jeff Billo on behalf of the PLWG |
| E-mail Address | jbillo@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248- 6334 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Guide Language Revision

Note to Y. Landin – need to capture update on Section 4 TOC

## DEFINITIONS

Relevant terms and definitions used in the Planning Guide can be found in Protocol Section 2, Definitions and Acronyms.  The terms within this Section 2.1 contains terms not defined in Protocols.

C

4.1	Introduction

(1)	ERCOT employs both reliability criteria and economic criteria in evaluating the need for transmission system improvements.  The economic criteria are included in Protocol Section 3.11.2, Planning Criteria.  This Planning Guide provides the reliability criteria.

(2)	The ERCOT System consists of those generation and Transmission Facilities (60 kV and higher voltages) that are controlled by individual Market Participants and that function as part of an integrated and coordinated system.

(3)	It is assumed that those entities that must comply with NERC planning criteria, as set forth in TPL-001, TPL-002, TPL-003 and TPL-004, will do so and ERCOT will not make any additional provisions that TSPs must follow the NERC criteria.

(4)  To maintain reliable operation of the ERCOT System, it is necessary that all stakeholders observe and subscribe to certain minimum planning criteria.  The criteria set forth herein constitute the aforementioned minimum planning criteria.  Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, ERCOT recognizes that events more severe than those outlined in these criteria could cause grid separation and other tests may also be performed.

(5)	The complexity and uncertainty inherent in the planning and operation of the ERCOT System make exhaustive studies impracticable; therefore, to gain maximum benefit from the limited number of tests performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

(6)	ERCOT will perform steady-state and dynamic analysis appropriate to ensure the reliability of the ERCOT System and identify appropriate solutions.

(7)	Each Transmission Service Provider (TSP) will perform steady-state, short circuit, and dynamic analysis appropriate to ensure the reliability of their portion of the ERCOT System and implement appropriate solutions

(8)	The base cases created by the Steady-State Working Group (SSWG), System Protection Working Group (SPWG), and ERCOT are available for use by Market Participants.

(9)	If a TSP has its own planning criteria in addition to those defined in this Planning Guide, the TSP shall provide documentation of those criteria to ERCOT.  ERCOT shall post the documentation on the Planning and Operations Information website.  The TSP shall notify ERCOT of any changes to their planning criteria and provide revised documentation within 30 days of such change.

4.1.1	Reliability Criteria

4.1.1.1	Planning Assumptions

(1)  Contingency Loss of an element includes the loss of an element with or without a single line-to-ground or three-phase fault with normal clearing

(2)  Common Tower Outage – the Contingency Loss of

(i)  a double-circuit transmission line consisting of two circuits sharing a tower for 0.5 miles or greater; or,

(ii)  any combination of two of the three circuits of a triple-circuit transmission line consisting of three circuits sharing a tower for 0.5 miles or greater.

(2)  Unavailability of a single generating unit includes an entire combined cycle train, if no part of the train can operate with one of the units off-line per the Resource Asset Registration Form.

(3)  The Contingency Loss of a single generating unit shall include the loss of an entire combined cycle train, if that is the expected consequence of normal clearing of the fault condition.

The following assumptions may be applied to the ERCOT-published base cases for use in planning studies:

(a)	Reasonable variations of load forecast.

(b)	Reasonable variations of generation commitment and dispatch applicable to transmission planning analyses on a case-by-case basis may include, but are not limited to, the following methods:

(i)	Production cost model simulation, security constrained optimal power flow, or similar modeling tools that analyze the ERCOT System using hourly generation dispatch assumptions;

(ii)	Modeling of high levels of intermittent generation conditions; or

(iii)	Modeling of low levels of or no intermittent generation conditions.

4.1.1.2	Reliability Performance Criteria

The following performance criteria (summarized in Table 1 below) shall be applicable to planning analyses in the ERCOT region.

- With all facilities in their normal state, following a Common Tower Outage, all facilities shall be within their applicable ratings, the system shall remain stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss.

- With any single generating unit unavailable, followed by Manual System Adjustments, followed by a Common Tower Outage or the Contingency Loss of a single generating unit, transmission circuit, or transformer, all facilities shall be within their applicable ratings, the system shall remain stable with no cascading or uncontrolled islanding, and there shall be no non-consequential load loss.

| Initial Condition | Event | Facilities within Applicable Ratings and System Stable with No Cascading or Uncontrolled Outages | Non-consequential load loss allowed |
| --- | --- | --- | --- |
| Normal System | Common Tower Outage | Yes | No |
| Unavailability of a generating unit, followed by Manual System Adjustments | Common Tower Outage; or, Contingency Loss of one of the following: - Generating unit - Transmission circuit - Transformer | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.   If a Transmission Facility improvement is required to meet the criteria in this section, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.

4.1.1.3	Voltage Stability Margin

Voltage stability margin shall be sufficient to maintain post-transient voltage stability under the following study conditions for each ERCOT or TSP-defined areas:

(a)	A 5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas; and NERC Category A or B operating conditions; and

(b)	A 2.5% increase in Load above expected peak supplied from resources external to the ERCOT or TSP-defined areas and NERC Category C operating conditions.

4.1.2	ERCOT Application of NERC Standards for System Assessments

4.1.2.1	Category C

(1)	Bus Section Definition - "Bus Section" shall be interpreted to mean any section of bus work, which would be isolated by normal relay/breaker operation when faulted.

(2)	Manual System Adjustments Definition - "Manual System Adjustments" shall be interpreted to include only operator actions that:

(a)	Would be made no later than one hour after clearing of the first fault;

(b)	Are made using remote control capability or communications with other operators having such capability;

(c)	Include circuit switching, changes in the schedules of Generation Resources operating at clearing of the first fault, and changes in the schedules of other Generation Resources that can contribute within one hour; and

(d)	Exclude the physical repair or replacement of damaged equipment and the starting of any Generation Resource that cannot contribute within one hour.

(3)	Planned Loss of Demand or Curtailed Firm Transfer Definition - All Load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged with associated written operating procedures.  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

(4)	Cascading Outage Definition - Cascading Outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

(5)	Implementation Guidelines - Evaluation of all the possible combination of facility Outages under Category C is not required.  Each TSP with bulk Transmission Facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events.  In either case, the selected contingencies must indicate more severe results or impacts based on the engineering judgment of the facility owner, ERCOT or any TSP.  An explanation of why any remaining contingencies would produce less severe system results shall be available as supporting information.

4.1.2.2	Category D

(1)	For the purpose of evaluating the consequences resulting from a Category D event, a Large Load or Major Load Center is an electrical demand of between 50 and 500 MW.  This may be a large single Load or a group of electrically close Loads.  The loss of this demand will not include any other system elements other than those directly connected.

(2)	Evaluations of Category D contingencies are not required to be performed annually.  Evaluations should be performed for the following:

(a)	Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study; and

(b)	Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, ERCOT or any TSP, have unacceptable consequences.