## Slide 1: Tab 9: ERCOT Pilot Project for Fast Responding Regulation Service (FRRS)
Kenneth Ragsdale
Principal, Market Design & Analysis
Board of Directors Meeting
ERCOT Public
September 18, 2012

## Slide 2: Overview
Tab 9 ERCOT Public
What is Fast Responding Regulation Service (FRRS)?
Potential Benefits of FRRS
Purpose of the FRRS Pilot Program
FRRS Qualification and Performance Criteria
Procurement and Settlement of FRRS
Proposed Implementation Schedule
Projected Costs
Review of Stakeholder Process
Questions

## Slide 3: What is Fast Responding Regulation Service (FRRS)?
FRRS is an Ancillary Service requiring participating Resources to ramp to full output within 60 cycles of an instruction or triggering event.
FRRS is intended to complement current Regulation Service.
FRRS is intended to respond first and help slow down the frequency decay while other Resources start to respond.
FRRS is intended to respond to large frequency drops to promptly help arrest the frequency decay.
California ISO, New York ISO, PJM, ISO New England and MISO will have or already have fast responding regulation.
Tab 9 ERCOT Public

## Slide 4: Potential Benefits of FRRS
Promptly arrest frequency decay during unit trips.
Reduce the use of traditional regulation.
Reduce the quantity of Regulation capacity required to be procured.
Provide better frequency control at a lower overall cost.
Tab 9 ERCOT Public

## Slide 5: Purpose of the FRRS Pilot Program
Gather and analyze data to determine potential improvements in ERCOT’s ability to arrest frequency decay during unit trips due to FRRS.
Gather and analyze data to determine potential reductions in procurement of current Regulation due to FRRS.
Assess the operational benefit and challenges of procuring and deploying FRRS.
Gather and analyze data to assist ERCOT in developing settlement methodologies for FRRS and current Regulation that use a pay-for-performance approach like that specified in FERC Order 755.
Tab 9 ERCOT Public

## Slide 6: FRRS Performance Criteria
Resources providing Fast Responding Regulation Service (FRRS-Up, FRRS-Down, or both) must meet the following performance criteria:
Resources must be able to detect and respond to ERCOT’s FRRS signal within 60 cycles of receiving the signal.
Resources must be able to automatically detect frequency deviations of .09Hz from 60Hz and provide full capacity response within 60 cycles.
FRRS Resources must provide at least 95% and no more than 110% of the obligated MW.
Failure to provide the obligated MW within the required time for 30% or more of the deployments during any hour shall be deemed a failure to provide and will result in clawback for that hour.
Tab 9 ERCOT Public

## Slide 7: Procurement of FRRS
ERCOT will conduct a weekly procurement of FRRS in which it will procure up to 65 MW per hour for FRRS-Up and up to 35 MW per hour for FRRS-Down. No changes are made to the existing REGUP and REGDN requirements.
Each Tuesday, QSEs representing qualified FRRS Resources inform ERCOT of the amounts available for the following Saturday through Friday.
ERCOT will prorate awards as necessary and send weekly awards to QSEs each Thursday.
FRRS Resources shall update COPs to reflect the final schedule as REGUP or REGDN.
Tab 9 ERCOT Public

## Slide 8: Settlement of FRRS
FRRS Resources are paid the DAM clearing price for Regulation Service multiplied by the quantity of awarded FRRS MW.
ERCOT creates SASM data cuts to reflect FRRS awards using REGUP and REGDN bill determinants. The operators do not actually execute a SASM.
Costs for FRRS will be assessed against QSEs according to Load Ratio Share.
ERCOT will claw back payments for all hours in which FRRS Resources failed their performance obligations.
Tab 9 ERCOT Public

## Slide 9: Projected Costs
Personnel Costs: It is expected that ERCOT will need to engage a contractor equivalent to .5 to 1 FTE for the duration of the pilot project.
Procurement Costs: The average cost for REGUP over the last 6 months has been about $9/MW and for REGDN has been about $6/MW. Based on these costs, the cost for 6 months of FRRS procurement is estimated to be about $3.4 Million.
Tab 9 ERCOT Public

## Slide 10: Proposed Pilot Schedule
ERCOT proposes the following timeline:
November 14, 2012: Qualification of FRRS Resources opens.
January 15, 2013: ERCOT begins accepting offers for first week of pilot.
January 17, 2013: ERCOT notifies Resources of first week’s commitments.
January 19, 2013: ERCOT begins deployment of FRRS.
May 1, 2013: ERCOT provides preliminary report to Board on FRRS (monthly updates will be provided to ETWG and PDCWG).
July 19, 2013: Pilot terminates (unless extended by Board or terminated earlier).
August/September 2013: ERCOT provides final report on pilot.
Tab 9 ERCOT Public

## Slide 11: Summary of Stakeholder Review Process
ERCOT discussed FRRS proposal 15 times at various stakeholder group meetings beginning in June 2012:
  Emerging Technologies Working Group, QSE Managers Working Group, Performance Disturbance Compliance Working Group
  Wholesale Market Subcommittee, Reliability Operations Subcommittee
  Technical Advisory Committee
Questions and comments from Market Participants and the various subcommittees have been addressed at stakeholder meetings and through formal written responses. ERCOT has revised the pilot based on this feedback.
The initial draft Governing Document was posted on 8/23/12 and revised based on written comments and discussions at 9/7/12 TAC meeting.
Tab 9 ERCOT Public

## Slide 12
Questions?
Tab 9 ERCOT Public