## Slide 1: ERCOT Pilot Project for Fast Responding Regulation Service (FRRS)
June 13, 2012 WMS and
June 14, 2012 ROS

## Slide 2: Agenda
Declining Grid Inertia of ERCOT Interconnection
ERCOT Frequency Profile Jan 2011 through Feb-2012
  ERCOT Frequency Profile – 4 second data
  ERCOT CPS1 Score
Qualifications and Performance Criteria
Purpose of FRRS Pilot Program
  What is FRRS?
  Why do we need it?
Fast Regulation Deployment Logic
  Fast regulation to complement the traditional regulation
Expected benefits of Fast Responding Regulation
How will FRRS be procured (priced and paid for) in the Pilot?
Implementation Schedule for the Pilot
Questions
ERCOT Public

## Slide 3: Declining Inertial Frequency Response in ERCOT
ERCOT Public
http://www.ercot.com/content/gridinfo/etts/keydocs/System_Inertial_Frequency_Response_Estimation_and_Impact_of_.pdf

## Slide 4: ERCOT Frequency Profile Jan 2011 through Feb-2012
ERCOT Public

## Slide 5
ERCOT Public

## Slide 6: Pilot FRRS Qualification Criteria
Resources providing FRRS must be able to follow FRRS signal
Resources requesting FRRS-up qualification
  Must be able to respond to large frequency decay triggered by loss of generation.
  Resources providing FRRS must provide full MW response within 60 cycles after frequency hits 59.91 Hz trigger.
  This capability must be demonstrated by the Resource Entity using high speed Frequency and MW data with resolution no less than 32 samples per second.
  For the purpose of demonstration, the Resource Entity may use off-set of -0.2 Hz to demonstrate the MW response.
ERCOT Public

## Slide 7: Pilot FRRS Qualification Criteria (continued)
Resources requesting FRRS-down qualification
  Must be able to respond to high frequency.
  Resources providing FRRS must provide full MW response within 60 cycles after frequency hits 60.09 Hz trigger.
  This capability must be demonstrated by the Resource Entity using high speed Frequency and MW data with resolution no less than 32 samples per second.
  For the purpose of demonstration, the Resource Entity may use off-set of +0.2 Hz to demonstrate the MW response.
Resources providing FRRS (Up and Down) must be able to continuously remain deployed for up to 8 minutes with 95% or more of the requested MW for successful qualification.
Resources that successfully demonstrate the requirement above will be qualified as FRRS capable Resources for the capacity that was requested for qualification.
ERCOT Public

## Slide 8: FRRS Performance Criteria
Resources providing Fast Responding Regulation Service shall meet the following performance criteria
MW response provided by Resources carrying FRRS in response to ERCOT FRRS signal shall be at least 95% and less than 110 % of the ERCOT deployment instruction for that Resource.
Resources must meet the requirement stated in (1) for 95% of all deployments within a month.
When FRRS-up is not fully deployed, for sudden frequency decay where frequency declines lower than 59.91 Hz, Resources providing FRRS-up shall immediately and appropriately respond to the declining frequency.
When FRRS-down is not fully deployed, for sudden frequency deviation that may cause frequency to exceed 60.09 Hz, Resources providing FRRS-down shall immediately and appropriately respond to frequency.
Failure to meet the requirement (2) will lead to reduction in capacity payment.
ERCOT Public

## Slide 9: Purpose of the FRRS pilot program
Gather and analyze data to assist in determining the potential improvements in ERCOTs ability to arrest frequency decay during unit trips due to the presence of FRRS
Gather and analyze data to assist in determining the potential reductions of current regulation that would be appropriate due to the presence of FRRS
Assess the operational benefit and challenges of procuring and deploying FRRS
Gather and analyze data to assist ERCOT in developing settlement methodologies for FRRS and current regulation that use a pay for performance approach similar to what is specified in FERC Order 755;
ERCOT Public

## Slide 10: FRRS-Up and FRRS-Down Deployment Logic
Deadband for FRRS trigger (±0.03 Hz)
Deployment period
Deployment period when frequency degrades further
Recalling
Maximum continuous deployment duration
Apply similar logic for Down-Regulation for high frequency
ERCOT may make additional parameter changes during pilot as needed
FRRS deployment signal logic will be shared with the pilot Resources
ERCOT Public

## Slide 11
ERCOT Public

## Slide 12: Frequency Decay Slope
ERCOT Public

## Slide 13: Potential benefits of FRRS
Promptly arrest frequency decay during unit trips
Diminishing use of traditional regulation
Reduction in Regulation capacity procurement
Better frequency control at a lower overall cost
ERCOT Public

## Slide 14: How is FRRS Procured during the Pilot?
FRRS-up and FRRS-down amounts are specified in advance for each hour. For the pilot, ERCOT will procure up to 65 MW per hour for FRRS-up and will procure up to 35 MW per hour for FRRS-down. No changes are made to the existing REGUP and REGDN requirements.
ERCOT has a list of “Qualified” FRRS Pilot Resources. Each Wednesday QSEs inform ERCOT of the amounts available for Saturday through Friday.
ERCOT prorates amounts to Pilot Resources as necessary. Final quantities sent to QSEs (for the upcoming week).
COPs for Pilot Resources shall reflect the final schedule as REGUP and REGDN.
ERCOT Public

## Slide 15: How is FRRS is Priced and Paid for during the Pilot?
ERCOT Settlements performs settlement by creating appropriate SASM data cuts. Current REGUP and REGDN bill determinants are used. A SASM is NOT executed by the operators.
DAM clearing prices shall be used to price the FRRS awards.
The cost for pilot MWs procured are paid for similar to other AS.
Adjustments can be made depending on actual availability and performance.
ERCOT Public

## Slide 16: Pilot Schedule
Power point presentations at WMS, ROS and ETWG in June and July.
Suggestions and comments due to ERCOT 6-27-12
ERCOT plans to present updates at July WMS and ROS meetings (7/11 and 7/12).
Draft Governing Document to be posted by 7-26-12. (7 days before TAC)
ERCOT plans to present at 8/2/12 TAC meeting.
Request approval for Pilot at the 9/18/12 BOD meeting.
Qualify Pilot Resources 9/18/12 through 4/30/13 (end of pilot). [6 month Pilot]
Begin procurements with Operating Day 11-1-12. Continue for 6 months unless stopped early by ERCOT. Extensions of pilot may be considered during first 6 months.
ERCOT Public

## Slide 17: Other Info
Regular updates to be provided to TAC during Pilot Project.
It is expected that ERCOT will need to engage a contractor equivalent to .5 to 1 FTE for the duration of the Pilot Project.
The average cost for REGUP over the last 6 months has been about $9/MW and for REGDN has been about $6/MW. The estimated cost for 6 months of FRRS procurement from pilot resources is estimated to be about $3.4 Million.
ERCOT Public

## Slide 18: Questions? Please send suggestions and comments to WMS or ROS exploder or ssharma@ercot.com kragsdale@ercot.com before COB 6-27-12
ERCOT Public