ERCOT Operations Report

November 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 11/2/2012 1:41 | 59.752 | 4 | Unit trip with 1223 MW net online. |
| 11/9/2012 5:04 | 59.880 | 406 | Up reg instruction delayed and deployed RRS. |
| 11/11/2012 10:49 | 59.862 | 24 | Unit trip with 412 MW net online. |
| 11/17/2012 10:23 | 59.731 | 88 | Unit trip with 642 MW net online. |
| 11/17/2012 12:34 | 59.825 | 60 | Multiple Unit trips with 580 MW net online. |
| 11/22/2012 11:53 | 59.787 | 76 | Unit trip with 830 MW net online. |
| 11/24/2012 5:01 | 59.837 | 56 | Unit trip with 462 MW net online. |
| 11/26/2012 16:05 | 59.823 | 32 | Multiple Unit trips with 729 MW net online. |
| 11/28/2012 12:29 | 59.793 | 68 | Unit trip with 832 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 11/02/2012 01:41:38 AM | DCS event | Approx. 8 sec | The event was caused by the loss of one unit. The unit was generating 1178 MW Net before trip. The frequency dropped to 59.69 Hz due to the event. The oscillating frequency of 0.58 Hz and 8.47% damping ratio was observed during the event. |
| 11/17/2012 10:23:17 AM | Unit Trip | Approx. 10 sec | The event was caused by the loss of one unit. The unit was generating 1231 MW Net prior to runback and the unit tripped with 642 MW. The frequency dropped to 59.72 Hz due to the event. The oscillating frequency of 0.71 Hz and 9.9% damping ratio was observed during the event. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 11/2/12 1:41:46 | 11/2/12 1:41:54 | 0:00:08 | 863.33 |  |
| 11/9/12 5:04:44 | 11/9/12 5:18:12 | 0:13:28 | 164.38 |  |
| 11/11/12 10:49:56 | 11/11/12 10:53:08 | 0:03:12 | 256.58 |  |
| 11/17/12 10:22:34 | 11/17/12 10:26:10 | 0:03:36 | 1372.4 |  |
| 11/17/12 12:34:10 | 11/17/12 12:37:10 | 0:03:00 | 494.55 |  |
| 11/22/12 11:53:56 | 11/22/12 11:57:28 | 0:03:32 | 756.06 |  |
| 11/24/12 5:01:24 | 11/24/12 5:05:12 | 0:03:48 | 320.07 |  |
| 11/26/12 16:05:24 | 11/26/12 16:08:56 | 0:03:32 | 604.78 |  |
| 11/28/12 12:29:34 | 11/28/12 12:32:22 | 0:02:48 | 473.35 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Cisco - Putnam 138kV & Leon Switch 138kV | Putnam 138kV - Leon Switch 138kV | 24 | N |
| DCKT Skyline - Calaveras 345 kV | Calaveras - Pawnee Switching Station 345 kV | 16 | N |
| Skyline - Calaveras 345 kV (N5_P4_2) | Skyline - Calaveras 345 kV (N5_P4) | 10 | N |
| Pawnee Switching Station - Calaveras 345 kV | Pawnee Switching Station Xf1 345/138 kV | 10 | N |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 7 | N |
| Salt Creek BEPC - Spur And Scurry Switch 138 kV | Aspermont AEP 138_69T1 138/69 kV | 7 | Y |
| DCKT Permian Basin SES - Wink Sub & Wickett Tap 138 kV | Northward - Wink Sub 69 kV | 5 | N |
| Odessa Ehv Switch Axfmr2t (3) 345/138 kV | Odessa Ehv Switch Axfmr3t (3) 345/138 kV | 5 | N |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69 kV | 4 | N |
| Comanche Switch (Oncor) - Comanche Peak SES 345 kV | Comanche Switch (Oncor) - Comanche Tap 138 kV | 4 | N |
| Skyline - Calaveras 345 kV (N5_P4) | Skyline - Calaveras 345 kV (N5_P4_2) | 4 | N |
| Midkiff Switch - Spraberry Switch 138 kV | Glasscock (Oncor) - Garden City 69 kV | 4 | N |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barrilla 69 kV | 4 | N |
| Falcon Seaboard - Morgan Creek SES 345 kV | Morgan Creek SES Axfmr1h (3) 345/138 kV | 3 | N |
| Bosque Switch - Whitney 138 kV | Lake Whitney Tnp - Whitney 138 kV | 3 | N |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North Axfmr1 138/69 kV | 3 | Y |
| North Edinburg - Lon Hill 345 kV | Las Pulgas - Rio Hondo 138 kV | 3 | Y |
| Duke / Hec - North Edinburg 138 kV (Duke_Nedin1) | Duke / Hec - North Edinburg 138 kV (Duke_Nedin2) | 3 | N |
| Midland East - Moss Switch 345 kV | Odessa North - Odessa Basin Switch 69 kV | 3 | N |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 2 |  |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 2 |  |
| Salt Creek BEPC - Spur And Scurry Switch 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 2 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | McDonald Road - Forsan Tap 138 kV | 2 |  |
| Falcon Seaboard - Midland East 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |  |
| DCKT Navarro - Watermill Switch & Limestone 345 kV | Jewett - Big Brown SES 345 kV (50) | 2 |  |
| Asphalt Mines - Uvalde AEP & Odlaw Switchyard 138kV | Hamilton Road - Maverick 138 kV | 2 |  |
| Bosque Switch - Whitney 345 kV | Rogers Hill BEPC - Elm Mott 138 kV | 2 |  |
| DCKT Graham SES - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 2 |  |
| Ector Harper - Moss Switch & Permian Basin SES 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 2 |  |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg AEP 138 kV | 2 |  |
| Caney Creek - Wharton & East Bernard & Dyann 138 kV | Lane City - Blessing 138 kV | 2 |  |
| DCKT Morgan Creek SES - China Grove Switch 138 kV | Morgan Creek SES Axfmr3h 138/69 kV | 2 |  |
| Sacroc - Sun Switch & Snyder 138 kV | Ennis Creek Switch Axfmr1 138/69 kV | 2 |  |
| Bracketville - Odlaw Switchyard & Hamilton Road 138 kV | Hamilton Road - Maverick 138 kV | 2 |  |
| DCKT Skyline - Calaveras 345 kV | Braunig - Cagnon 345 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | Forsan Tap - Crmwd 7 Tap 138 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| DCKT Permian Basin SES - Wink Sub & Wickett Tap 138 kV | Wickett Tnp - Winkler County 6 Tnp 69 kV | 1 |  |
| Aspermont AEP - Spur 138 kV | Wolfgang - Rotan 69 kV | 1 |  |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney Tnp 138 kV | 1 |  |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North - Odessa Basin Switch 69 kV | 1 |  |
| North Edinburg - Lon Hill 345 kV | North Edinburg - Rachal 138 kV | 1 |  |
| Falcon Seaboard - Midland East 345 kV | McDonald Road - Forsan Tap 138kV | 1 |  |
| DCKT Navarro - Watermill Switch & Limestone 345 kV | Jewett - Big Brown SES 345 kV (40) | 1 |  |
| Ajo - Rio Hondo 345 kV | Las Pulgas - Rio Hondo 345 kV | 1 |  |
| Ajo - Rio Hondo 345 kV | North Edinburg Nedin_XC2 345 kV | 1 |  |
| Flat Creek Switch - Stephenville (Oncor) 138 kV | Putnam 138kV - Pecan Bayou 138 kV | 1 |  |
| DCKT Watermill - Tricorner And Trinidad SES 345 kV | Trinidad SES Axfmr6 (3) 345/138 kV | 1 |  |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Jones Street Tnp - Lakepointe Tnp 138 kV | 1 |  |
| Crane (Oncor) Axfmr1 138/69 kV | Holt Switch Axfmr1 138/69 kV | 1 |  |
| DCKT Greens Bayou - King 345 kV | Greens Bayou At2L (3) 345/138 kV | 1 |  |
| Big Lake - Twin Buttes 138 kV | Santiago - Live Oak AEP 138 kV | 1 |  |
| DCKT Comanche Peak SES Units 1 & 2 | Whitney Wht1h 345/138kV | 1 |  |
| Wink Sub - Permian Basin SES 138 kV | Wickett Tnp - Winkler County 6 Tnp 69 kV | 1 |  |
| DCKT South Channel - Pair & Shell 138 kV | Waburn - Taylor 138 kV | 1 |  |
| Andrews North Axfmr1 and Axfmr2 138/69 kV | Holt Switch Axfmr1 138/69 kV | 1 |  |
| Bosque Switch - Elm Mott 345 kV | Rogers Hill BEPC - Elm Mott 138 kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Kennedy Switch - Kennedy Sub 69 kV | 1 |  |
| Andrews North – Holt Switch & No Trees Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which made our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 7 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

11/02 	Mt. Enterprise SPS #7 and #21 removed.

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 11/01/2012 | Transmission and Security Desk V1 Rev21 | 617 |
| 11/01/2012 | Shift Supervisor Desk V1 Rev18 | 616 |
| 11/01/2012 | Resource Desk V1 Rev20 | 615 |
| 11/01/2012 | Reliability Unit Commitment Desk V1 Rev17 | 614 |
| 11/01/2012 | Real Time Desk V1 Rev21 | 613 |
| 11/01/2012 | DC Tie Desk V1 Rev17 | 612 |

## Load Shed Incidences

11/30 12:03	15 MW of load shed in West Texas.

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

11/02 17:00 41,459 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | 2.85 |
| August | 3.07 | 2.29 | 2.28 | 2.96 |
| September | 3.68 | 3.14 | 2.70 | 3.43 |
| October | 2.92 | 2.37 | 3.51 | 2.99 |
| November | 1.93 | 3.46 | 3.38 | 2.90 |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.98 |

OCN, Advisory, Watch & Emergency Notices

Capacity

None

Transmission Watch

11/5 14:43 	ERCOT issued a transmission watch for Rio Grande Valley area.

Watch

None

Emergency Notice

11/30 12:03	ERCOT issued an emergency notice for real time overloads in West Texas area. At 1315 the emergency notice was cancelled and all the TO’s were notified.

Texas RE Event Analysis

None