Operations Working Group Meeting

Wednesday, 11/14/12

Austin - MET Center

In Attendance:

Curtis Graves – Austin Energy

Doug Whitworth – TRE

Paula Mueller – TRE

Robert Bailey – NRG

Bob Temple - WETT

Brenda Hampton – Luminant

Robert Avila – BPUB

John Warren - LCRA

Jerry Willms - LST

Laura Zotter – Austin Energy (TO)

Tip Tipton - Brazos

Ross Owen – Oncor (TO)

Jeff Sims – CPS

Patrick Trevino – CPS

Karl Tammar – Sharyland

Kevin Morley – CNP

Larry Gurley – BTU

Ken Lindberg – BTU

David Penny – TRE

Frank Owens - CTT

Yvette Landin – ERCOT (RC)

Jimmy Hartmann – ERCOT (RC)

Vijay Betanabhatla – ERCOT (RC)

Dial-In Attendees:

David Kee – CPS

John Wester – Austin Energy

Fred Sherman – GPL

Billy McCraner – Tenaska

Kevin Sills - Oncor

Isabel Flores - ERCOT

- Antitrust Admonition – Meeting opened at 9:30 with a review of the Antitrust Admonition by Frank Owens.

- ROS Meeting –

Frank reviewed the new process of ROS getting a full report from each sub group.

- August OWG Meeting Notes - Notes approved.

- NOGRR Reviews

  - 101NOGRR Market Transparency for DC Tie Outage Information

This NOGRR provides that ERCOT shall produce a detailed report regarding any outage of a Direct Current Tie (DC Tie) in a timely manner.  Outages of interconnection points between the ERCOT and non-ERCOT Control Areas have market implications on both the ERCOT market and the interconnected market.

Tenaska provided comments and ERCOT outage group cannot accommodate the comments for confidentially reasons. Tenaska will follow up with Woody Rickerson on which parts of the comments are unacceptable to ERCOT.

Impact analysis: ERCOT has <= $10K Impact

Endorsed IA and forwarded to ROS.

  - 104NOGRR Removal of Transmission Operator Definition from the Nodal Operating Guide

This NOGRR proposes deleting the definition of Transmission Operator from the Nodal Operating Guides.

ERCOT owes comments on this NOGR to TRS by December. ERCOT proposed to table the NOGR.

OWG agreed to table NOGR 104 till January

  - 106NOGRR Delegation of Firm Load Shedding Responsibility

This NOGRR clarifies that a Distribution Service Provider (DSP) may make an agreement with another Entity that delegates the responsibility for managing both automatic and Energy Emergency Alert (EEA) firm Load shed.

Larry from BTU explained that the TSP is not willing to take responsibility for Load shed. BTU as the TO wants to take the responsibility but cannot with the existing language in the Operating Guides

John Warren from LCRA mentioned that LCRA is responsible for loadshed of a lot of Oncor’s load and said he is willing to share information with BTU if that set up can work for them.

OWG agreed to table NOGR 106 as it is related to NOGR 104 which has been tabled till January and also give time for BTU to discuss with LCRA/Oncor.

  - 105NOGRRGeneration Resource Frequency Response Test Procedure, submitted by the Performance Disturbance Compliance Working Group

This NOGRR adds a Governor Test form for Controllable Load Resources and proposes minor corrections to calculations.  (PDCWG) Language review and ERCOT comments

OWG recommends approving the NOGR with ERCOT comments and OWG revisions

Send out for impact analysis to ERCOT.

- Monthly Operations Report

Vijay reviewed the report, no comments or questions were received.

- Nodal Protocol and Guides Resolution Task Force Report

The resolution task force did not meet.

- Operations Task Force Report

No Updates

- Seminar Task Force Report

No updates

- Texas RE Update Report

Paula Mueller from TRE addressed the group and provided update on the upcoming TRE protocol compliance audits. It has been 2 years since the last protocol compliance audit. So TRE prepared a schedule for the 2013 audit. This will be in coordination with the NERC audit schedule. The schedule is posted on the TRE website. Not everyone being audited by NERC on 2013 will be audited by TRE for the protocol compliance. But anyone that does not have a NERC audit in 2013 will not be audited by TRE.

Ross Owen inquired about the audit period for which Paula responded that the audit period starts on December 2010 when the nodal protocols became effective.

- System Operations Report

Jimmy provided the System Operations Report. He said there were new ERCOT procedures posted to review.  He reviewed two that impacted the group.  He mentioned that the Time Error correction changed from 3 seconds to 30 seconds was implemented on November 1st and since then no Time Error corrections were done. The current Time Error accumulation is at 14 seconds

He also mentioned that on November 1st, System Operations started activating constraints at 98% in TCM instead of 100% loading as was in the past. He asked if anyone else had questions over the recent changes.

- Other

Biennial Reactive test data in NDCRC

Isabel Flores said that a lot of units that are due for an update started testing and the results are coming in.

Ross Owen asked Isabel to provide an update in January after most of the test results are received. He made an observation that most units are submitting curves which just meet the 0.95 Pf as required in the protocols and might not be submitting their full capability as needed for the applications to have accurate reactive information

OWG Scope Document

OWG scope document was reviewed and no updates are needed at this time

Texas RE recommendations

  - David Penny mentioned that language in the Protocols indicates real -time data for reliability purposes must be accurate within 3% percent.  Language in the Operating Guides indicates voltage is to be maintained within 2% of the voltage profile.  These requirements appear to conflict with each other, even though by the hierarchal process, the Protocols supersede the Operating Guides in this case.  Additionally, language in ERCOT’s Steady State Voltage Control Procedure states that transmission voltage should not exceed 105% nor fall below 95% of the nominal voltage during normal operation of the system and that transmission voltage during emergencies (including contingency events) should not exceed equipment over excitation ratings

OWG assigned this as an action item for OTF to review the language

  - David Penny mentioned that based on data provided by the TOs, there appeared to be instances during cycling of feeders the TOs were not meeting their load-shed obligation for brief periods of time.

OWG assigned this as an action item for OTF to review the language of the operating guides

- Future Meeting Date

Wednesday, December 19th

- Meeting Adjourned at 12:15.

Notes compiled by Vijay Betanabhatla