## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2013 R1
----> | Changes for 2013 are shown in bold red font
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on December 1, 2010. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
----> | AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
AAL value used in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.016930
F2 = 0.000400
F3 = 0.019720
AAL for ERCOT (15 mins) = 9,304
For "E" Primary Customers
F1 = 0.010920
F2 = 0.000018
F3 = 0.001970
AAL for ERCOT (15 mins) = 9,304
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
|  | Ratio of Peak to AAL |  |  |  |  | Note: Peak load and AAL
|  | CNP | ERCOT |  |  |  | went down in 2012 for
|  | 2.0304 | 1.7951 |  |  |  | both ERCOT and CNP
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2010 for use in 2011 |  | 2011 for use in 2012 |  | 2012 for use in 2013 |  | 2011/2010 | 2012/2011
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3591.25 | 14365 | 3777.5 | 15110 | 3690.75 | 14763 | 1.0519 | 0.97704
CNP AAL | 1781 | 7124 | 1859.25 | 7437 | 1817.75 | 7271 | 1.0439 | 0.97768
ERCOT Peak | 16507 | 66028 | 17104 | 68416 | 16701.5 | 66806 | 1.0362 | 0.97647
ERCOT AAL | 9034 | 36136 | 9463 | 37852 | 9304 | 37216 | 1.0475 | 0.9832
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2012 as follows:
1. Substation Transformer Losses (The A B constants for substation transformers was updated for 2013)
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
The total no-load losses are 21.111 MW, which is a slight increase from the 20.312 MW used since 2009.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
This value is 55.567 MW at 17,432 MVA, which is a slight increase from 53.531 MW used since 2009,
but it is a reduction relative to the load squared.
This results in a total of 76.678 MW of substation transformer losses at approximately 17,432 MW at CNP.
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor for 2013)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
For 2012, there is no further change in the system loss equations.
3. Distribution Transformer Losses (The A B constants for distribution transformers was updated for 2013)
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for no-load losses for a distribution system that has both old and new transformers.
The load losses from both methods were very close so the load losses from GIS were used.
Since this calculation was done in 2009, the increase in distribution transformers was determined by looking at the increase in
transformer banks for the years 2009, 2010 and 2011. This increase, approximatley 0.8% per year, was used to determine
the proportional increase in no-load losses.
The A constant for load losses was adjusted for 2012, by using the 2009 losses and adjusting the input loading to distribution
transformers to be 13,839 MW. See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses (No change in the A B constants for secondary conductor for 2013)
The constant in the system loss equation for secondary losses for 2012 is same as used in previous years.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2012 is 9,304 MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were continually adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis. The
F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2013 are also shown above.
Overall results:
For "E" Primary Customers |  |  | 2008 | 2009 | 2010 | 2011 | 2012 for use in 2013
|  | DLF at AAL | 1.267% | 1.254% | 1.254% | 1.311% | 1.291%
|  | DLF at ERCOT Peak | 2.018% | 2.039% | 2.039% | 2.131% | 2.072%
For "D" Secondary Customers |  |  | 2008 | 2009 | 2010 | 2011 | 2012 for use in 2013
|  | DLF at AAL | 3.535% | 3.681% | 3.681% | 3.663% | 3.705%
|  | DLF at ERCOT Peak | 4.034% | 4.124% | 4.124% | 4.218% | 4.178%
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162
or email at richard.moffatt@centerpointenergy.com.
CenterPoint Energy Distribution Loss Factor For 2013
October 16, 2012

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor for 2013.xls | [13 empty] | With Scaling | Using F1, F2 & F3 Coefficients |  |  | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2012 | Secondary | 2012 | 2012 | 2012 | 2012 | 2012 | Total | 2012 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 21.1122 | 28.8878 | 0.00095083 | 21.1132 | 42.23% | 28.8868 | 133.9864 | -105.0996 | 0.0039153 | 155.1035 | 310.2% | 310.2%
|  |  |  | 135 | 21.1151 | 113.8849 | 0.014778 | 21.1299 | 15.65% | 113.8701 | 133.9925 | -20.1224 | 0.00014352 | 155.1225 | 114.9% | 114.9%
|  |  |  | 500 | 21.1575 | 478.8425 | 0.26125 | 21.4187 | 4.284% | 478.5813 | 134.1015 | 344.4798 | 0.042062 | 155.5622 | 31.11% | 31.11%
1279.6039 | 5118.4156 |  | 250 | 1000 | 21.2946 | 978.7054 | 1.0914 | 22.386 | 2.239% | 977.614 | 134.4678 | 843.1462 | 0.25198 | 157.1057 | 15.71% | 15.71%
3071.0494 | 12284.1975 | 1 | 600 | 2400 | 22.165 | 2377.835 | 6.4422 | 28.6073 | 1.192% | 2371.3927 | 136.8206 | 2234.5721 | 1.7699 | 167.1978 | 6.967% | 6.967% | 6.573% | 0.9591% | 1.192% | 1.192% |  |  | 28.6073 | 167.1978
3582.8909 | 14331.5637 | 2 | 700 | 2800 | 22.5454 | 2777.4546 | 8.7895 | 31.3349 | 1.119% | 2768.6651 | 137.8499 | 2630.8151 | 2.4533 | 171.6382 | 6.13% | 6.13% | 5.813% | 0.9339% | 1.119% | 1.119% |  |  | 31.3349 | 171.6382
4094.7325 | 16378.93 | 3 | 800 | 3200 | 22.9843 | 3177.0157 | 11.5004 | 34.4846 | 1.078% | 3165.5154 | 139.037 | 3026.4784 | 3.2467 | 176.7683 | 5.524% | 5.524% | 5.266% | 0.93% | 1.078% | 1.078% |  |  | 34.4846 | 176.7683
4606.5741 | 18426.2962 | 4 | 900 | 3600 | 23.4816 | 3576.5184 | 14.5745 | 38.0561 | 1.057% | 3561.9439 | 140.3813 | 3421.5625 | 4.1497 | 182.5872 | 5.072% | 5.072% | 4.861% | 0.9404% | 1.057% | 1.057% |  |  | 38.0561 | 182.5872
5118.4156 | 20473.6625 | 5 | 1000 | 4000 | 24.0375 | 3975.9625 | 18.0118 | 42.0493 | 1.051% | 3957.9507 | 141.8824 | 3816.0683 | 5.1618 | 189.0935 | 4.727% | 4.727% | 4.556% | 0.9606% | 1.051% | 1.051% |  |  | 42.0493 | 189.0935
5630.2572 | 22521.0287 | 6 | 1100 | 4400 | 24.652 | 4375.348 | 21.8121 | 46.4641 | 1.056% | 4353.5359 | 143.5397 | 4209.9962 | 6.2825 | 196.2863 | 4.461% | 4.461% | 4.323% | 0.9882% | 1.056% | 1.056% |  |  | 46.4641 | 196.2863
6142.0987 | 24568.395 | 7 | 1200 | 4800 | 25.3249 | 4774.6751 | 25.9753 | 51.3002 | 1.069% | 4748.6998 | 145.3528 | 4603.347 | 7.5113 | 204.1643 | 4.253% | 4.253% | 4.145% | 1.021% | 1.069% | 1.069% |  |  | 51.3002 | 204.1643
6653.9403 | 26615.7612 | 8 | 1300 | 5200 | 26.0563 | 5173.9437 | 30.5011 | 56.5575 | 1.088% | 5143.4425 | 147.3211 | 4996.1214 | 8.8478 | 212.7263 | 4.091% | 4.091% | 4.008% | 1.058% | 1.088% | 1.088% |  |  | 56.5575 | 212.7263
7165.7819 | 28663.1275 | 9 | 1400 | 5600 | 26.8463 | 5573.1537 | 35.3895 | 62.2358 | 1.111% | 5537.7642 | 149.4442 | 5388.32 | 10.2914 | 221.9713 | 3.964% | 3.964% | 3.904% | 1.099% | 1.111% | 1.111% |  | 0 | 62.2358 | 221.9713
7677.6234 | 30710.4937 | 10 | 1500 | 6000 | 27.6948 | 5972.3052 | 40.6403 | 68.335 | 1.139% | 5931.665 | 151.7214 | 5779.9435 | 11.8417 | 231.8982 | 3.865% | 3.865% | 3.827% | 1.142% | 1.139% | 1.149% |  | 1 | 68.935 | 231.8982
8189.465 | 32757.86 | 11 | 1600 | 6400 | 28.6018 | 6371.3982 | 46.2532 | 74.855 | 1.17% | 6325.145 | 154.1525 | 6170.9926 | 13.4982 | 242.5057 | 3.789% | 3.789% | 3.771% | 1.187% | 1.17% | 1.19% |  | 2 | 76.135 | 242.5057
8701.3066 | 34805.2262 | 12 | 1700 | 6800 | 29.5673 | 6770.4327 | 52.2282 | 81.7955 | 1.203% | 6718.2045 | 156.7367 | 6561.4678 | 15.2605 | 253.7927 | 3.732% | 3.732% | 3.732% | 1.234% | 1.203% | 1.233% | 0 | 3 | 83.8355 | 253.7927
9213.1481 | 36852.5925 | 13 | 1800 | 7200 | 30.5913 | 7169.4087 | 58.5651 | 89.1564 | 1.238% | 7110.8436 | 159.4737 | 6951.3698 | 17.1281 | 265.7582 | 3.691% | 3.704% | 3.708% | 1.282% | 1.238% | 1.278% | 1 | 4 | 92.0364 | 266.6782
9724.9897 | 38899.9587 | 14 | 1900 | 7600 | 31.6738 | 7568.3262 | 65.2638 | 96.9376 | 1.275% | 7503.0624 | 162.363 | 7340.6994 | 19.1004 | 278.401 | 3.663% | 3.689% | 3.696% | 1.332% | 1.275% | 1.325% | 2 | 5 | 100.7376 | 280.3432
10236.8312 | 40947.325 | 15 | 2000 | 8000 | 32.8149 | 7967.1851 | 72.324 | 105.1389 | 1.314% | 7894.8611 | 165.404 | 7729.4572 | 21.177 | 291.7199 | 3.646% | 3.685% | 3.695% | 1.382% | 1.314% | 1.374% | 3 | 6 | 109.9389 | 294.7865
10748.6728 | 42994.6912 | 16 | 2100 | 8400 | 34.0145 | 8365.9855 | 79.7456 | 113.7601 | 1.354% | 8286.2399 | 168.5962 | 8117.6438 | 23.3575 | 305.7138 | 3.639% | 3.691% | 3.703% | 1.434% | 1.354% | 1.424% | 4 | 7 | 119.6401 | 310.0071
11260.5144 | 45042.0575 | 17 | 2200 | 8800 | 35.2726 | 8764.7274 | 87.5284 | 122.801 | 1.395% | 8677.199 | 171.9392 | 8505.2598 | 25.6414 | 320.3816 | 3.641% | 3.705% | 3.718% | 1.486% | 1.395% | 1.475% | 5 | 8 | 129.841 | 326.0038
11772.3559 | 47089.4237 | 18 | 2300 | 9200 | 36.5892 | 9163.4108 | 95.6724 | 132.2616 | 1.438% | 9067.7384 | 175.4324 | 8892.306 | 28.0283 | 335.7222 | 3.649% | 3.726% | 3.741% | 1.539% | 1.438% | 1.528% | 6 | 9 | 140.5416 | 342.7756
12284.1975 | 49136.79 | 19 | 2400 | 9600 | 37.9643 | 9562.0357 | 104.1773 | 142.1416 | 1.481% | 9457.8584 | 179.0754 | 9278.783 | 30.5175 | 351.7345 | 3.664% | 3.753% | 3.769% | 1.593% | 1.481% | 1.581% | 7 | 10 | 151.7416 | 360.3212
12796.0391 | 51184.1562 | 20 | 2500 | 10000 | 39.3979 | 9960.6021 | 113.043 | 152.4409 | 1.524% | 9847.5591 | 182.8677 | 9664.6914 | 33.1088 | 368.4174 | 3.684% | 3.786% | 3.802% | 1.647% | 1.524% | 1.634% | 8 | 11 | 163.4409 | 378.6396
13307.8806 | 53231.5225 | 21 | 2600 | 10400 | 40.8901 | 10359.1099 | 122.2693 | 163.1593 | 1.569% | 10236.8407 | 186.8087 | 10050.032 | 35.8016 | 385.7696 | 3.709% | 3.824% | 3.84% | 1.701% | 1.569% | 1.689% | 9 | 12 | 175.6393 | 397.7296
13819.7222 | 55278.8887 | 22 | 2700 | 10800 | 42.4407 | 10757.5593 | 131.856 | 174.2967 | 1.614% | 10625.7033 | 190.8981 | 10434.8052 | 38.5954 | 403.7902 | 3.739% | 3.867% | 3.882% | 1.756% | 1.614% | 1.744% | 10 | 13 | 188.3367 | 417.5902
14331.5637 | 57326.255 | 23 | 2800 | 11200 | 44.0499 | 11155.9501 | 141.803 | 185.853 | 1.659% | 11014.147 | 195.1352 | 10819.0119 | 41.4899 | 422.478 | 3.772% | 3.913% | 3.928% | 1.812% | 1.659% | 1.799% | 11 | 14 | 201.533 | 438.2203
14843.4053 | 59373.6212 | 24 | 2900 | 11600 | 45.7176 | 11554.2824 | 152.1102 | 197.8278 | 1.705% | 11402.1722 | 199.5196 | 11202.6526 | 44.4845 | 441.832 | 3.809% | 3.962% | 3.977% | 1.867% | 1.705% | 1.855% | 12 | 15 | 215.2278 | 459.6186
15355.2469 | 61420.9875 | 25 | 3000 | 12000 | 47.4438 | 11952.5562 | 162.7774 | 210.2212 | 1.752% | 11789.7788 | 204.0508 | 11585.728 | 47.5788 | 461.8509 | 3.849% | 4.015% | 4.029% | 1.923% | 1.752% | 1.912% | 13 | 16 | 229.4212 | 481.7842
15867.0884 | 63468.3537 | 26 | 3100 | 12400 | 49.2286 | 12350.7714 | 173.8043 | 223.0329 | 1.799% | 12176.9671 | 208.7284 | 11968.2387 | 50.7724 | 482.5337 | 3.891% | 4.07% | 4.084% | 1.98% | 1.799% | 1.969% | 14 | 17 | 244.1129 | 504.7159
16378.93 | 65515.72 | 27 | 3200 | 12800 | 51.0718 | 12748.9282 | 185.1909 | 236.2627 | 1.846% | 12563.7373 | 213.5518 | 12350.1854 | 54.0647 | 503.8793 | 3.937% | 4.128% | 4.141% | 2.036% | 1.846% | 2.026% | 15 | 18 | 259.3027 | 528.4127
16890.7716 | 67563.0862 | 28 | 3300 | 13200 | 52.9736 | 13147.0264 | 196.9371 | 249.9106 | 1.893% | 12950.0894 | 218.5206 | 12731.5688 | 57.4554 | 525.8866 | 3.984% | 4.188% | 4.2% | 2.093% | 1.893% | 2.083% | 16 | 19 | 274.9906 | 552.8733
17402.6131 | 69610.4525 | 29 | 3400 | 13600 | 54.9338 | 13545.0662 | 209.0425 | 263.9764 | 1.941% | 13336.0236 | 223.6342 | 13112.3894 | 60.944 | 548.5546 | 4.033% | 4.251% | 4.261% | 2.15% | 1.941% | 2.141% | 17 | 20 | 291.1764 | 578.0968
17914.4547 | 71657.8187 | 30 | 3500 | 14000 | 56.9526 | 13943.0474 | 221.5072 | 278.4598 | 1.989% | 13721.5402 | 228.8922 | 13492.648 | 64.53 | 571.882 | 4.085% | 4.315% | 4.324% | 2.207% | 1.989% | 2.199% | 18 | 21 | 307.8598 | 604.082
18426.2962 | 73705.185 | 31 | 3600 | 14400 | 59.0299 | 14340.9701 | 234.3308 | 293.3608 | 2.037% | 14106.6392 | 234.2941 | 13872.3451 | 68.213 | 595.8679 | 4.138% | 4.381% | 4.389% | 2.264% | 2.037% | 2.257% | 19 | 22 | 325.0408 | 630.8279
18938.1378 | 75752.5512 | 32 | 3700 | 14800 | 61.1658 | 14738.8342 | 247.5134 | 308.6791 | 2.086% | 14491.3209 | 239.8394 | 14251.4815 | 71.9925 | 620.511 | 4.193% | 4.448% | 4.455% | 2.321% | 2.086% | 2.316% | 20 | 23 | 342.7191 | 658.3333
19449.9794 | 77799.9175 | 33 | 3800 | 15200 | 63.3601 | 15136.6399 | 261.0546 | 324.4147 | 2.134% | 14875.5853 | 245.5276 | 14630.0577 | 75.8681 | 645.8105 | 4.249% | 4.517% | 4.523% | 2.379% | 2.134% | 2.374% | 21 | 24 | 360.8947 | 686.5971
19961.8209 | 79847.2837 | 34 | 3900 | 15600 | 65.613 | 15534.387 | 274.9544 | 340.5673 | 2.183% | 15259.4327 | 251.3583 | 15008.0744 | 79.8394 | 671.765 | 4.306% | 4.587% | 4.591% | 2.437% | 2.183% | 2.433% | 22 | 25 | 379.5673 | 715.6184
21369.3852 | 85477.5409 |  | 4175 | 16700 | 72.11 | 16627.89 | 315.0262 | 387.1362 | 2.318% | 16312.8638 | 268.1232 | 16044.7405 | 91.2499 | 746.5094 | 4.47% |  | 4.787% | 2.596% | 2.318%
9304 | 37216 |  | 1817.75 | 7271
15 min | ERCOT |  | 15 min | CNP | [12 empty] | Secondary | Primary
9304 | 37216 | AAL | 1817.75 | 7271 | 29.8468 | 7241.1532 | 59.7431 | 89.5899 | 1.232% | 7181.4101 | 159.9821 | 7021.428 | 17.475 | 267.047 | 3.673% |  | 3.705% | 1.291% | At ERCOT AAL
16701.5 | 66806 | Peak | 3690.75 | 14763 | 65.0085 | 14697.9915 | 246.1435 | 311.152 | 2.108% | 14451.848 | 239.2635 | 14212.5844 | 71.6001 | 622.0156 | 4.213% |  | 4.178% | 2.072% | At ERCOT Peak
18890.7925 | [14 empty] | Scaling for % Losses
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Secondary | Primary |  | 2013
(When ERCOT is at peak, CNP is 4.5 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | 0.23% | 0.21% |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor | [5 empty] | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2012 Values ----> | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  |  | 2009 Values ----> | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01693 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.0004 | middle
[17 empty] | F3 = | 0.01972 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value |  |  | F1 = | 0.01092 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 1.8e-05 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.00197 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 9,304 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below and to the right)
2013
Secondary Constants
F1 = | 0.01693 | right
F2 = | 0.0004 | middle
F3 = | 0.01972 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for 2013 DLF
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| 76.6788 = | A * (17432 * 17432) + 21.1118
| A = | 1.8286e-07
| B = | 21.1118 | Total No-Load Losses For Substation Transformers = 21.111757 MW
Total Load Losses = 55.567 MW at 17,432 MW load level
2012
[5 empty] | No Load Losses | 21.1118
[5 empty] | Load Losses | 55.567
[5 empty] | Total | 76.6788
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Distribution Transformers
| 230.524 = | A * (13,839 * 13,839) + 133.986
| A = | 5.0407e-07 | Total No-Load Losses For Distribution Transformers = 133.986 MW
| B = | 133.986 | Total Load Losses = 96.538 MW based on 13,839 MW input to Dist Trfs (corresponds to total CNP load = 14,125 MW)
2012
|  | No Load Losses |  | 133.986
|  | Load Losses |  | 96.538
|  | Total |  | 230.524
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified