Scenario 1:  Business as usual with Demand Response - 2022

New Resources:

Annual Generation Energy Mix:

Demand Response:

| City | Capacity (MW) |
| --- | --- |
|  | Industrial | Residential/Commercial |
| Austin | 60 | 275 |
| Dallas | 160 | 733 |
| Houston | 200 | 734 |
| San Antonio | 80 | 458 |

| Peak load: | Peak renewable: |
| --- | --- |
| Hour: 8/4/2022 hour 16 | Hour: 4/22/2022 hour 8 |
| System load (coincident peak): 89214 MW | System load: 49447.8 MW |
| Thermal & Hydraulic output: 86298 MW | Renewable output: 9488.8 MW |

Import limits determined by AC voltage stability analysis:

| Load Center | Interface Limits (MW) | Potential year of voltage instability | Critical Contingencies (Under G-1) |
| --- | --- | --- | --- |
| Dallas | 18890 | 2022 | Trinidad-Tricorner-Watermill |
| Houston | 8827 | 2022 | Roans Prairie-Kuykendahl & Singleton-Tomball |
| Austin / San Antonio | 3033 | 2027 | Hill Country-Marion & Skyline-Marion |
| Valley | Not tested since incremental future generation in the region will only improve the system stability. Instead, previous interface limit was imposed at 2512 MW |

Base Case Overloads:

System flows at peak load hour:                                    System flows at peak wind hour:

*All numbers are in GW

Congestion map:                                                                                Most congested Elements:

Economic Projects Tested

Economic Results

| Tested Project | Capital cost | Reliability benefit | Adjusted Capital Cost for Reliability Benefit | Production Cost Savings | 1/6 of Adjusted Capital Cost | Meet ERCOT Economic Criteria? |
| --- | --- | --- | --- | --- | --- | --- |
| Watermill-Navarro | 150.2 | -67.0 | 217.2 | 0.2 | 36.2 | No |
| Fayette-O Brien | 241.7 | -108.8 | 132.9 | 0.6 | 22.2 | No |
| Lufkin-Jordan | 430.2 | 36.7 | 466.9 | 4.1 | 77.8 | No |
| TNP One-Salem-Zenith | 444.6 | -105.3 | 339.3 | 6.2 | 56.6 | No |
| Upgrade Gibbons Creek-Singleton | 23.8 | n/a | n/a | 0.5 | 4.0 | No |
| Upgrade Green Bayou 345/138 kV | 11.9 | n/a | n/a | 2.8 | 2.0 | Yes |
| Upgrade S. Texas-Hillje, and Hillje-O’Brien | 254 | -54.1 | 199.9 | 4.1 | 33.3 | No |
| Cagnon-Miguel | 193.3 | 87.4 | 280.7 | 3 | 46.8 | No |
| Cagnon-Miguel & Cagnon 345/138 kV | 217.1 | n/a | n/a | 4.5 | 36.2 | No |
| Cagnon-Pawnee | 241.7 | 137.3 | 379.0 | 3.7 | 63.2 | No |
| Cagnon-Pawnee & Cagnon 345/138 kV | 265.4 | n/a | n/a | 4.9 | 44.2 | No |
| Kendall-Hill Country | 145 | n/a | n/a | -8.2 | 24.2 | No |
| Upgrade Elgin-Taylor | 15.3 | n/a | n/a | 1 | 2.6 | No |
| Upgrade Hill Country-Sky | 30.3 | n/a | n/a | 1.2 | 5.1 | No |
| *All numbers are in millions in 2022. |  |  |  |  |  |  |

Scenario 2:  Business as usual with retirements - 2022

New Resources                                                                   Annual Generation Energy Mix:

Retirement Resources (Natural gas units over 50 years old)

| Peak load: | Peak renewable: |
| --- | --- |
| Hour: 8/4/2022 hour 16 | Hour: 3/23/2022 hour 4 |
| System load (coincident peak): 89214 MW | System load: 38126 MW |
| Thermal & Hydraulic output: 85159 MW | Renewable output: 9281 MW |

Import limits determined by AC voltage stability analysis:

| Load Center | Interface Limits (MW) | Potential year of voltage instability | Critical Contingencies |
| --- | --- | --- | --- |
| Dallas | 19949 | 2022 | Tricorner/Watermill |
| Houston | 8735 | 2019 | Singleton-Zenith |
| San Antonio | 4048 | 2028 | Hill Country - Marion & Skyline - Marion |
| Austin | 3839 | 2028 | Elm Creek-South Texas |
| Valley | Not tested since incremental future generation in the region will only improve the system stability. Instead, previous interface limit was imposed at 2512 MW |

Base Case Overloads:

System flows at peak load hour:                                    System flows at peak wind hour:

*All numbers are in GW

Congestion map:                                                                                Most congested Elements:

Economic Projects Tested (All Black lines 345kV Double Circuit except for Hays Kendall)

Economic Results

| Tested Project | Capital cost | Reliability benefit | Adjusted Capital Cost for Reliability Benefit | Production Cost Savings | 1/6 of Adjusted Capital Cost | Meet ERCOT Economic Criteria ? |
| --- | --- | --- | --- | --- | --- | --- |
| Fayette-O Brien | 241.7 | 345.2 | -103.5 | 30.8 | -17.3 | YES |
| Lufkin-Jordan | 439.1 | 138.5 | 300.6 | 28 | 50.1 | NO |
| TNP One-Salem-Zenith | 444.6 | 520.4 | -75.7 | 37.5 | -12.6 | YES |
| Hillje-Obrien and South Texas-Hillje upgrade | 265.3 | 262.3 | 3 | 28.3 | 0.5 | YES |
| Navarro-Zenith | 597.8 | 101.1 | 496.7 | 29.7 | 82.8 | NO |
| Limestone - Gibbons Creek -Zenith | 327.2 | 361.6 | -34.4 | 40.9 | -5.7 | YES |

Scenario 3:  Business as usual with wind - 2022

New Resources

Annual Generation Energy Mix:

| Peak load: | Peak renewable: |
| --- | --- |
| Hour: 8/4/2022 hour 16 | Hour: 3/26/2022 hour 22 |
| System load (coincident peak): 89214 MW | System load: 40382 MW |
| Thermal & Hydraulic output: 84231 MW | Renewable output: 14525 MW |

Import limits determined by AC voltage stability analysis:

| Load Center | Interface Limits (MW) | Potential year of voltage instability | Critical Contingencies (Under G-1) |
| --- | --- | --- | --- |
| Dallas | 20318 | 2026 | Parker-Hicks sw/Eagle mountain |
| Houston | 9440 | 2028 | Roans Prairie-Kuykendhal & Singleton-Tomball |
| San Antonio | 3796 | 2030 | Hill Country-Marion |
| Austin | 4572 | Beyond 2032 | Elm Creek-South Texas |
| Valley | Not tested since incremental future generation in the region will only improve the system stability. Instead, previous interface limit was imposed at 2512 MW |

Base Case Overloads:

System flows at peak load hour:                                    System flows at peak wind hour:

*All numbers are in GW

Congestion map:                                                                                Most congested Elements:

Economic Projects Tested (All Black lines 345kV Double Circuit except for Hays-Kendall)

Economic Results

| Tested Project | Capital cost | Reliability benefit | Adjusted Capital Cost for Reliability Benefit | Production Cost Savings | 1/6 of Adjusted Capital Cost | Meet ERCOT Economic Criteria ? |
| --- | --- | --- | --- | --- | --- | --- |
| Limest-Gibn Crk- Zenith | 327.2 | 120.6 | 206.6 | 36.6 | 34.4 | Yes |
| Watermill-Big Brown | 208.2 | 23.1 | 185.1 | 0.1 | 30.9 | No |
| Lake Creek - Navaro | 104.1 | 42.1 | 62.0 | 1.7 | 10.3 | No |
| LakeCrk -wtm | 297.4 | 19.0 | 278.4 | 0.4 | 46.4 | No |
| Clear Spring - Hill County | 104.1 | 0.0 | 104.1 | 4.1 | 17.4 | No |
| Hays - Kendall 2nd 345kV ckt | 41.8 | 0.0 | 41.8 | 3.2 | 7.0 | No |
| Sandow - Garfield | 133.8 | 0.0 | 133.8 | 4.0 | 22.3 | No |

Scenario 5A:  Drought - 2022

New Resources

Annual Generation Energy Mix:

| Peak load: | Peak renewable: |
| --- | --- |
| Hour: 8/16/2022 hour 16 | Hour: 3/15/2022 hour 23 |
| System load (coincident peak): 92613 MW | System load: 39645 MW |
| Thermal & Hydraulic output: 82442 MW | Renewable output: 15749 MW |

Import limits determined by AC voltage stability analysis:

| Load Center | Interface Limits (MW) | Potential year of voltage instability | Critical Contingencies (Under G-1) |
| --- | --- | --- | --- |
| Dallas | 18890 | 202 | Trinidad-Tricorner/Watermill |
| Houston | 8827 | 2024 | Roan-Kuykendahl & Singleton-Tomball, Fayette-Zenith, Hillje-W.A. Parish, or South Texas-Dow |
| San Antonio | 3033 | 2028 | Hill Country - Marion & Skyline - Marion |
| Austin | 3839 | 2028 | Elm Creek-South Texas |
| Valley | Not tested since incremental future generation in the region will only improve the system stability. Instead, previous interface limit was imposed at 2512 MW |

Base Case Overloads:

System flows at peak load hour:                                    System flows at peak wind hour:

*All numbers are in GW

Congestion map:                                                                                Most congested Elements:

Economic Projects Tested (All Black lines 345kV Double Circuit except for Hays Kendall)

Economic Results

| Tested Project | Capital Cost | Reliability benefit | Capital Cost Adjusted for Reliability Benefit | Production Cost Savings | 1/6 of adjusted Capital Cost | Meet ERCOT Economic Criteria ? |
| --- | --- | --- | --- | --- | --- | --- |
| Limestone-Singleton | 163.6 | 9.7 | 153.9 | 26.1 | 25.6 | Yes |
| Watermill-Bigbrown | 208.2 | 153.0 | 55.2 | 0.6 | 9.2 | No |
| Bigbrown-Venus | 223.1 | 0.0 | 223.1 | 0.2 | 37.2 | No |
| LakeCreek-Navaro | 104.1 | 9.7 | 94.4 | 0.3 | 15.7 | No |
| Lake Creek-Watermill | 297.4 | 19.5 | 278.0 | 1.3 | 46.3 | No |
| Clear Spring-Hill Country | 104.1 | 0.0 | 104.1 | 3.1 | 17.4 | No |
| Hays-Kendall | 41.8 | 0.0 | 41.8 | 4.0 | 7.0 | No |
| Sandow-Garfield | 133.8 | 9.7 | 124.1 | 5.1 | 20.7 | No |

Scenario 7:  Business as usual with High Natural Gas Price - 2022

New Resources

Annual Generation Energy Mix:

Economic Retirement Resources

| Peak load: | Peak renewable: |
| --- | --- |
| Hour: 8/4/2022 hour 16 | Hour: 4/28/2022 hour 18 |
| System load (coincident peak): 89214 MW | System load: 58017 MW |
| Thermal & Hydraulic output: 70350 MW | Renewable output: 22252 MW |

Import and Export limits determined by AC voltage stability analysis:

| Area | Interface Limits (MW) | Potential year of voltage instability | Critical Contingencies (Under G-1 for Houston) |
| --- | --- | --- | --- |
| Dallas | 19914 | 2025 | Navarro-Watermill |
| Houston | 9267.3 | 2028 | Roans Prairie-Kuykendahl & Singleton-Tomball |
| Austin | 4579 | Beyond 2032 | Hutto-Saladoss |
| San Antonio | 3803 | 2031 | Hill County - Marion and Skyline - Marion |
| Panhandle | 6014.6 | N/A | Dermot-Cottonwood |
| Valley | Not tested since incremental future generation in the region will only improve the system stability. Instead, previous interface limit was imposed at 2512 MW |

Base Case Overloads:

System flows at peak load hour:                                    System flows at peak wind hour:

*All numbers are in GW

Congestion map:                                                                                Most congested Elements:

Economic Projects Tested

Economic Results

| Tested Project | Capital cost | Reliability benefit | Adjusted Capital Cost for Reliability Benefit | Production Cost Savings | 1/6 of Adjusted Capital Cost | Meet ERCOT Economic Criteria? |
| --- | --- | --- | --- | --- | --- | --- |
| Bowman-Benbrook | $435.0 | $ (188.90) | $623.9 | $15.0 | $104.0 | No |
| Clear Crossing-Benbrook | $531.6 | $ (145.30) | $676.9 | $30.0 | $112.8 | No |
| Parker-Benbrook | $80.5 | $ (145.30) | $225.8 | $37.0 | $37.6 | Yes |
| Wolf Hollow-Benbrook | $162.6 | $ (145.30) | $307.8 | $28.0 | $51.3 | No |
| Fayette-O'Brien | $241.7 | $ (52.33) | $294.0 | $37.0 | $49.0 | No |
| TNP One-Salem-Zenith | $444.6 | $ (73.15) | $517.8 | $232.0 | $86.3 | Yes |
| Limestone-Gibbons Creek-Zenith | $391.4 | $ (20.87) | $412.3 | $274.0 | $68.7 | Yes |
| Brown-Zenith | $860.3 | $ 25.99 | $834.3 | $236.0 | $139.0 | Yes |
| Lufkin-Jordan | $439.1 | $ 13.72 | $425.4 | $190.0 | $70.9 | Yes |
| Navarro-Zenith | $597.8 | $ (57.60) | $655.5 | $208.0 | $109.2 | Yes |
| Cagnon-Pawnee | $241.7 | $ 23.12 | $218.5 | $4.0 | $36.4 | No |
| Kendall-Hill Country-Haysen | $338.3 | $ 60.03 | $278.3 | $26.0 | $46.4 | No |
| Brown-Hill Country | $507.5 | $ 4.57 | $502.9 | $125.0 | $83.8 | Yes |
| Bakersfield-Rio Bravo | $978.7 | $ 27.40 | $951.3 | $94.0 | $158.5 | No |
| Cottonwood-Clear Crossing, Tesla-Graham 500 kV | $970.7 | $ 15.82 | $954.9 | $117.0 | $159.1 | No |
| *All numbers are in millions in 2022. |  |  |  |  |  |  |