## Slide 1: AEPSC Airline/ North Padre Island Area Improvements Project Regional Planning Group (RPG) Review; ERCOT Independent Review
Jeff Billo
Manager, Transmission Planning
TAC
ERCOT Public
January 3, 2013
1

## Slide 2: Background
American Electric Power Service Corporation (AEPSC) received ERCOT Board of Directors endorsement for projects in the Corpus Christi area in December of 2009
  Part of project set included a new 138 kV line from Barney Davis to Laguna and a 138/69 kV autotransformer at Laguna in order to meet reliability criteria
Prior to submitting the Certificate of Convenience and Necessity (CCN) application for the Barney Davis to Laguna 138 kV line, AEPSC received public comments via open house meetings and explored alternative solutions
  Routing analysis drove cost estimates higher than anticipated in 2009 analysis
Based on the public input, environmental assessment and routing analysis AEPSC concluded that an alternative project set represented a better long-term solution for the needs in the area
ERCOT Public

## Slide 3: RPG Review
AEPSC submitted revised project set for RPG Review in July 2012
ERCOT Public
Primary reliability concern:
  With one Airline 138/69 kV transformer out of service, the contingency loss of the other Airline transformer will cause a local voltage collapse
  Includes critical load at Naval Base substation
  Exposure is year-round

## Slide 4: Endorsement
ERCOT Independent Review analyzed eight options including original project set (Option 5) and AEPSC revised project set (Option 2)
  Focused on N-1-1 AC contingency reliability analysis in 2013 spring and fall peak cases
  Analyzed two future load growth sensitivity scenarios
ERCOT will request the ERCOT BOD endorse the following improvements associated with the AEPSC revised project set (Option 2):
  Construct a new 138 kV transmission line from Barney Davis to Naval Base such that the circuit Rate B is approximately 320 MVA
  Install a 138/69 kV autotransformer at Naval Base such that the circuit Rate B is approximately 165 MVA
The cost estimate for these improvements is ~ $54.7 million
ERCOT Public

## Slide 5: Comments/ Questions?
ERCOT Public
New Barney Davis-Naval Base 138 kV line
New Naval Base 138/69 kV autotransformer
Option 2 Upgrades