ERCOT Operations Report

December 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 12/10/2012 12:32 | 59.833 | 36 | Unit trip with 790 MW net online. |
| 12/12/2012 7:31 | 59.856 | 32 | Unit trip with 650 MW net online. |
| 12/13/2012 13:17 | 59.869 | 12 | Unit trip with 767 MW net online. |
| 12/14/2012 16:13 | 59.841 | 20 | Unit trip with 464 MW net online. |
| 12/14/2012 19:16 | 59.869 | 104 | Gen Deviation of 700 MW in 4 minutes |
| 12/25/2012 4:30 | 59.774 | 92 | Unit trip with 840 MW net online. |
| 12/28/2012 18:12 | 59.898 | 4 | Multiple unit trips with 316 MW net online. |
| 12/29/2012 16:24 | 59.886 | 8 | Multiple unit trips with 655 MW net online. |
| 12/10/2012 12:32 | 59.833 | 36 | Unit trip with 790 MW net online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

None

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 12/10/12 12:32:58 | 12/10/12 12:36:02 | 0:03:04 | 386.29 |  |
| 12/12/12 7:31:16 | 12/12/12 7:34:24 | 0:03:08 | 299.82 |  |
| 12/13/12 13:17:18 | 12/13/12 13:20:04 | 0:02:46 | 247.62 |  |
| 12/14/12 16:13:10 | 12/14/12 16:17:02 | 0:03:52 | 684 |  |
| 12/14/12 19:16:26 | 12/14/12 19:21:26 | 0:05:00 | 668.63 |  |
| 12/25/12 4:30:26 | 12/25/12 4:35:06 | 0:04:40 | 861.67 |  |
| 12/28/12 18:12:34 | 12/28/12 18:15:50 | 0:03:16 | 272.04 |  |
| 12/29/12 16:24:22 | 12/29/12 16:28:10 | 0:03:48 | 441.21 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outagesRemedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Asphalt Mines – Uvalde AEP & Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138kV | 14 | N |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 13 | N |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg AEP 138 kV | 12 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Orlando - Vernon 138 kV | 10 | N |
| Aspermont AEP - Spur 138 kV | Wolfgang - Rotan 69 kV | 10 | N |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 10 | N |
| Midland East - Moss Switch 345 kV | General Tire Switch - Southwestern Portland Tap 138 kV | 9 | N |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 9 | N |
| Basecase | Laquinta - Lobo 138 kV | 6 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Abilene Mulberry Creek - Oklaunion 345 kV | 5 | N |
| North Edinburg - Lon Hill 345 kV | Las Pulgas - Rio Hondo 138kV | 5 | N |
| Graham East - Graham Switch & Graham SES 138kV | Graham Switch - Graham 69kV | 5 | Y |
| Basecase | Ena Snyder Wind - Wkn_Bkr 69 kV | 4 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Cisco - Leon Switch 138 kV | 4 | N |
| North Edinburg - Lon Hill 345kV | North Edinburg - Rachal 138 kV | 4 | N |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney TNP 138 kV | 4 | Y |
| Pawnee Switching Station - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 4 | N |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Lewisville Switch - Jones Street TNP 138 kV | 3 | N |
| Comanche Switch (Oncor) - Comanche Peak SES 345 kV | Comanche Switch (Oncor) - Comanche Tap 138 kV | 3 | N |
| DCKT Sam Switch - Venus Switch 345 kV | Whitney Axfmr2 138/69 kV | 3 | N |
| Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345kV | 3 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Paint Creek - Murray Switch 138 kV | 2 |  |
| North Edinburg - Lon Hill 345 kV | Yturria Sub - Raymondville 2 138 kV | 2 |  |
| North Edinburg - Lon Hill 345 kV | Las Pulgas - Raymondville 2 138kV | 2 |  |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Nelson Sharpe 138 kV | 2 |  |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69 kV | 2 |  |
| DCKT Limestone - Navarro 345 kV | Big Brown SES - Jewett 345 kV (50) | 2 |  |
| DCKT Hackberry - Norwood Switch & Carrollton Northwest 345 kV | DFW D-East 1 - DFW C-East 138 kV | 2 |  |
| Big Spring West - Big Spring Air Park & Big Spring Switch 138 kV | Martin Capacitor - Stanton East 69 kV | 2 |  |
| DCKT Salado Switch - Killeen Switch 345 kV | Belton - Belton Southwest 138 kV | 2 |  |
| Sacroc - Sun Switch & Snyder 138 kV | Sun Switch - Morgan Creek SES 138 kV | 2 |  |
| Midland East Axfmr1h (3) 345/138 kV | Moss Switch Axfmr1h 345/138 kV | 2 |  |
| Fort Worth Substation - West Denton 138 kV | Jim Christal Substation - North Denton Interchange 138 kV | 2 |  |
| DCKT Skyline - Calaveras 345 kV | Cagnon Axfmr4L (3) 345/138 kV | 2 |  |
| Laquinta - Lobo 138 kV | Falfurrias 138_69A1 138/69 kV | 2 |  |
| Cagnon Axfmr3h (3) 345/138 kV | Cagnon Axfmr4h (3) 345/138 kV | 2 |  |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345kV (260_A) | 2 |  |
| Weatherford Switch - Oran Sub 138 kV | Oran Sub Axfmr2L 138/69 kV | 2 |  |
| DCKT Paris Switch - Valley SES And Valley South 345 kV | Paris Switch Axfmr1h (3) 345/138 kV | 2 |  |
| Salt Creek Bepc - Spur And Scurry Switch 138 kV | Wolfgang - Rotan 69 kV | 2 |  |
| Basecase | Snyder Axfmr1 138/69 kV | 1 |  |
| North Edinburg - Lon Hill 345kV | Laquinta - Lobo 138 kV | 1 |  |
| Graham East - Graham Switch & Graham SES 138kV | Olney Xfmr22 138/69 kV | 1 |  |
| Bosque Switch - Whitney 138 kV | Lake Whitney TNP - Whitney 138kV | 1 |  |
| DCKT Limestone - Navarro 345kV | Navarro - Big Brown SES 345kV (10) | 1 |  |
| DCKT Limestone - Navarro 345kV | Twin Oak Switch - TNP One Plant 345kV (261_A) | 1 |  |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Jones Street TNP - Lakepointe TNP 138kV | 1 |  |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 1 |  |
| DCKT Roans Prairie - Kuykendahl - King and Singleton - Tomball 345 kV | Singleton - Zenith 345 kV (SNGZEN99) | 1 |  |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Fort Worth Substation - Teasley Substation 138kV | 1 |  |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Jim Christal Substation - North Denton Interchange 138 kV | 1 |  |
| DCKT Valley South - Valley SES & Paris Switch 345kV | Paris Switch Axfmr1h (3) 345/138 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | Morgan Creek SES Axfmr1h (3) 345/138kV | 1 |  |
| Gibbons Creek - Singleton 345 kV (SNGXGC75) | Gibbons Creek - Singleton 345 kV (SNGXGC99) | 1 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Marion 24AT2 345/138 kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345kV | Coleto Creek - Kennedy Switch 138kV | 1 |  |
| DCKT Gabriel - Glasscock LCRA & Rivery 138kV | Marshall Ford - Lago Vista 138kV | 1 |  |
| Barton Switch - Graham Switch 138kV | Advance - Shady Grove 69kV | 1 |  |
| Big Lake - Twin Buttes 138 kV | San Angelo Concho - San Angelo Mathis Field 69 kV | 1 |  |
| Odessa Ehv Switch - Longshore Switch 345kV | Morgan Creek SES Axfmr1h (3) 345/138 kV | 1 |  |
| Meadow Sub – PH Robinson 345 kV | Hastings TNP - Friendswood TNP 138 kV | 1 |  |
| Vernon 138_69t1 138/69 kV | Lake Pauline 138_69_1 138/69 kV | 1 |  |
| DCKT Longshore Switch - Quail Switch & Morgan Creek SES 345 kV | Morgan Creek SES Axfmr1h 138/69 kV | 1 |  |
| Whitepoint 345A 345/138 kV | Sinton - Skidmore 69 kV | 1 |  |
| Cisco - Putnam 138kV & Leon Switch 138 kV | Putnam 138kV - Leon Switch 138 kV | 1 |  |
| DCKT Comanche Peak SES Units 1 & 2 | Laquinta - Lobo 138 kV | 1 |  |
| DCKT Odessa Ehv Switch - Longshore Switch & Quail Switch 345 kV | Morgan Creek SES Axfmr1h (3) 345/138 kV | 1 |  |
| Coleto Creek - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 1 |  |
| DCKT Morgan Creek SES - China Grove Switch 138 kV | Morgan Creek SES Axfmr3h 138/69 kV | 1 |  |
| Nursery Sub - Sam Rayburn Switching Station 69 kV | Danevang Switching Station - Plainview Sub 69 kV | 1 |  |
| Bosque Switch - Whitney 345 kV | Elmot Axfmr1L (3) 345/138 kV | 1 |  |
| DCKT Willow Creek Switch - Parker Switch 345 kV | Fort Worth Substation - Teasley Substation 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | Laquinta - Lobo 138 kV | 1 |  |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu_Jack_Creek 345 kV | 1 |  |
| DCKT Twin Buttes - Brown Switch & San Angelo Red Creek 345 kV | Twin Buttes T1H (3) 345/138 kV | 1 |  |
| DCKT Cagnon - Kendall 345kV and Cisco - Helotes 138 kV | Medina Lake - Tally_Rd 138kV | 1 |  |
| DCKT Euless To Liggett Switch 138kV | DFW D-East 1 - DFW C-East 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which made our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 19 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

12/19 	Barney Davis SPS was modified.

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

12/26 10:00 45,577 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | 2.51 |
| March | 3.24 | 2.24 | 2.02 | 3.49 |
| April | 2.66 | 2.47 | 3.55 | 2.78 |
| May | 2.90 | 2.63 | 3.27 | 3.09 |
| June | 2.89 | 2.84 | 2.28 | 2.85 |
| July | 2.83 | 2.39 | 1.63 | 2.85 |
| August | 3.07 | 2.29 | 2.28 | 2.96 |
| September | 3.68 | 3.14 | 2.70 | 3.43 |
| October | 2.92 | 2.37 | 3.51 | 2.99 |
| November | 1.93 | 3.46 | 3.38 | 2.90 |
| December | 3.70 | 2.60 | 2.99 | 3.47 |
| Annual Average | 3.11 | 2.83 | 2.83 | 3.02 |

OCN, Advisory, Watch & Emergency Notices

Capacity

None

Transmission Watch

12/4 14:34 	ERCOT issued a transmission watch for Rio Grande Valley area. The watch was cancelled at 20:12.

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None