| PGRR Number | 023 | PGRR Title | Contingency Filing Requirements |
| --- | --- | --- | --- |
| Date Posted |  | October 10, 2012 |  |

| Requested Resolution | Normal |
| --- | --- |
| Planning Guide Section Requiring Revision | 6.9, Contingency Filing Requirements (new) |
| Protocol Section(s) Requiring Revision | None. |
| Revision Description | This Planning Guide Revision Request (PGRR) adds a requirement for Transmission Service Providers (TSPs) to submit and annually review a list of contingencies for their portion of the ERCOT System. The language ensures that the appropriate contingencies are being submitted for ERCOT and North American Electric Reliability Corporation (NERC) planning criteria. |
| Reason for Revision | There are currently no requirements in the Protocols or Market Guides for TSPs to submit their contingency lists. The contingency definitions are critical for planning the ERCOT System. |

Business Case

| Business Case | 1 | Requires TSPs to submit the appropriate contingencies for planning analysis which should ensure reliable planning of the ERCOT System. |
| --- | --- | --- |

| Sponsor |  |
| --- | --- |
| Name | Sergio Garza on behalf of the Planning Working Group (PLWG) |
| E-mail Address | Sergio.garza@lcra.org |
| Company | LCRA |
| Phone Number | (512) 578-4149 |
| Cell Number |  |
| Market Segment | Cooperative |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512-248-4513 |

Proposed Guide Language Revision

6.9	Contingency Filing Requirements

(1)	Each Transmission Service Provider (TSP), or its Designated Agent, shall provide updates to the ERCOT list of steady-state contingencies corresponding to the steady-state base cases for its’ existing system and planned future Transmission Facilities and posts the list to the Planning and Operations Information website.  The list shall be reviewed and updated to coincide with changes made to the steady-state base cases, per the schedule for updating the Steady State Working Group (SSWG) base cases.  The list shall contain the following contingencies:

(a) 	North American Electric Reliability Corporation (NERC) Category B contingencies not covered by automatic contingency processing capabilities of the various power-flow applications;

(b) 	Contingencies representing the Forced Outage of a double circuit (two circuits on the same structures in excess of 0.5 miles in length); and,

(c)	Severe impact NERC Category C and D contingencies for the TSP’s portion of the ERCOT System.