## Sheet1
Operations and Planning Synchronization Task Force - Issues List Matrix
# |  | Description | Status | ISSUE RESOLUTION
1 | Consider use of an Operations feedback loop (e.g. monthly report to the ROS) to identify and address credible scenarios for further study.
| a | Transmission elements associated with an ERCOT Transmission Watch. | In Progress | The current practice of publishing a list of Transmission Watches in the monthly ERCOT Operations Report plus the implementation of NPRR393 should be adequate to alert Transmission Planners to perform studies if needed.
| b | Transmission elements that are chronically denied Maintenance Outages. | In Progress | Transmission Planners should periodically confer with Operators to create a list of circuits that are difficult to take out of service and then perform appropriate studies to aid the outage request process.
| c | Congestion analysis for constraints that are consistently causing security violations similar to the concepts in NPRR393. | In Progress | Implementation of NPRR393 will provide the congestion analysis that Transmission Planners need to identify constraints that require study.
| d | Real-time developed mitigation plans requiring load-shed for a credible single contingency, including duration of event and amount of planned load shed. | Complete | Add an extra column to the ROS Operations Report to indicate that the Mitigation Plan (MP) for SCED congestion required a load shed plan.
| e | When ERCOT performs outage analysis, if redispatch of generation is needed to avoid congestion, then that information should be made known to the TSP. This would enable TSPs to voluntarily reschedule the outages if there is flexibility in doing so. Learning about generation redispatch costs after the fact is of limited value. | Complete | ERCOT is already doing this by sending the requesting TSP a questionnaire if the ERCOT study detects an operational constraint. This alerts the TSP that generation redispatch will be needed to avoid congestion.
| f | Each ERCOT developed TOAP should be posted on the Nodal MIS on or before the effective date (preferably when outage is approved) and should include information such as the underlying scheduled outage that it is associated with and its date range, as well as, relevant load and generation unavailability assumptions used in its development. | In Progress | ERCOT believes it will be difficult to manage this on the MIS. Nonetheless, ERCOT reps on the OPSTF will discuss this with their Outage Coordinators and report back to OPSTF. TOAPs associated with forced outages & done on the fly may not be posted.
| g | ERCOT to report transmission clearance related congestion in more detail including the underlying scheduled outage, the congestion rents associated with the clearances, and the associated TOAP description, if applicable, as well as a basic description of which actual conditions were more stressful than study conditions. | In Progress | OPSTF believes the implementation of NPRR393 will go a long way toward meeting this need. Also, much of this is already being reported in the monthly Operations and Planning reports to ROS. For example, congestion rents are in the Planning report while outages are in the Operations report.
2 | Ensure that Real-Time Operations, Outage Planning and Transmission Planning processes are aligned in the use of operating generic transmission limits. |  | In Progress | GTLs reflect market based limits for studies that are economic in nature. Transmission planners need to respect SOLs & IROLs for reliability studies, but if studying congestion the lower GTL limits should be used.
3 | Consider clarifications and improvements to the Five Year Transmission Plan process. |  | In Progress
| a | Consistent publication date for Five Year Transmission Plan. | " | Others are writing a PGRR that will propose the 5-Yr Plan be completed by Dec. 31 each year.
| b | Consideration of incomplete Five Year Transmission Plan reliability projects in seasonal RAP/MP/SPS development. | " | ERCOT Sys. Planning to make internal process changes to push TSPs for RAP/MP/SPS development and will formalize this in the 5-Yr Plan process or scoping document.
| c | Exempt RPG review of Five Year Transmission Plan reliability projects that have an estimated cost less than $50M. | " | ERCOT planning disagrees and believes others need the opportunity to comment during the RPG process.
| d | Define and implement an urgent RPG review process for all Five Year Transmission Plan reliability projects that have a need date of less than 36 months. | " | ERCOT planning believes this is essentially being done since TSPs are initiating projects & ordering equipment before the 5-Yr Plan is completed.
| e | Ensuring projects in the Five Year Transmission Plan are completed in a timely manner. This includes unforeseen consideration of load variability, transmission outages and construction complexities that may require earlier completion. | " | This goal should be achieved when the 95% threshold is implemented along with the Year 6 SSWG base case.
4 | Appropriate ratings
| a | Ensure Load and Ratings assumption consistency. | In Progress | During extreme weather conductor ratings decrease and planners should compensate by monitoring a lower line loading threshold like 95% of ratings.
| b | Should SCED be limited by 2-hour ratings or make use of 15-minute ratings? | In Progress | The ERCOT Operations "DRAP" improvement should solve this issue.
| c | Should planning studies be more conservative by using the planning normal rating (Rate A) for a select set of contingencies? | In Progress | OPSTF is seriously considering a proposal to revise the Planning Guides to propose improvements when line loadings reach 95% verses 100% of ratings.
| d | Use of dynamic ratings in planning studies. | In Progress | Most lines in ERCOT are modeled with dynamic ratings in the Operations Model. Lines are not dynamically rated in ERCOT reliability studies, but are dynamically modeled in economic (UPLAN) studies.
5 | Appropriate load levels to consider in planning studies
| a | Ensure that area load forecasts in the planning base cases are aligned with actual area peak loads. | Complete | OPSTF recommended that TSPs model the 90th percentile load forecast in SSWG base cases. ROS did not approve the proposal.
| b | Establish a basis for load variations, including area seasonal variations. | In Progress | For small local areas and load pockets planners may model the undiversified load level as a reasonable load variation. For regional or weather zone load variations, planners may model the 90th percentile load forecast. A PGRR may be required to implement this language.
| c | Review the planning process relative to validating load forecasting inputs of discrete load additions and determine whether process improvements need to be made. | In Progress | There needs to be an oversight/validation procedure in place within the RPG or ALDR processes to determine when load projections & transmission improvements should be allowed in SSWG base cases. Many ISOs outside ERCOT have a load interconnection process where this issue could be handled.
6 | Use of double circuit contingencies to develop operating limits – ERCOT Operations conservatively considers all double circuit contingencies. Evaluate appropriate use of double circuit contingencies. |  | In Progress | OPSTF discussed a proposal that an DCKT outage be considered only if it caused a reliability problem. The 'push-back' was that it is hard for the market to model contingencies that are sometimes run and sometimes not. ERCOT commented that this would be complex, burdensome and require new tools for Sys. Operations.
| b | In a SCED run, consider not redispatching generation for double circuit outages pre-contingency, as long as the loading is below the 15 minute rating and it can be decreased with online generation. In other words, make redispatch of online generation a valid Mitigation Plan for loading problems due to double circuit outages. Limits can be placed on its use such as: | In Progress | ERCOT systems are not capable of making redispatch of online generation a valid Mitigation Plan…a major system change would be required.
|  | · The loss of the circuit or transformer should not lead to a cascading outage | " | "
|  | · The needed responsive reserve should be carried on two or more generation units and should be deliverable within 15 minutes | " | "
7 | Long-term unavailability of autotransformers |  | Complete | OPSTF recommended that N-1-1 studies be run for 345 kV autotransformers and that the PLWG develop a PGRR. Approved by ROS 9-13-2012.
| a | N-1-1 for autotransformers as a credible contingency for which load interruption is not allowed.
| b | Use of defined spare equipment strategy as mitigation for N-1-1 scenario.
| c | Use of defined distribution feeder switching or distribution transformer loading strategy as mitigation for N-1-1 scenario.
8 | Generator unit unavailability and modeling issues
| a | Combined cycle trains as a credible single contingency for which load interruption is not allowed. | In Progress | This issue may already be covered in the Planning Guides.
| b | Use of “typical” or “historical” Planned, Maintenance and Forced Outages and/or derates in an area. | In Progress | Implemenation of the 95% threshold should handle the threat associated with this issue.
| c | Use of extreme generator unit unavailability in an area and/or ERCOT-wide. | In Progress | While it's hard to define all key extreme events, ERCOT should add this step to its bi-annual 10-Yr (LTSA) study.
| d | Unavailability of intermittent resources in an area. | In Progress | Others are developing a PGRR to address this issue.
| e | Ensure alignment of anticipated maximum output from RARF submittals, operational tests and Pmax used in the planning base cases. | In Progress | OPSTF has concerns that Gross values are being used for PMAX in SSWG base cases when Net Values are needed.
9 | Consideration of transmission maintenance outages in planning studies. |  | In Progress | Issue 9 supports TSP efforts to justify projects based on the difficulties involved in obtaining planned outages for specific lines. No PGRR needed as ERCOT Guides & NERC Standards require known outages to be modeled in planning studies. Planners should use input from Operators and new N-1-1 PSS/E scanning feature to identify difficult planned outages that require study before outage requests are submitted.
| a | Use of “typical” or “historical” Planned, Maintenance and Forced Outages in an area. | " | "
| b | Use of construction related outages in determination and timing of planning solutions. | " | "
10 | Security-constrained deliverability of ancillary services – determine a methodology to account for ancillary service requirements in the generation dispatch or load response in planning and operating studies. |  | In Progress | On 11-28-12 OPSTF briefly discussed this issue. Modeling A/S in UPLAN runs the gen further up the dispatch stack which raises congestion costs reported in study results.
11 | Simultaneous feasibility of generation dispatch solutions – ensure planning studies adequately anticipate operational constraints. |  | In Progress | This issue refers to using re-dispatch to solve a problem without causing another problem. ERCOT is doing this in its 5-Yr Plan study using UPLAN and PowerWorld (not available in PSS/E).
12 | Planning Cases and Scenarios. |  | In Progress
| a | Model voltage regulation at actual reference point (typically the generator bus). | " | Planners model regulation at the hi-side POI as required by the Protocols and Stability Studies. But real-world gen regulates the low-side with the result that during contingencies actual gen voltage support is less than what planners see in their models.
| b | Accurate reactive modeling of generation (mainly wind) resources – use reactive capability curve instead of maximum values. | " | There is concern that reactive Test Data is not getting into the SSWG base cases.
| c | Accurate modeling of reactive loads as seen from the transmission system. | " | Issue still being researched. ALDR instructions require that pf data be taken where the meter is located.
13 | RMR Studies. |  | Complete | NPRR465 submitted by Centerpoint Energy and reviewed by OPST. August, 2012 ROS recommendation and endorsement.
| a | Consider generator unit unavailability in RMR studies.
| b | Consider expanding RMR studies for future year generator unit unavailability.