| NOGRR Number | 105 | NOGRR Title | Generation Resource Frequency Response Test Procedure |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Recommended Approval |
| Date of Decision |  | January 10, 2013 |  |
| Proposed Effective Date |  | Upon system implementation. |  |
| Priority and Rank |  | Priority – 2013; Rank - 840 |  |
| Nodal Operating Guide Section Requiring Revision |  | 8, Attachment C, Turbine Governor Speed Tests |  |
| Protocol Section(s) Requiring Revision |  | None. |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds a Governor test form for Controllable Load Resources and proposes minor corrections to calculations. |  |
| Reason for Revision |  | To correct errors in equations and to add Controllable Load Resources to the test forms and procedures. |  |
| Procedural History |  | - On 10/30/12, NOGRR105 was posted. - On 11/13/12, ERCOT comments were posted. - On 11/14/12, the Operations Working Group (OWG) considered NOGRR105. - On 12/18/12, an Impact Analysis was posted. - On 12/19/12, OWG considered the 11/14/12 OWG Report and Impact Analysis for NOGRR105. - On 1/10/13, ROS considered NOGRR105. |  |
| OWG Decision |  | On 11/14/12, the OWG was in consensus to recommend approval of NOGRR105 as amended by the 11/13/12 ERCOT comments and as revised by OWG. On 12/19/12, OWG was in consensus to endorse and forward the 11/14/12 OWG Report as revised by OWG and Impact Analysis for NOGRR105 to ROS with a recommended priority of 2013 and rank of 840. |  |
| Summary of OWG Discussion |  | On 11/14/12, the 11/13/12 ERCOT comments were discussed. On 12/19/12, it was stated that Generation Resources will be allowed, at ERCOT’s discretion, to perform frequency tests during Off-Line status. |  |
| ROS Decision |  | On 1/10/13, ROS unanimously voted to recommend approval of NOGRR105 as recommended by OWG in the 12/19/12 OWG Report. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 1/10/13, there was no discussion. |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | Corrections to the formulas will benefit Resources. |
|  | 2 | Controllable Load Resources have an increase in options for submitting testing data required by the Protocols. |

| Sponsor |  |
| --- | --- |
| Name | David Kee on behalf of the Performance, Disturbance, Compliance Working Group (PDCWG) |
| E-mail Address | dekee@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | 210-353-6912 |
| Cell Number | 210-667-5206 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512-248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 111312 | Proposed corrections to equations throughout Section 8C to reflect the changes proposed by the PDCWG. |

Proposed Guide Language Revision

ERCOT Nodal Operating Guides

Section 8

Attachment C

Turbine Governor Speed Tests

Table of Contents:  Section 8C

Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor	3

Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor	6

Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor	8

Definitions	10

Generation resource Frequency Response Test Procedure	11

Generation resource FREQUENCY RESPONSE TEST FORM	14

HISTORICAL GENERATION RESOURCE or controllable load resource FREQUENCY RESPONSE TEST FORM	17

Intermittent renewable resource (IRR) Frequency Response Test Procedure	19

Intermittent renewable resource (IRR) FREQUENCY RESPONSE TEST FORM	21

Controllable load resource Frequency Response Test Procedure	22

Controllable load resource FREQUENCY RESPONSE TEST FORM	24

# Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County):

Unit Name:  					Date of test:

QSE:						Resource Entity:

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the Governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM |  |  |  |  |  |  |
| Frequency Hz |  |  |  |  |  |  |

Speed Changer Travel Time:

(a)	From Low-Speed Stop to High-Speed Stop in _________seconds.

(b)	From High-Speed Stop to Low-Speed Stop in _________seconds.

Over-speed Trip Test Speed at _________rpm.

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Representative:

# Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600=3850−3570×1003600=7.78%

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600=3600−3310×1003600=8.06%

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the Governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600=3500−3210×1003600=8.06%

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the Governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM | 3850 | 3570 | 3600 | 3310 | 3500 | 3210 |
| Frequency Hz | 64.2 | 59.5 | 60.0 | 55.0 | 58.3 | 53.5 |

Speed Changer Travel Time:

(a)	From low-speed stop to high-speed stop in 	73	seconds.

(b)	From high-speed stop to low-speed stop in 	74	seconds.

Over-speed trip test speed at 	3965	rpm.

Comments:

# Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County):

Unit Name:  					Date of test:

QSE:						Resource Entity:

Turbine Governor Speed Regulation Test Procedures

(a)	Simulate unit On-Line and turbine speed at 3600 RPM.

(b)	Set Load reference at minimum value.

(c)	Monitor valve demand signal and record as value “A” (in %).

(d)	Reduce speed until valve demand just reaches maximum value.
Record valve demand as value “B” (in %) and speed as value “C” (in RPM).

(e)	Set speed at 3600 and Load reference at maximum value.

(f)	Monitor valve demand signal and record as value “D” (in %).

(g)	Increase speed until valve demand just reaches minimum value.
Record valve demand as value “E” (in %) and speed as value “F” (in RPM).

Turbine Governor Speed Regulation Test Results

|  | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Valve Demand (%) |  |  |  |  |  |  |
| Speed (rpm) |  |  |  |  |  |  |

Speed Regulation With Decreasing Speed

RD=100B−A×3600−C3600×100

Speed Regulation With Increasing Speed

RI=100D−E×F−36003600×100

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Representative:

# Definitions

| System Frequency Response | This response is a function of two key variables: the Primary Frequency Response from Governors and Load dampening of the connected Load. |
| --- | --- |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no Load to full Load. It is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead-Band | The range of deviations of system frequency (+/-) that produces no turbine Governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| Valve Position Limiter | A device that acts on the speed and Load governing system to prevent the Governor-controlled valves from opening beyond a pre-set limit. |
| Blocked Governor Operation | Operating the generating unit with the control system adjusted to prevent the turbine governor from responding to system frequency (speed) variations. In an effort to reduce speed Governor operation in some generating units, turbine control systems can be adjusted to block the operation of the Governor after the unit is in parallel with the system and is running at its desired output. Selection of a high percent droop characteristic or a large Governor Dead-Band constitutes a form of blocked Governor action. |
| Variable Pressure Operation | Varying the boiler pressure to improve turbine efficiency at lower Loads. Two methods are normally used. The first method, the turbine control (G.E.) or Governor (Westinghouse) valves are positioned in the wide-open position and the generator is changed by changing the boiler pressure. With this method, there is very little, if any response to frequency excursions. The second method, the valves are positioned at approximately 50% open. The valves are still able to respond to system disturbances. Normal changes in generation requirements are made by varying the boiler pressure until the unit is at rated pressure. After full pressure is reached, the turbine valves are used to make the required generation changes. |

# Generation resource Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Generation Resource is tested On-Line at a Load level that allows the Generation Resource to increase or decrease Load without reaching low operating limits or high operating limits.  If the Generation Resource cannot be tested On-Line then it will notify ERCOT that it will be conducting an Off-Line test.  The recommended level is 92% Base Load or below.

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded and signal “Generation Resource Frequency Response On” becomes active.

4.	The following signals should be recorded at least two seconds:  Unit MW Output, “Generation Resource Frequency Response On.”

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the Generation Resource should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Droop shall be set not to exceed 5% with a maximum frequency Dead-Band of +/- 0.036 Hz.

Definitions

Generation Resource Base Load = maximum Load capability for the season when frequency response test is performed

Gain MW for 0.1Hz = P(Droop∗60−GovernorDead−Band)∗10P∗10Droop∗60

Where:

P = Generation Resource Base Load (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz (+12 rpm and -12 rpm, for 3600 sync speed machines), outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz *10*Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = Combustion Turbine Base Load (MW)

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

Combustion Turbine Base Load = 150 MW

Droop = 0.05 or 5% (use 0.05 for calculation)

Governor Dead-Band = 0.036

Gain MW to 0.1 Hz = 150∗105∗60150[(0.05∗60)−0.036]∗10 = +/- 5.06 MW/0.1 Hz

MW Contribution = 5.06*10*+/- (0.2) = +/-10.12 MW

Expected under-frequency response:	 +10.12 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response: 	-10.12 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response: +7.08 MW in 15 sec. for -0.2 Hz offset

Minimum accepted over-frequency response:    -7.08 MW in 15 sec. for +0.2 Hz offset

Calculated droop for 8 MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated droop = -150∗−0.260∗8 = 0.0625 or 6.25%

# Generation resource FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | CT Base Load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  ____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Representative: __________________________	______

Generation Resource and controllable load resource Primary Frequency Response test Procedures Based on Historical Data

Description of Historical Verification

The purpose of this template is to allow the Entity that operates a Generation Resource or a Controllable Load Resource to demonstrate acceptable frequency response of its Generation Resource(s) or Controllable Load Resource(s) based on historical data in order to minimize testing costs, scheduling conflicts and the risk of damage to equipment or Forced Outage.

1.	All verifications will be based on at least one of the Performance, Disturbance, Compliance Working Group’s (PDCWG’s) list of Measurable Events as defined in the Protocols.  Different turbines can be tested using different events.

2.	For clarification purposes, the A, B, B+30 and C points are defined in Protocol Section 8.5.2, Primary Frequency Response Measurements.  Point A will be considered the start of the verification process.  The exact time of each Point is identified in the PDCWG Disturbance Report on the event.

3.	The following signals should be recorded at EMS scan rate:  Unit MW Output and ERCOT Actual Frequency from the PDCWG Disturbance Report on the event.

4.	The verification is considered successful if 70% of the calculated MW contribution is delivered at B point and maintained for an additional 30 seconds.

5.	Droop should be set not to exceed 5% and a maximum frequency Dead-Band of +/- 0.036Hz.

6.	On request, ERCOT Operations will supply frequency data and time of each evaluation point (A, C, B & B+30) for the event data chosen for the test.

7.	Intermittent Renewable Resources (IRRs) located behind one point of interconnection, metered by one ERCOT-Polled Settlement (EPS) Meter, and operated as an integrated Facility may combine IRRs for the purposes of this test.

Definitions

Generation Resource Base Load = maximum rated capability (this value is not reduced for temporary output limitations of the Generation Resource due to auxiliary equipment outages, weather conditions, or fuel limitations, it is the “nameplate” rating of the Generation Resource).  For the IRR, the Base Load for purposes of this test shall be the Real-Time telemetered High Sustained Limit (HSL) (MW) of the IRR at the time of the Measurable Event.  The IRR shall use only a Measurable Event in which the IRR’s HSL is greater than 50% of the IRR’s total design output capability.

Gain MW for 0.1Hz = P∗10Droop∗60P(Droop∗60−GovernorDead−Band)∗10

Where:

P = Generation Resource or Controllable Load Resource Base Load (MW)

Droop 	= droop (%)

Calculated droop = - P∗ΔHzC,B,B+3060∗ΔMWC,B,B+30

Where:

P = Generation Resource or Controllable Load Resource Base Load (MW)

ΔHz = Change in frequency (Hz) between Point A and Point C, B, B+30, taking into account Governor Dead-Band

ΔMW = Change in power output (MW) between Point A and Point C, B, B+30

Example

Generation Resource

Base Load = 150 MW

Governor Dead-Band = 0.036 Hz

Droop = 0.05 or 5% (use of 0.05 for calculation)

Frequency is 0.1 Hz outside of Governor Dead-Band at Point C, B, or B + 30

Gain MW = 150∗105∗60150[(0.05∗60)−0.036]∗10 = +/-5.06 MW/0.1 Hz

Expected under-frequency ∆MW:	 +5.06 MW in 15 sec. for -0.1 Hz offset

Expected over-frequency ∆MW: 	-5.06 MW in 15 sec. for +0.1 Hz offset

Minimum accepted under-frequency ∆MW: +3.54 MW in 16 sec. for -0.1 Hz offset

Minimum accepted over-frequency ∆MW:    -3.54 MW in 16 sec. for +0.1 Hz offset

Calculated droop for 5 MW increase in power output in 16 sec. for -0.1 Hz offset:                  Calculated droop = -150∗−0.160∗5 = 0.05 or 5.00%

# HISTORICAL GENERATION RESOURCE or controllable load resource FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 			Location (County):

Unit Name: 					Date of Event:

QSE: 						Resource Entity:

Historical Results

| Evaluation Point | Time | Frequency |
| --- | --- | --- |
| Point A |  |  |
| Point C |  |  |
| Point B |  |  |
| Point B+30 |  |  |

| 1 | Generation Resource Base Load |  |
| --- | --- | --- |
| 2 | MW at A Point |  |
| 3 | MW at B Point |  |
| 4 | MW at B + 30 Point |  |
| 5 | MW at C Point |  |
| 6 | Rated MW at B Point |  |
| 7 | Rated MW at B+30 Point |  |
| 8 | Response at B Point (MW) |  |
| 9 | Response at B+30 Point (MW) |  |
| 10 | Per Unit (PU) Response at B point |  |
| 11 | Per Unit (PU) Response at B+30 Point |  |
| 12 | (PASSED/FAILED) Pass if #10 & #11 ≥ 0.70 , else Fail |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  _______________________________________

QSE Representative:  ________________________________________________

Date submitted to ERCOT Representative:

# Intermittent renewable resource (IRR) Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Intermittent Renewable Resource (IRR) is tested On-Line at a Load level that allows the IRRs to increase or decrease Load without reaching low operating limits or high operating limits.

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded.

4.	The MW output signal should be recorded at least every two seconds.

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the IRR should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Droop shall be set not to exceed 5% with a maximum frequency Dead-Band of +/- 0.036Hz.

9.	IRRs located behind one Point of Interconnection (POI), metered by one ERCOT-Polled Settlement (EPS) Meter, and operated as an integrated Facility may combine IRRs for the purposes of this test.

Definitions

IRR Base Load = IRR telemetered High Sustained Limit (HSL) at the time of the test. The test shall be performed at an output level which is greater than 50% of IRR’s total design output capability.

Gain MW for 0.1Hz consistent with a selected droop percentage =

P∗10Droop∗60−GovernorDead−Band

Where:

P = IRR telemetered HSL (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz, outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz * 10 * Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = IRR telemetered HSL (MW)

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

IRR telemetered HSL = 150 MW

Droop = 0.05 or 5% (use 0.05 for calculation)

Governor Dead-Band = 0.036 Hz

Gain MW for 0.1Hz = 150∗105∗60150[(0.05∗60)−0.036]∗10 = +/- 5.06 MW/0.1 Hz

∆MW Contribution = 5.06 * 10* +/-0.2 = +/-10.12 MW

Expected under-frequency response:	 +10.12 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response: 	-10.12 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response: +7.08 MW in 16 sec. for -0.2 Hz offset

Minimum accepted over-frequency response:    -7.08 MW in 16 sec. for +0.2 Hz offset

Calculated droop for 8MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated percent droop = -150∗−0.260∗8 *100 = 6.25%

# Intermittent renewable resource (IRR) FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | IRR Base Load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated Minimum MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  ____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep.: __________________________

# Controllable load resource Frequency Response Test Procedure

Description of the Test

1.	The frequency response function of the Controllable Load Resource is tested On-Line at a Load level that allows Controllable Load Resources to increase or decrease Load without reaching Low Power Consumption (LPC) or Maximum Power Consumption (MPC).

2.	The test is performed by adding a frequency offset signal that exceeds the Governor Dead-Band value to the measured frequency signal.  This should create an immediate step change in the measured frequency signal.

3.	The test starts at time t0 when the frequency Dead-Band is exceeded.

4.	The MW output signal should be recorded at least every two seconds.

5.	The duration of the test is 100 seconds.  After 100 seconds, the offset signal should be removed and the Controllable Load Resource should return to pretest power output.

6.	The test should be conducted both with positive and negative frequency offsets.

7.	The test is considered successful after the signal becomes active if at least 70% of the calculated MW contribution is delivered within 16 seconds and the response is maintained for an additional 30 seconds.

8.	Droop shall be set not to exceed 5% with a maximum frequency Dead-Band of +/- 0.036Hz.

Definitions

Controllable Load Resource Base Load = Controllable Load Resource telemetered MPC at the time of the test.  The test shall be performed at an output level that allows the Controllable Load Resource to increase or decrease Load without reaching LPC or MPC.

Gain MW for 0.1Hz consistent with a selected droop percentage =

P(Droop∗60−GovernorDead−Band)∗10

Where:

P = Controllable Load Resource telemetered MPC (MW)

Droop 	= droop (%)

Frequency Offset = +0.2 Hz and -0.2 Hz, outside Governor Dead-Band

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1 Hz * 10 * Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

Where:

P = Controllable Load Resource telemetered MPC

ΔHz = Change in frequency (Hz), taking into account Governor Dead-Band

ΔMW = Change in power output (MW)

Example

Controllable Load Resource telemetered MPC = 150 MW

Droop = 5%

Governor Dead-Band = 0.036 Hz

Gain MW to 0.1 Hz = 150[(0.05∗60)−0.036]∗10 = +/- 5.06 MW/0.1 Hz

∆MW Contribution = 5 * 10* +/-0.2 = +/-10.12 MW

Expected under-frequency response:-10.12 MW in 16 sec. for -0.2 Hz offset

Expected over-frequency response: 	+10.12 MW in 16 sec. for +0.2 Hz offset

Minimum accepted under-frequency response: -7.08 MW in 16 sec. for -0.2 Hz offset

Minimum accepted over-frequency response:    +7.08 MW in 16 sec. for +0.2 Hz offset

Note: The negative sign in expected under-frequency response and minimum accepted under-frequency response denotes the required reduction in power consumption. Similarly the positive sign in expected over-frequency response and minimum accepted over-frequency response denotes the required increase in power consumption.

Calculated droop for 8 MW increase in power output in 16 sec. for -0.2 Hz offset:

Calculated percent droop = -150∗−0.260∗8 = 6.25%

# Controllable load resource FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | CLR Base Load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated Minimum MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ________________________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  ____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep.: ______________________

Westinghouse recommends using only this test.

Westinghouse recommends using only this test.