## Slide 1: Sinton to Beeville to Kenedy Load Addition Project Regional Planning Group (RPG) Review; ERCOT Independent Review
Jeff Billo
Manager, ERCOT Transmission Planning
TAC
ERCOT Public
February 7, 2013
1

## Slide 2: Background
Eagle Ford Shale related load growth in Bee and Goliad Counties is expected to cause reliability criteria violations on the 69 kV system in the area:
In September 2012 American Electric Power Service Corporation (AEPSC) submitted a project to upgrade the transmission system in the area for RPG review and comment
ERCOT Public
Highest Loaded Element | Contingency | Post contingency Loading in 2017
Kenedy Switch – Kenedy 69 kV line | Beeville – Chase Tap 69 kV line Beeville – Normana 69 kV line | 258 %
Edroy – Smith 69 kV line | Lon Hill – Orange Grove 138 kV line Lon Hill – North Edinburg 345 kV line | 142 %
Normana – Pettus 69 kV line | Kenedy Switch – Kenedy 69 kV line | 227%
Sinton – Skidmore 69 kV line | Lon Hill – Orange Grove 138 kV line Lon Hill – North Edinburg 345 kV line | 138%

## Slide 3: ERCOT Independent Review
Analyzed three options to solve the reliability issues in the area
  Primarily focused on steady state thermal and voltage reliability analysis
  Concluded that Option 2 was the most cost effective option to meet the needs for the area
  Ran additional generator outage and load growth sensitivities
ERCOT Public

## Slide 4: Endorsement
ERCOT will seek Board of Director endorsement for the following recommended project set (Option 2):
  Build a new 138 kV Big Oak substation near 69 kV Big Oak switching station (Big Oak 69 kV will be built on STEC’s Beeville – Goliad 69 kV line)
  Rebuild the existing 69 kV line (approximately 6.20 miles) from Pettus to Normana and from Normana to STEC Beeville to Big Oak (approximately 16 miles) as a double circuit 69 kV and 138 kV line with 180 MVA and 463 MVA (emergency rating), respectively. The 138 kV line from Tuleta should terminate at the new 138 kV Big Oak substation
  Rebuild the existing 69 kV line (approximately 29 miles) from Coleto Creek to Fannin to Berclair as a double circuit 69 kV and 138 kV line with 180 MVA and 463 MVA (emergency rating), respectively. The 138 kV line from Coleto Creek should terminate at the new 138 kV Big Oak substation
  Rebuild Sinton – Skidmore – Beeville 69 kV transmission line (approx. 29.5 miles) on double-circuit capable structures such that the emergency rating is at least 180 MVA
  Move the loads from Pettus (73 MVA) and Big Oak (21 MVA) 69 kV substations to Tuleta and Big Oak 138 kV substations; respectively
  Install a 15 ohm series reactor at Edroy on the Mathis 69 kV transmission line
  Upgrade the Orange Grove - Casa Blanca 69 kV line (approx. 6.7 miles) such that the emergency rating is at least 180 MVA
  Install 9.6 Mvar capacitor bank at STEC Beeville Prison 69 kV substation
  Upgrade the STEC Mathis – Mathis sub 69 kV line so that the emergency rating is at least 180 MVA
The cost estimate for these improvements is $85.15 million
ERCOT Public

## Slide 5: Comments/ Questions?
ERCOT Public