## Slide 1: Kenedy to Nixon to Seguin Line Upgrade Project Regional Planning Group (RPG) Review; ERCOT Independent Review
Jeff Billo
Manager, ERCOT Transmission Planning
TAC
ERCOT Public
February 7, 2013
1

## Slide 2: Background
Milton and Helena substations constructed in 2012 to serve a portion of the growing Eagle Ford Shale load in Karnes County
Forecasts for load on the Kenedy-Nixon-Seguin 69 kV line have continued to grow
ERCOT Public
Helena
Milton

## Slide 3: Reliability Issue
Kenedy-Nixon-Seguin line is currently rated 34 MVA
  With Eagle Ford Shale load growth the line is projected to experience post-contingency overloads in 2013 and pre-contingency overloads by 2017
ERCOT Public
 | Kenedy-Nixon-Seguin Line Forecasted Loads (MW) |  |  |  |  | 
Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
KENEDY SWITCHING STATION #1 | 2.41 | 4.97 | 5.13 | 5.29 | 5.45 | 5.6
HELENA | 16 | 22.15 | 22.59 | 23.04 | 23.5 | 23.97
MILTON | 19.44 | 30 | 30.4 | 30.8 | 31.2 | 31.6
MAGNOLIA | 0.06 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
NIXON SOUTH | 4.05 | 8.22 | 8.38 | 8.54 | 8.69 | 8.85
Total | 42.0 | 65.5 | 66.6 | 67.8 | 69.0 | 70.1

## Slide 4: RPG Review
In October 2012 the Lower Colorado River Authority Transmission Service Corporation (LCRA TSC), Guadalupe Valley Electric Cooperative (GVEC), American Electric Power (AEP), and South Texas Electric Cooperative (STEC) submitted a joint project to upgrade the transmission system in the area for RPG review and comment
ERCOT analyzed the reliability issues in the area as part of the 2012 Five-Year Transmission Plan and concluded that the recommended project set best met the system needs
ERCOT Public

## Slide 5: Endorsement
ERCOT will seek Board of Director endorsement for the following recommended project set:
  Upgrade and convert the existing 69 kV transmission lines between the Kenedy Switch, Nixon, and Seguin Substations to 138 kV with 795 ACSR conductor. Upgrade the facilities at the Kenedy Switch (AEP), Helena, Magnolia Tap, Magnolia (AEP), Milton, Nixon (AEP), Nixon, and Seguin substations to 138 kV
  Add a new 138/69 kV substation named Deer Creek at the intersection of the GVEC Seguin-Gonzales and the LCRA TSC Nixon-Luling 69 kV transmission lines and add a 138/69 kV 45 MVA autotransformer at Deer Creek. Terminate the 138 kV transmission line from Nixon and Seguin at the Deer Creek 138 kV bus and terminate the 69 kV transmission line from Luling and Gonzales at the Deer Creek 69 kV bus
  Relocate the existing 138/69 kV, 45 MVA autotransformer from the Seguin Substation to the Nixon Substation
The cost estimate for these improvements is $55.3 million
ERCOT Public

## Slide 6: Comments/ Questions?
ERCOT Public