## Sheet1
Operations and Planning Synchronization Task Force - Issues List Matrix
+ |  | DESCRIPTION | Recommendation | ISSUE RESOLUTION/RESPONSE
1 | Consider use of an Operations feedback loop (e.g. monthly report to the ROS) to identify and address credible scenarios for further study.
| a | Transmission elements associated with an ERCOT Transmission Watch. | No Action Required | The current practice of publishing a list of Transmission Watches in the monthly ERCOT Operations Report if a mitigation plan is not identified, plus the implementation of NPRR393 should be adequate to alert Transmission Planners to perform studies if needed.
| b | Transmission elements that are chronically denied Maintenance Outages. | No Action Required | Transmission Planners and Operators should periodically confer with each other to create a list of circuits that are difficult to take out of service and then perform appropriate studies to aid the outage request process. Since TOP-002-2.1b R2 requires operators to participate in the system planning study process and provide an operating personnel perspective, no further recommendation is needed.
| c | Congestion analysis for constraints that are consistently causing security violations similar to the concepts in NPRR393. | No Action Required | Implementation of NPRR393 will clarify Inactive SCED Constraint Reporting that allows for transparency in Real-Time for constraints that are overloaded. Transmission Planners will be able to utilize this information to identify constraints that require study.
| d | Real-time developed mitigation plans requiring load-shed for a credible single contingency, including duration of event and amount of planned load shed. | Implemented | Add an extra column to the ROS Operations Report to indicate that the Mitigation Plan (MP) for SCED congestion required a load shed plan.
| e | When ERCOT performs outage analysis, if redispatch of generation is needed to avoid congestion, then that information should be made known to the TSP. This would enable TSPs to voluntarily reschedule the outages if there is flexibility in doing so. Learning about generation redispatch costs after the fact is of limited value. | No Action Required | ERCOT is already doing this by sending the requesting TSP a questionnaire if the ERCOT study detects an operational constraint. This alerts the TSP that generation redispatch will be needed to avoid congestion.
| f | Each ERCOT developed TOAP should be posted on the Nodal MIS on or before the effective date (preferably when outage is approved) and should include information such as the underlying scheduled outage that it is associated with and its date range, as well as, relevant load and generation unavailability assumptions used in its development. | In Progress | ERCOT believes it will be difficult to manage this on the MIS. Nonetheless, ERCOT reps on the OPSTF will discuss this with their Outage Coordinators and report back to OPSTF. TOAPs associated with forced outages & done on the fly may not be posted.
| g | ERCOT to report transmission clearance related congestion in more detail including the underlying scheduled outage, the congestion rents associated with the clearances, and the associated TOAP description, if applicable, as well as a basic description of which actual conditions were more stressful than study conditions. | No Action Required | OPSTF believes the implementation of NPRR393 will be adequate for meeting this need. Also, much of this is already being reported in the monthly Operations and Planning reports to ROS. For example, congestion rents are in the Planning report while outages are in the Operations report.
2 | Ensure that Real-Time Operations, Outage Planning and Transmission Planning processes are aligned in the use of operating generic transmission limits. |  | Best Practice | GTLs reflect market based limits for studies that are economic in nature. Transmission planners need to respect SOLs & IROLs for reliability studies, but if studying congestion the lower GTL limits should be used.
3 | Consider clarifications and improvements to the Five Year Transmission Plan process.
| a | Consistent publication date for Five Year Transmission Plan. | PGRR TBD | OPSTF recommends that ROS direct the PLWG to create a PGRR that establishes a December 31 deadline for the 5-year/RTP plan.
| b | Consideration of incomplete Five Year Transmission Plan reliability projects in seasonal RAP/MP/SPS development. | Process Change | ERCOT Sys. Planning to make internal process changes to seek Transmission Service Provider (TSP) RAP/MP/SPS development and formalize this in the 5-Yr Plan process.
| c | Exempt RPG review of Five Year Transmission Plan reliability projects that have an estimated cost less than $50M. | No Action Required | OPSTF believes others need the opportunity to comment on all projects reviewed in the RPG process. ERCOT Protocols and Planning Guides (3.1.4.2 paragraph 1) exempt tier 1, 2, and 3 projects included in the 5-year plan from ERCOT review. In addition projects under $15M (tier 4) are exempt from RPG review.
| d | Define and implement an urgent RPG review process for all Five Year Transmission Plan reliability projects that have a need date of less than 36 months. | No Action Required | OPSTF believes this is essentially being done since TSPs are initiating projects & ordering equipment before the 5-Yr Plan is completed. PUCT Substantive Rule 25.101 (b)(3)(D) allows ERCOT to designate a transmission line as critical which expedites the CCN process at the PUCT.
| e | Ensuring projects in the Five Year Transmission Plan are completed in a timely manner. This includes unforeseen consideration of load variability, transmission outages and construction complexities that may require earlier completion. | PGRR TBD (see 4c) | OPSTF is recommending a proposal to revise the Planning Guides to propose improvements when line loadings reach 95% verses 100% of ratings. Additionally the implementation of PGRR026 will lead to the creation of a year 6 SSWG case which should allow projects to be identified sooner.
4 | Appropriate ratings
| a | Ensure Load and Ratings assumption consistency. | PGRR TBD (see 4c) | During extreme weather conductor ratings decrease. OPSTF is recommending a proposal to revise the Planning Guides to propose improvements when line loadings reach 95% verses 100% of ratings.
| b | Should SCED be limited by 2-hour ratings or make use of 15-minute ratings? | No Action Required | The ERCOT Operations "DRAP" improvement should solve this issue.
| c | Should planning studies be more conservative by using the planning normal rating (Rate A) for a select set of contingencies? | PGRR TBD | The OPSTF survey determined that a majority of the lines are using identical rate A and rate B values. OPSTF is recommending a proposal to revise the Planning Guides to propose improvements when line loadings reach 95% verses 100% of ratings.
| d | Use of dynamic ratings in planning studies. | No Action Required | Most lines in ERCOT are modeled with dynamic ratings in the Operations Model. Lines are not dynamically rated in ERCOT reliability studies, but are dynamically modeled in economic (UPLAN) studies. OPSTF believes that this approach is appropriate.
5 | Appropriate load levels to consider in planning studies
| a | Ensure that area load forecasts in the planning base cases are aligned with actual area peak loads. | Not Approved | OPSTF recommended that TSPs model the 90th percentile load forecast in SSWG base cases. ROS did not approve the proposal.
| b | Establish a basis for load variations, including area seasonal variations. | Best Practice | For small local areas and load pockets planners should model the undiversified load level as a reasonable load variation. For regional or weather zone load variations, planners should model a reasonable high load forecase scenario, such as a 90th percentile load forecast.
| c | Review the planning process relative to validating load forecasting inputs of discrete load additions and determine whether process improvements need to be made. | In Progress | There needs to be an oversight/validation procedure in place within the RPG or ALDR processes to determine when load projections & transmission improvements should be allowed in SSWG base cases. Many ISOs outside ERCOT have a load interconnection process where this issue could be handled.
6 | Use of double circuit contingencies to develop operating limits – ERCOT Operations conservatively considers all double circuit contingencies. Evaluate appropriate use of double circuit contingencies. |  | OWG Action Required | OPSTF discussed a proposal that an DCKT outage be considered only if it caused a reliability problem. The 'push-back' was that it is hard for the market to model contingencies that are sometimes run and sometimes not. ERCOT commented that this would be complex, burdensome and require new tools for Sys. Operations. OPSTF recommends for the ROS to direct OWG to modify the Operating Guides language to better reflect the actual practice.
| b | In a SCED run, consider not redispatching generation for double circuit outages pre-contingency, as long as the loading is below the 15 minute rating and it can be decreased with online generation. In other words, make redispatch of online generation a valid mitigation plan for loading problems due to double circuit outages. Limits can be placed on its use such as: | No Action Required | The ERCOT Operations "DRAP" improvement should solve this issue.
|  | · The loss of the circuit or transformer should not lead to a cascading outage | " | "
|  | · The needed responsive reserve should be carried on two or more generation units and should be deliverable within 15 minutes | " | "
7 | Long-term unavailability of autotransformers |  | Approved | OPSTF recommended that N-1-1 studies be run for 345 kV autotransformers and that the PLWG develop a PGRR. Approved by ROS 9-13-2012.
| a | N-1-1 for autotransformers as a credible contingency for which load interruption is not allowed.
| b | Use of defined spare equipment strategy as mitigation for N-1-1 scenario.
| c | Use of defined distribution feeder switching or distribution transformer loading strategy as mitigation for N-1-1 scenario.
8 | Generator unit unavailability and modeling issues
| a | Combined cycle trains as a credible single contingency for which load interruption is not allowed. | No Action Required | PGRR024 will clarify current practice. Therefore no further action is required.
| b | Use of “typical” or “historical” Planned, Maintenance and Forced Outages and/or derates in an area. | PGRR TBD (see 4c) | OPSTF is recommending a proposal to revise the Planning Guides to propose improvements when line loadings reach 95% verses 100% of ratings. Implemenation of the 95% threshold should reduce the threat associated with this issue.
| c | Use of extreme generator unit unavailability in an area and/or ERCOT-wide. | No Action Required | It is expected that the new NERC Standard TPL-001-2 (Wide area events affecting the Transmission System - Steady State Assessment) will address this. Therefore no action is recommended.
| d | Unavailability of intermittent resources in an area. | No Action Required | PGRR024 will clarify current practice. Therefore no further action is required.
| e | Ensure alignment of anticipated maximum output from RARF submittals, operational tests and Pmax used in the planning base cases. | No Action Required | For SSWG cases ERCOT and SSWG members use seasonal net PMAX from the RARF. No further changes recommended.
9 | Consideration of transmission maintenance outages in planning studies. |  | Best Practice | Issue 9 supports TSP efforts to justify projects based on the difficulties involved in obtaining planned outages for specific lines. No PGRR needed as ERCOT Guides & NERC Standards require known outages to be modeled in planning studies. Planners should use input from Operators and planning software such as the new N-1-1 PSS/E scanning feature to identify difficult planned outages that require study before outage requests are submitted.
| a | Use of “typical” or “historical” Planned, Maintenance and Forced Outages in an area. | " | "
| b | Use of construction related outages in determination and timing of planning solutions. | " | "
10 | Security-constrained deliverability of ancillary services – determine a methodology to account for ancillary service requirements in the generation dispatch or load response in planning and operating studies. |  | In Progress | On 11-28-12 OPSTF briefly discussed this issue. Modeling A/S in UPLAN runs the gen further up the dispatch stack which raises congestion costs reported in study results.
11 | Simultaneous feasibility of generation dispatch solutions – ensure planning studies adequately anticipate operational constraints. |  | No Action Required | This issue refers to using re-dispatch to solve a problem without causing another problem. No action required because ERCOT is doing this in its 5-Yr Plan study using UPLAN and PowerWorld (not available in PSS/E).
12 | Planning Cases and Scenarios.
| a | Model voltage regulation at actual reference point (typically the generator bus). | DWG Action Required | Planners generally model regulation at the hi-side POI as required by the Protocols and Stability Studies. But real-world generation sometimes regulates the low-side with the result that during contingencies actual gen voltage support is less than what planners see in their models. The RARF contains a field that designates where the location of the voltage regulation is (on high or low side). This information is currently not widely being used. OPSTF recommends DWG look into this issue with respect to operations and planning and make recommendataions to the ROS.
| b | Accurate reactive modeling of generation (mainly wind) resources – use reactive capability curve instead of maximum values. | No Action Required | There is concern that Test Data is not getting into the RARF and therefore the SSWG base cases (protocols section 3.7). ERCOT will modify the reactive capability for resources in the SSWG base cases by subtracting Aux load reactive in the RARF reactive capability curve point 4 reactive values. This data change was implemented during December 2012 TPIT update. The data is available to ERCOT and TSPs to manually create a reactive capability curve. OPSTF is not recommending any further changes.
| c | Accurate modeling of reactive loads as seen from the transmission system. | SSWG Action Required | Issue still being researched. ALDR instructions require that pf data be taken where the meter is located. OPSTF recommends that the ROS direct the SSWG to clarify compensating for transformer losses when modeling loads on the high side of the transformer of 60kV or above. This should result in clarifying section 4.2 of the SSWG Procedural Manual.
13 | RMR Studies. |  | Approved | NPRR465 submitted by Centerpoint Energy and reviewed by OPSTF. August, 2012 ROS recommendation and endorsement.
| a | Consider generator unit unavailability in RMR studies.
| b | Consider expanding RMR studies for future year generator unit unavailability.