ERCOT Operations Report

January 2013 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 1/2/2013 14:41 | 59.794 | 92 | Unit trip with 835 MW net. |
| 1/4/2013 9:41 | 59.701 | 8 | Unit trip with 1308 MW net. |
| 1/6/2013 21:49 | 59.865 | 12 | Unit trip with 655 MW net. |
| 1/8/2013 16:40 | 59. 693 | 8 | Unit trip with 1370 MW net. |
| 1/11/2013 22:37 | 59.854 | 20 | Unit trip with 460 MW net. |
| 1/13/2013 20:35 | 59.819 | 48 | Unit trip with 838 MW net. |
| 1/15/2013 10:04 | 59.829 | 304 | Multiple unit trips with 750 MW net. |
| 1/19/2013 23:10 | 59.817 | 28 | Unit trip with 718 MW net. |
| 1/22/2013 16:06 | 59. 765 | 40 | Unit trip with 857 MW net. |
| 1/24/2013 21:24 | 59.879 | 8 | Unit trip with 500 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 1/4/2013 9:41:38 | DCS event | Approx. 14 sec | The event was caused by the loss of one unit. The unit was generating 1308 MW net before trip, the frequency dropped to 59.70 Hz. The oscillating frequency of 0.67 Hz with 19% damping ratio was observed. |
| 1/8/2013 16:40:22 | DCS event | Approx. 12 sec | The event was caused by the loss of one unit. The unit was generating 1370 MW net before trip, the frequency dropped to 59.695 Hz. Two oscillating frequencies of 0.69 Hz with 5% damping ratio and 0.85 Hz with 15% damping ratio were observed. |
| 1/22/2013 16:06:18 | Unit Trip | Approx. 12 sec | The event was caused by the loss of one unit. The unit was generating 857 MW net before trip, the frequency dropped to 59.765 Hz. No significant oscillation was observed. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/1/13 19:21:02 | 1/1/13 19:24:38 | 0:03:36 | 386.29 | Unit trip with 140 MW net |
| 1/2/13 14:41:30 | 1/2/13 14:44:36 | 0:03:06 | 911.79 |  |
| 1/4/13 9:41:48 | 1/4/13 9:44:34 | 0:02:46 | 1449.4 |  |
| 1/6/13 21:49:16 | 1/6/13 21:51:40 | 0:02:24 | 382.51 |  |
| 1/8/13 16:40:30 | 1/8/13 16:42:10 | 0:01:40 | 1346 |  |
| 1/9/13 2:53:10 | 1/9/13 2:54:58 | 0:01:48 | 167.66 | Unit trip with 265 MW net |
| 1/11/13 9:26:42 | 1/11/13 9:28:22 | 0:01:40 | 354.56 | Unit trip with 115 MW net |
| 1/11/13 22:37:14 | 1/11/13 22:40:15 | 0:03:01 | 489.52 |  |
| 1/13/13 20:35:14 | 1/13/13 20:38:38 | 0:03:24 | 692.73 |  |
| 1/15/13 10:04:18 | 1/15/13 10:12:34 | 0:08:16 | 905.66 |  |
| 1/19/13 23:10:22 | 1/19/13 23:13:26 | 0:03:04 | 774.11 |  |
| 1/22/13 16:06:26 | 1/22/13 16:09:42 | 0:03:16 | 874.57 |  |
| 1/24/13 21:24:46 | 1/24/13 21:26:30 | 0:01:44 | 194.08 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Asphalt Mines - Uvalde AEP & Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 13 | N |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Orlando - Vernon 138 kV | 9 | N |
| Basecase | Laquinta - Lobo 138 kV | 7 | N |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 7 | N |
| Bosque Switch - Whitney 138 kV | Lake Whitney TNP - Whitney 138 kV | 7 | N |
| DCKT Whitepoint - Lon Hill & South Texas Project 345 kV | Sinton - Skidmore 69 kV | 7 | N |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 7 | N |
| Fort Stockton Plant - Barrilla 138 kV | Fort Stockton Switch - Barrilla 69 kV | 5 | N |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney TNP 138 kV | 4 | N |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Fort Worth Substation - Teasley Substation 138 kV | 4 | N |
| Rd Wells Interchange - West Denton 138 kV | Fort Worth Substation - Teasley Substation 138 kV | 4 | N |
| Tpco McCampbell - Portland 138 kV | Rincon - Whitepoint 138 kV (Rincon_White_2) | 4 | N |
| DCKT Morgan Creek SES - China Grove Switch 138 kV | Morgan Creek SES Axfmr3h 138/69 kV | 4 | Y |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 3 | N |
| Lobo - San Miguel 345_138 kV Switchyards 345 kV | San Diego - Freer 69 kV | 3 | N |
| Aspermont AEP - Spur 138 kV | Spur 138_69_1 138/69 kV | 3 | N |
| West Denton - Roanoke Switch 345 kV | Fort Worth Substation - Teasley Substation 138 kV | 3 | N |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - BTU_Jack_Creek 345 kV | 3 | N |
| Scurry Switch - Sun Switch 138 kV | Roby - Longworth 69 kV | 2 |  |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345 kV | Jim Christal Substation - North Denton Interchange 138 kV | 2 |  |
| Rd Wells Interchange - West Denton 138 kV | Jim Christal Substation - North Denton Interchange 138 kV | 2 |  |
| Greens Bayou At1_H (3) 345/138 kV | Greens Bayou At2_H (3) 345/138 kV | 2 |  |
| Eskota Switch Axfmr1 138/69 kV | Abilene Northwest - Ely Rea Tap 69 kV | 2 |  |
| Pawnee Switching Station - San Miguel 345_138 kV Switchyards 345 kV | Pawnee Switching Station Xf1 345/138 kV | 2 |  |
| Los Fresnos - Loma Alta Substation & La Palma 138 kV | La Palma - Villa Cavazos 138 kV | 2 |  |
| Laquinta - Lobo 138 kV | Falfurrias 138_69A1 138/69 kV | 2 |  |
| Fern - Ball Park 138 kV | Kirby - Holbrook 138 kV | 2 |  |
| Salt Creek BEPC - Spur And Scurry Switch 138 kV | Wolfgang - Rotan 69 kV | 2 |  |
| Coleto Creek - Pawnee Switching Station 345 kV | Coleto Creek - Kenedy Swtich 138 kV | 2 |  |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Lewisville Switch - Jones Street TNP 138 kV | 2 |  |
| Basecase | Post Oak Wind (Potomes) 138 kV | 1 |  |
| Basecase | Bastrop Energy Center - Garfield Lcra 345 kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Spur - Girard Tap 69 kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Orlando - Vernon 138kV | 1 |  |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 1 |  |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Sonora - Friess Ranch 69 kV | 1 |  |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Abilene Mulberry Creek - Oklaunion 345 kV | 1 |  |
| DCKT Graham SES - Long Creek & Cook Field Road Switch 345 kV | Cisco - Leon Switch 138 kV | 1 |  |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Airco AEP 138kV | 1 |  |
| Aspermont AEP - Spur 138kV | Wolfgang - Rotan 69 kV | 1 |  |
| DCKT Graham SES - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 1 |  |
| DCKT Graham SES - Parker Switch 345 kV | West Denton - Roanoke Switch 345 kV | 1 |  |
| DCKT Graham SES - Parker Switch 345 kV | Sonora - Friess Ranch 69kV | 1 |  |
| DCKT Twin Buttes - Brown Switch & San Angelo Red Creek 345 kV | Twin Buttes T1H (3) 345/138 kV | 1 |  |
| DCKT Twin Buttes - Brown Switch & San Angelo Red Creek 345 kV | Twin Buttes T1H (3) 345/138 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | McDonald Road - Forsan Tap 138 kV | 1 |  |
| Falcon Seaboard - Morgan Creek SES 345 kV | Stanton East - Martin Capacitor 69 kV | 1 |  |
| Kleberg AEP - Loyola 138 kV | Loyola Sub 138_69_1 138/69kV | 1 |  |
| DCKT Kendall - Haysen 345kV & Boerne - Fairra 138 kV | Comfort - Cico 138 kV | 1 |  |
| DCKT Barney Davis - Holly & Airline AEP 138 kV | Naval Base - North Padre 138 kV | 1 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Seguin - Seguin West 138 kV | 1 |  |
| China Grove Switch - Morgan Creek SES 138 kV (6220) | China Grove Switch - Morgan Creek SES 138 kV (6225) | 1 |  |
| DCKT Twin Oak Switch - Gibbons Creek & BTU_Jack_Creek 345 kV | Jewett - Singleton 345 kV (260_A) | 1 |  |
| Hiway 9 138_69a2 138/69 kV | Koch Up River 138_69A1 138/69 kV | 1 |  |
| Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV | 1 |  |
| Moss Switch - Holt Switch & Amoco North Cowden 138 kV | Odessa North - Odessa Basin Switch 69 kV | 1 |  |
| Kyle - San Marcos 138 kV | Turnersville - Buda 138 kV | 1 |  |
| Lake Pauline - Munday East 138 kV | Lake Pauline 138_69_1 138/69 kV | 1 |  |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345kV (260_A) | 1 |  |
| DCKT Cedar Bayou Plant - Chambers & North Belt 345 kV | Cedar Bayou Plant At2b_H (3) 345/138 kV | 1 |  |
| DCKT Greens Bayou - King 345 kV | Greens Bayou Plant At2_H (3) 345/138 kV | 1 |  |
| Brown Switch - Killeen Switch 345 kV (35090) | Brown Switch - Killeen Switch 345kV (35095) | 1 |  |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 |  |
| Lobo 2_345_138_H 345/138 kV | San Diego - Freer 69 kV | 1 |  |
| Odessa North Axfmr1 138/69 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Sweeny Cogen Sclpata_L 138/69 kV | Brazoria TNP - Clemons Tap TNP 69 kV | 1 |  |
| Comanche Switch (Oncor) - Brown Switch 345 kV | Brown Switch - Killeen Switch 345 kV (35095) | 1 |  |
| DCKT Comanche Peak SES Units 1 & 2 | Laquinta - Lobo 138 kV | 1 |  |
| Pawnee Switching Station Xf1 345/138 kV | Coleto Creek - Kenedy Swtich 138 kV | 1 |  |
| DCKT Sweetwater East Switch - Abilene Mulberry Creek & Long Creek 345 kV | Bluff Creek - Abilene Mulberry Creek 345 kV | 1 |  |
| Crane Arco to Pegasus (7)138 kV | Garden City - Glasscock (Oncor) 69 kV | 1 |  |
| DCKT Willow Creek Switch - Parker Switch 345 kV | Graham SES - Parker Switch 345 kV | 1 |  |
| DCKT Skyline - Calaveras 345 kV | Braunig - Cagnon 345 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which made our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 6 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

- 01/14 	Baytown 138/345kV Autotransformers AT1 and AT2

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

01/16 SCED failed to run for an interval.

Communication Issues

None

## ERCOT peak (Unofficial)

01/16 08:00 50,687 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 |  |
| March | 2.24 | 2.02 | 3.49 |  |
| April | 2.47 | 3.55 | 2.78 |  |
| May | 2.63 | 3.27 | 3.09 |  |
| June | 2.84 | 2.28 | 2.85 |  |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 3.50 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 1/8/2013 | 17:47 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/15/2013 | 11:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/26/2013 | 10:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Watch

None

Emergency Notice

01/16 	SCED failed to run for an interval.

Texas RE Event Analysis

None