| NOGRR Number | 108 | NOGRR Title | QSE and TSP Hotline Responsibilities |
| --- | --- | --- | --- |
| Date Posted |  | December 3, 2012 |  |

| Requested Resolution | Normal |
| --- | --- |
| Nodal Operating Guide Section Requiring Revision | 7.1.2, QSE and TSP Responsibilities |
| Protocol Section(s) Requiring Revision | None. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds the requirement for Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs) to have a touchtone keypad on their Hotline phone. |
| Reason for Revision | This NOGRR adds the requirement for the QSEs and TOs 24x7 control centers to have a touchtone keypad on their Hotline phone in order to provide an acknowledgement of receipt of Verbal Dispatch Instruction (VDI). |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - ERCOT will be able to easily track which QSEs and TOs understood VDI. |
|  | 2 | - Approximately only 10% of QSE/TO do not have a touchtone keypad on their Hotline phone. |

| Sponsor |  |
| --- | --- |
| Name | Colleen Frosch |
| E-mail Address | cfrosch@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4219 |
| Cell Number | 512-868-7006 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | 512-248-3867 |

Proposed Guide Language Revision

### 7.1.2	QSE and TSP Responsibilities

QSE and TSP Responsibilities include the following:

(a)	TSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance of the WAN hardware.  Appropriate WAN documents can be obtained by contacting the ERCOT Account Manager.

(b)	ERCOT WAN participants shall provide physical security systems compliant with the applicable Critical Infrastructure Protection (CIP) requirement of the North American Electric Reliability Corporation (NERC) Reliability Standards.

(c)	Any TSP or QSE facility, whether primary or back-up, will be required to connect directly to the ERCOT WAN; this includes connectivity to both the MPLS and PTP networks.  ERCOT will work with each Market Participant to determine the most appropriate WAN demarcation point.  Criteria for determining demarcation points include:

(i)	Reliability;

(ii)	Location of data centers;

(iii)	Control centers;

(iv)	Disaster recovery facilities;

(v)	Energy and Market Management System (EMMS) equipment;

(vi)	ICCP equipment; and

(vii)	PBX equipment installation.

(d)	ERCOT is responsible for the reliable transport of critical market communications and will make the ultimate determination of the demarcation point location.

(e)	Market Participants that serve both TSP and QSE functions at one location will only require one ERCOT WAN connection as defined in Section 7.1, ERCOT Wide Area Network, at that location.

(f)	If a TSP and QSE share a centralized private branch exchange (PBX), separate OPX circuits will be terminated for each participant.

(g)	Each Market Participant is required to extend the ERCOT OPX and Hotline voice circuits into its system operations desk that is staffed continuously.  ERCOT will deliver the OPX and Hotline to a channel bank provided by the Market Participant.  The OPX and Hotline voice circuits are transported on separate Digital Signal Level 0 (DS0) channels.  In the event a Market Participant represents other Entities through an agency agreement approved by ERCOT, each Entity represented must have dedicated OPX circuits.  In these cases, a single Hotline button will be used for the Market Participant and all of the represented Entities.  It is the Market Participant’s responsibility to deliver the Hotline and the OPX to the Market Participant’s system operations desk in a manner that reasonably assures continuous communication with ERCOT and is not affected by PBX features such as automatic transfer or roll to voice mail.  Also, a touchtone keypad is required for the Hotline to be able to provide an acknowledged receipt.  The demarcation point for all voice circuits is the Market Participant’s channel bank.

(h)	Each TSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN as required by the ERCOT Protocols.  For TSPs these include, but may not be limited to, voice communications, ICCP, and Supervisory Control and Data Acquisition (SCADA) for substations and other Transmission Facilities.  For QSEs these include, but may not be limited to, voice communications, ICCP, and SCADA for Resources.

(i)	ERCOT WAN participants shall provide adequate physical facilities to support the ERCOT WAN communications equipment.  The physical facilities and communications equipment requirements include:

(i)	Provide an analog business phone line or PBX analog extension for troubleshooting and maintenance of equipment;

(ii)	Provide a height of 24” of rack space in a 19” wide rack;

(iii)	Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with four receptacles in the 19” rack listed above;

(iv)	Provide building wiring from circuit termination to equipment rack;

(v)	Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility;

(vi)	Within one-hour notice, provide emergency access to the facility to ERCOT employees or contractors;

(vii)	Provide on site personnel to escort ERCOT employees or contractors;

(viii)	Provide a firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN;

(ix)	Provide connectivity from Market Participant firewall or router to ERCOT LAN located at Market Participant site.  Market Participants are responsible for their own security through this connection;

(x)	Provide a channel bank with at least one T1 interface and four Foreign Exchange Station (FXS) ports.  Connect FXS (e.g. PBX, key system) to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive;

(xi)	Dual cable entrances to Market Participant, connecting to different Telco Central Offices is highly recommended; and

(xii)	Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

Figure 1 ERCOT Wide Area Network Overview

(j)	For each new Competitive Renewable Energy Zone (CREZ) transmission line, listed below, an associated communications path should be established to provide a high degree of dependability, security, and immunity from interference.  Additionally this communications path should support high bandwidth (155 mb/s or greater), low latency (unidirectional delay no greater that one millisecond per 100 miles), and be engineered to meet 99.999% availability with capacity reserved for regulated utility protection, monitoring and control.  Redundant communication paths are required unless this necessitates retrofitting existing facilities.  In these Operating Guides, CREZ consists of the following new 345 kV circuits and associated stations:

(i)	Bluff Creek to Brown double circuit;

(ii)	Brown to Newton double circuit;

(iii)	Newton to Killeen double circuit;

(iv)	Killeen to Salado add second circuit;

(v)	Scurry County South Switching Station to West Shackelford double circuit;

(vi)	Scurry County South Switching Station to Tonkawas double circuit;

(vii)	Scurry County South Switching Station to Long Draw Station double circuit;

(viii)	Dermott Switching Station to Scurry County South Switching Station double circuit;

(ix)	Dermott Switching Station to Willow Creek double circuit;

(x)	Central Bluff to Bluff Creek double circuit;

(xi)	West Shackelford to Navarro/Sam Switch double circuit;

(xii)	Sand Bluff Station to Divide double circuit capable;

(xiii)	Bearkat Station to Sand Bluff station double circuit capable;

(xiv)	Gillespie to Newton double circuit capable;

(xv)	Kendall to Gillespie double circuit capable;

(xvi)	North McCamey to Odessa double circuit capable;

(xvii)	Bakersfield to North McCamey double circuit capable;

(xviii)	Bakersfield to Big Hill double circuit capable;

(xix)	Big Hill to Kendall double circuit capable;

(xx)	Big Hill to Twin Butte double circuit capable;

(xxi)	Riley to Edith Clarke double circuit;

(xxii)	Nazareth to Hereford double circuit capable;

(xxiii)	Nazareth to Silverton double circuit capable;

(xxiv)	Hereford to White Deer double circuit capable;

(xxv)	Silverton to Cottonwood Station double circuit;

(xxvi)	Silverton to Edith Clarke double circuit;

(xxvii)	Cottonwood Station to Dermott Switching Station double circuit;

(xxviii)	Cottonwood Station to Edith Clarke double circuit;

(xxix)	White Deer to Silverton double circuit;

(xxx)	Gray to Riley double circuit;

(xxxi)	Gray to White Deer double circuit;

(xxxii)	Edith Clarke to West Shackelford double circuit;

(xxxiii)	Sweetwater East to Central Bluff double circuit;

(xxxiv)	Tonkawa to Sweetwater East double circuit;

(xxxv)	Long Draw Station to Sand Bluff Station double circuit capable;

(xxxvi)	Long Draw Station to Grelton Station double circuit capable;

(xxxvii)	Grelton Station to Odessa double circuit capable;

(xxxviii)	Riley to Bowman double circuit;

(xxxix)	Riley to West Krum double circuit;

(xl)	West Krum to Anna double circuit;

(xli)	Willow Creek to Hicks double circuit;

(xlii)	Bowman to Jacksboro double circuit capable;

(xliii)	Jacksboro to Willow Creek double circuit; and

(xliv)	Willow Creek to Parker double circuit.

(k)	QSEs and TSPs shall supply, implement, and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides.