| SCR Number | 773 | SCR Title | Addition of Regulation Feedback to Generation to be Dispatched Calculation |
| --- | --- | --- | --- |
| Date Posted |  | January 30, 2013 |  |

| Requested Resolution | Urgent status is requested as this System Change Request (SCR) improves Regulation bias and establishes a feedback mechanism between Security-Constrained Economic Dispatch (SCED) and ERCOT Load Frequency Control (LFC). Analysis shows that there is a Regulation Service bias resulting in a decrease in Regulation Service availability for extended periods of time. The Performance Disturbance Compliance Working Group (PDCWG) was tasked with evaluating the issue and providing a solution. Analysis of the initial solution, tuning of the ERCOT LFC system with limited data, showed that the offset has not changed. The PDCWG concluded that changing the dispatch in SCED was the next appropriate step. |
| --- | --- |
| Supporting Protocol or Guide Section | 6.5.7.3, Security Constrained Economic Dispatch |
| Other Document Reference/Source | None. |
| System Change Description | This SCR updates the formula used by the system to calculate the amount of generation to be dispatched that takes into account a configurable quantity for Regulation Service that has been deployed. |
| Reason for System Change | To address the need for reducing Regulation Service usage. |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - Reduce the amount of Regulation Service deployed. |

| Sponsor |  |
| --- | --- |
| Name | David Kee on behalf of the PDCWG |
| E-mail Address | dekee@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | 210-353-6912 |
| Cell Number | 210-667-5206 |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | 512-248-3867 |

Business Case for Proposed System Change

Issue:

ERCOT’s current generation to be dispatched calculation does not have a regulation feedback mechanism, which results in Regulation Service deployment in one direction for longer durations.

Resolution:

Following modifications are needed:

- Add the K4 configurable factor together with the rolling average of regulation deployed to the following equations.

Generation to be Dispatched = Total Gen +K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLRR + K4*Regulation Deployed.

- Ability to use the rolling average of Regulation Service deployed over X minutes, where value X can be configured.