| PGRR Number | 028 | PGRR Title | Evaluation of Compliance with Reactive Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | February 27, 2013 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Planning Guide Section Requiring Revision |  | 5.6.1, Evaluation of Compliance with Reactive Power Requirements (new) |  |  |
| Protocol Section(s) Requiring Revision |  | None. |  |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) defines ERCOT’s process for evaluating proposed Generation Resources’ abilities to provide Reactive Power. Protocol Section 3.15, Voltage Support, defines reactive capability requirements for Generation Resources. Paragraph (3) of Protocol Section 16.5, Registration of a Resource Entity, requires ERCOT to opine upon the capability of the proposed Generation Resource’s ability to meet these requirements. |  |  |
| Reason for Revision |  | This PGRR is in response to concerns raised during the October 15, 2012 Photovoltaic and Storage Workshop. This PGRR proposes to clarify how Entities proposing Generation Resources must design their new facilities. |  |  |
| Procedural History |  | - On 2/12/13, PGRR028 and an Impact Analysis were posted. - On 2/27/13, the Planning Working Group (PLWG) considered PGRR028. |  |  |
| PLWG Decision |  | On 2/27/13, the PLWG was in consensus to table PGRR028 for one month. |  |  |
| Summary of PLWG Discussion |  | On 2/27/13, participants requested that PGRR028 be tabled to allow additional time for review. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - Clarifies ERCOT’s process of evaluating proposed Generation Resources. |

| Sponsor |  |
| --- | --- |
| Name | John Adams |
| E-mail Address | jadams@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-3130 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

5.6.1	Evaluation of Compliance with Reactive Power Requirements

(1)	ERCOT shall evaluate whether the proposed Generation Resources are designed to comply with the Reactive Power capability and voltage control requirements as specified by the Protocols. In order to accomplish this evaluation, ERCOT will confirm that proposed Generation Resources are able to deliver Reactive Power to a high side voltage range of 1.0 per unit to 1.04 per unit at the Point of Interconnection (POI) without adjustment to no-load transformer taps or other equipment requiring the Generation Resource to come Off-Line.  Further, ERCOT will also confirm that with adjustment to no-load transformer taps or other Off-Line adjustments proposed Generation Resources are designed to provide Reactive Power at the full operational voltage range of 0.95 per unit to 1.05 per unit at the POI.  For the evaluation, ERCOT shall consider:

(a)	“Exhibit C” (or a similar exhibit) included in the Standard Generation Interconnection Agreement (SGIA); and

(b)	The data submitted through the Resource registration process.

(2)	ERCOT will indicate whether the design of the proposed Generation Resource complies with the operational standards established in Protocol Section 3.15, Voltage Support, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.  Nothing in this Section 5.6.1 shall be construed to change the Reactive Power and voltage control requirements prescribed in the Protocols.