## REPORT V7 INFO
REPORT NAME | mmm yyyy - Nodal Monthly Aggregate WPF Report
VERSION | v7
VERSION LAST UPDATED | 2012-02-02
VERSION NOTE | Changes from v6: Changed the COP Performance Analysis to allow for some precision buffer. Instead of highlighting hours when COP HSL >STWPF, hours are now highlighted if COP HSL-STWPF > 2% of Installed Capacity
ADDITIONAL INFORMATION
DAY-AHEAD | Data retrieved at 14:30 on previous day.
HOUR-AHEAD | Data retrieved an hour prior to the Operating Hour. Ex: For the Operating Hour 15:00, the data is retrieved at 13:00 Note: Operating Hours are Hour Ending intervals.
STWPF | Short-Term Wind Power Forecast: 50% Probability of Exceedance Forecast from AWS Truepower.
COP HSL | Current Operating Plan High Sustainability Limit. Entered value should be less than or equal to the STWPF. See COP Practices document for more info. (Note: This refers to the COP HSLs of WGRs that have a COP Resource Status indicating they are online (i.e. it excludes OFF, OUT, OFFNS, EMR, n/a))
ESTIMATED UNCURTAILED OUPUT | This value is obtained from summing the TELEMETERED High Sustainability Limits (HSL) of each WGRs. If a WGR is uncurtailed, the telemetered HSL should be equal to current telemeterd net output capability . If a WGR is being curtailed, the HSL should represent their estimated output potential. See Section 6.5.5.2 Operational Data Requirements for Nodal Protocol for more info.
ABSOLUTE MW ERROR for STWPF | The absolute value of the MW ERROR between the ESTIMATED UNCURTAILED OUTPUT and the aggregated STWPF (Note: A STWPF interval is included in the aggregation only if the unit was online in real-time for that interval (i.e. it excludes Telemetered Resource Statuses OFF, OUT, OFFNS, EMR, n/a). If a WGR's real-time Resource Status changes from Online to Offline in the middle of an hourly interval, the resource is assumed online.)
ABSOLUTE MW ERROR for COP HSL | The absolute value of the MW ERROR between the ESTIMATED UNCURTAILED OUTPUT and the aggreagted COP HSLs.
OVER-FORECASTING | When the actual observation (eg. ESTIMATED UNCURTAILED OUTPUT ) is below the forecasted values (eg. STWPF). In this case the MW ERROR (Actual Observation - Forecasted Value) will be negative.
UNDER-FORECASTING | When the actual observation (eg. ESTIMATED UNCURTAILED OUTPUT ) is above the forecasted values (eg. STWPF). In this case the MW ERROR (Actual Observation - Forecasted Value) will be positive.
HISTOGRAMS | The histograms display the frequency (number of hours) when over-forecasting and under-forecasting occurred in a specified period (eg. On-Peak Hours, Off-Peak Hours …)
REGIONS | A regional error analysis was performed for the following two regions: SOUTH-HOUSTON (withtout HorseHollow Gen-tie (HHGT) Unit) and WEST-NORTH (with the HorseHollow Gen-tie). The HHGT Units are excluded from the SOUTH region since the physical location of the unit is in the WEST. Please note that to protect Resource data, we are not providing the raw data used in this analysis and are only presenting the MAPE results summary.
ASSUMPTIONS | 1. This report assumes accurate WGR Telemetry (MW, HSL, RESOURCE STATUS). 2. This report neglects losses on the HorseHollow Gen-Tie. 3. This report assumes accurate COP entries. 4. A new WGR is only considered in the calculations after we have a full day of actual/forecast/COP HSL data sets.

## QMWG SYSTEM-WIDE DATA
QMWG DATA: SYSTEM-WIDE Monthly Mean Absolute Percent Error -Trend
MONTH-YEAR | Monthly Mean Estimated Uncurtailed Power Output [MW] | Monthly Mean Absolute Percent Error of Installed Capacity [%]
|  | Day-Ahead 1430 Mean |  | Hour-Ahead Mean
|  | STWPF | COP HSL | STWPF | COP HSL
2012-02-01 | 3659.5333 | 10.31% | 10.23% | 7.383% | 7.552%
2012-03-01 | 4422.2454 | 9.179% | 9.22% | 6.318% | 6.339%
2012-04-01 | 3973.7 | 10% | 10% | 6.1% | 6.2%
2012-05-01 | 3683.2 | 10.2% | 10.2% | 6.5% | 6.6%
2012-06-12 | 3389.9174 | 10.66% | 10.7% | 6.033% | 6.217%
2012-07-12 | 2665 | 6.5% | 6.7% | 4.9% | 5.2%
2012-08-12 | 2356.1353 | 6.9% | 7.113% | 4.953% | 5.112%
2012-09-12 | 2873.7 | 7.8% | 7.8% | 4.3% | 4.5%
2012-10-12 | 3465.8 | 8% | 8.3% | 5% | 5.4%
2012-11-12 | 3529 | 6.2% | 6.6% | 4.1% | 4.2%
2012-12-12 | 3893.1 | 8.1% | 8.9% | 5.4% | 5.9%
2013-01-13 | 3008.1092 | 8.315% | 8.294% | 5.045% | 5.169%
2013-02-13 | 3776.9 | 9.7% | 9.9% | 5.7% | 6%

## DAY-AHEAD HISTOGRAMS
ALL HOURS : Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 2
-4250 to -3750 | 7 | 5
-3750 to -3250 | 2 | 2
-3250 to -2750 | 6 | 9
-2750 to -2250 | 22 | 24
-2250 to -1750 | 36 | 42
-1750 to -1250 | 54 | 50
-1250 to -750 | 58 | 64
-750 to -250 | 124 | 133
-250 to 250 | 102 | 101
250 to 750 | 96 | 86
750 to 1250 | 67 | 64
1250 to 1750 | 45 | 42
1750 to 2250 | 35 | 32
2250 to 2750 | 12 | 11
2750 to 3250 | 6 | 5
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 38.84% | 35.71%
Over Forecasting (MW Error <=250) | 45.98% | 49.26%
'ON-PEAK' HOURS (Operating Hours 7-22) :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 1
-4250 to -3750 | 4 | 3
-3750 to -3250 | 2 | 2
-3250 to -2750 | 3 | 4
-2750 to -2250 | 11 | 13
-2250 to -1750 | 26 | 26
-1750 to -1250 | 32 | 31
-1250 to -750 | 36 | 43
-750 to -250 | 86 | 90
-250 to 250 | 69 | 71
250 to 750 | 65 | 57
750 to 1250 | 37 | 35
1250 to 1750 | 36 | 35
1750 to 2250 | 28 | 25
2250 to 2750 | 7 | 7
2750 to 3250 | 6 | 5
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 39.96% | 36.61%
Over Forecasting (MW Error <=250) | 44.64% | 47.54%
'OFF-PEAK' HOURS (Operating Hour 1-6, 23-24) :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 1
-4250 to -3750 | 3 | 2
-3750 to -3250 | 0 | 0
-3250 to -2750 | 3 | 5
-2750 to -2250 | 11 | 11
-2250 to -1750 | 10 | 16
-1750 to -1250 | 22 | 19
-1250 to -750 | 22 | 21
-750 to -250 | 38 | 43
-250 to 250 | 33 | 30
250 to 750 | 31 | 29
750 to 1250 | 30 | 29
1250 to 1750 | 9 | 7
1750 to 2250 | 7 | 7
2250 to 2750 | 5 | 4
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 36.61% | 33.93%
Over Forecasting (MW Error <=250) | 48.66% | 52.68%
Operating Hours 1-2, 23-24 :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 1
-4250 to -3750 | 2 | 1
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 6 | 5
-2250 to -1750 | 5 | 7
-1750 to -1250 | 5 | 5
-1250 to -750 | 12 | 11
-750 to -250 | 13 | 16
-250 to 250 | 20 | 21
250 to 750 | 19 | 16
750 to 1250 | 15 | 17
1250 to 1750 | 7 | 4
1750 to 2250 | 4 | 4
2250 to 2750 | 4 | 3
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 43.75% | 39.29%
Over Forecasting (MW Error <=250) | 38.39% | 41.96%
Operating Hour 3-6 :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 1 | 1
-3750 to -3250 | 0 | 0
-3250 to -2750 | 3 | 4
-2750 to -2250 | 5 | 6
-2250 to -1750 | 5 | 9
-1750 to -1250 | 17 | 14
-1250 to -750 | 10 | 10
-750 to -250 | 25 | 27
-250 to 250 | 13 | 9
250 to 750 | 12 | 13
750 to 1250 | 15 | 12
1250 to 1750 | 2 | 3
1750 to 2250 | 3 | 3
2250 to 2750 | 1 | 1
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 29.46% | 28.57%
Over Forecasting (MW Error <=250) | 58.93% | 63.39%
Operating Hours 7-10
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 1
-4250 to -3750 | 1 | 0
-3750 to -3250 | 1 | 1
-3250 to -2750 | 1 | 2
-2750 to -2250 | 1 | 1
-2250 to -1750 | 9 | 11
-1750 to -1250 | 17 | 16
-1250 to -750 | 11 | 12
-750 to -250 | 22 | 22
-250 to 250 | 13 | 15
250 to 750 | 20 | 19
750 to 1250 | 10 | 6
1250 to 1750 | 4 | 4
1750 to 2250 | 2 | 2
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 32.14% | 27.68%
Over Forecasting (MW Error <=250) | 56.25% | 58.93%
Operating Hours 11-14 :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 1 | 0
-2750 to -2250 | 3 | 4
-2250 to -1750 | 5 | 4
-1750 to -1250 | 5 | 7
-1250 to -750 | 9 | 9
-750 to -250 | 20 | 21
-250 to 250 | 21 | 23
250 to 750 | 16 | 13
750 to 1250 | 6 | 6
1250 to 1750 | 9 | 8
1750 to 2250 | 10 | 11
2250 to 2750 | 3 | 2
2750 to 3250 | 4 | 4
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 42.86% | 39.29%
Over Forecasting (MW Error <=250) | 38.39% | 40.18%
Operating Hours 15-18 :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 6 | 5
-2250 to -1750 | 4 | 4
-1750 to -1250 | 7 | 5
-1250 to -750 | 4 | 6
-750 to -250 | 20 | 25
-250 to 250 | 20 | 17
250 to 750 | 12 | 10
750 to 1250 | 12 | 13
1250 to 1750 | 12 | 14
1750 to 2250 | 10 | 7
2250 to 2750 | 3 | 4
2750 to 3250 | 2 | 1
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 45.54% | 43.75%
Over Forecasting (MW Error <=250) | 36.61% | 41.07%
Operating Hours 19-22 :Day-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 3 | 3
-3750 to -3250 | 1 | 1
-3250 to -2750 | 1 | 1
-2750 to -2250 | 1 | 3
-2250 to -1750 | 8 | 7
-1750 to -1250 | 3 | 3
-1250 to -750 | 12 | 16
-750 to -250 | 24 | 22
-250 to 250 | 15 | 16
250 to 750 | 17 | 15
750 to 1250 | 9 | 10
1250 to 1750 | 11 | 9
1750 to 2250 | 6 | 5
2250 to 2750 | 1 | 1
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 39.29% | 35.71%
Over Forecasting (MW Error <=250) | 47.32% | 50%

## HOUR-AHEAD HISTOGRAMS
ALL HOURS : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 1 | 2
-3750 to -3250 | 1 | 0
-3250 to -2750 | 0 | 2
-2750 to -2250 | 8 | 8
-2250 to -1750 | 8 | 10
-1750 to -1250 | 17 | 28
-1250 to -750 | 64 | 90
-750 to -250 | 180 | 203
-250 to 250 | 197 | 172
250 to 750 | 105 | 92
750 to 1250 | 63 | 40
1250 to 1750 | 18 | 19
1750 to 2250 | 6 | 3
2250 to 2750 | 4 | 3
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 29.17% | 23.36%
Over Forecasting (MW Error <=250) | 41.52% | 51.04%
'ON-PEAK' HOURS (Operating Hours 7-22) : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 1 | 1
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 2 | 1
-2250 to -1750 | 3 | 4
-1750 to -1250 | 6 | 10
-1250 to -750 | 37 | 62
-750 to -250 | 123 | 137
-250 to 250 | 138 | 121
250 to 750 | 69 | 60
750 to 1250 | 46 | 31
1250 to 1750 | 15 | 14
1750 to 2250 | 4 | 3
2250 to 2750 | 4 | 3
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 30.8% | 24.78%
Over Forecasting (MW Error <=250) | 38.39% | 48.21%
'OFF-PEAK' HOURS (Operating Hour 1-6, 23-24) : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 1
-3750 to -3250 | 1 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 6 | 7
-2250 to -1750 | 5 | 6
-1750 to -1250 | 11 | 18
-1250 to -750 | 27 | 28
-750 to -250 | 57 | 66
-250 to 250 | 59 | 51
250 to 750 | 36 | 32
750 to 1250 | 17 | 9
1250 to 1750 | 3 | 5
1750 to 2250 | 2 | 0
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 25.89% | 20.54%
Over Forecasting (MW Error <=250) | 47.77% | 56.7%
Operating Hours 1-2, 23-24 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 0
-2750 to -2250 | 2 | 4
-2250 to -1750 | 2 | 1
-1750 to -1250 | 2 | 8
-1250 to -750 | 11 | 8
-750 to -250 | 24 | 34
-250 to 250 | 33 | 24
250 to 750 | 18 | 21
750 to 1250 | 16 | 8
1250 to 1750 | 3 | 4
1750 to 2250 | 1 | 0
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 33.93% | 29.46%
Over Forecasting (MW Error <=250) | 36.61% | 49.11%
Operating Hour 3-6 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 1
-3750 to -3250 | 1 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 4 | 3
-2250 to -1750 | 3 | 5
-1750 to -1250 | 9 | 10
-1250 to -750 | 16 | 20
-750 to -250 | 33 | 32
-250 to 250 | 26 | 27
250 to 750 | 18 | 11
750 to 1250 | 1 | 1
1250 to 1750 | 0 | 1
1750 to 2250 | 1 | 0
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 17.86% | 11.61%
Over Forecasting (MW Error <=250) | 58.93% | 64.29%
Operating Hours 7-10 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 1 | 1
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 0
-2750 to -2250 | 1 | 1
-2250 to -1750 | 0 | 0
-1750 to -1250 | 3 | 6
-1250 to -750 | 19 | 25
-750 to -250 | 35 | 41
-250 to 250 | 41 | 31
250 to 750 | 7 | 4
750 to 1250 | 4 | 3
1250 to 1750 | 1 | 0
1750 to 2250 | 0 | 0
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 10.71% | 6.25%
Over Forecasting (MW Error <=250) | 52.68% | 66.07%
Operating Hours 11-14 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 0
-2750 to -2250 | 0 | 0
-2250 to -1750 | 0 | 0
-1750 to -1250 | 1 | 1
-1250 to -750 | 2 | 7
-750 to -250 | 34 | 34
-250 to 250 | 27 | 29
250 to 750 | 18 | 15
750 to 1250 | 18 | 16
1250 to 1750 | 6 | 5
1750 to 2250 | 3 | 2
2250 to 2750 | 3 | 3
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 42.86% | 36.61%
Over Forecasting (MW Error <=250) | 33.04% | 37.5%
Operating Hours 15-18 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 0
-2750 to -2250 | 0 | 0
-2250 to -1750 | 1 | 1
-1750 to -1250 | 1 | 1
-1250 to -750 | 2 | 6
-750 to -250 | 19 | 26
-250 to 250 | 43 | 39
250 to 750 | 23 | 24
750 to 1250 | 16 | 7
1250 to 1750 | 5 | 7
1750 to 2250 | 1 | 1
2250 to 2750 | 1 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 41.07% | 34.82%
Over Forecasting (MW Error <=250) | 20.54% | 30.36%
Operating Hours 19-22 : Hour-Ahead
| MW Error STWPF | MW Error COP HSL
X-Axis | (Estimated Uncurtailed Output -STWPF) [MW] | (Estimated Uncurtailed Output - COP HSL) [MW]
<-4250 | 0 | 0
-4250 to -3750 | 0 | 0
-3750 to -3250 | 0 | 0
-3250 to -2750 | 0 | 1
-2750 to -2250 | 1 | 0
-2250 to -1750 | 2 | 3
-1750 to -1250 | 1 | 2
-1250 to -750 | 14 | 24
-750 to -250 | 35 | 36
-250 to 250 | 27 | 22
250 to 750 | 21 | 17
750 to 1250 | 8 | 5
1250 to 1750 | 3 | 2
1750 to 2250 | 0 | 0
2250 to 2750 | 0 | 0
2750 to 3250 | 0 | 0
3250 to 3750 | 0 | 0
3750 to 4250 | 0 | 0
> 4250 | 0 | 0
Percent of Hours
Under Forecasting (MW Error > 250) | 28.57% | 21.43%
Over Forecasting (MW Error <=250) | 47.32% | 58.93%

## COP HSL PERFORMANCE
December 2012
COP HSL PERFORMANCE
By Operating Day | Percent of Hours when: |  | By Operating Hour | Percent of Hours when:
| DAY-AHEAD COP HSL-STWPF > 2% Installed Capacity TARGET 0% | HOUR-AHEAD COP HSL-STWPF > 2% Installed Capacity TARGET 0% |  | DAY-AHEAD COP HSL-STWPF > 2% Installed Capacity TARGET 0% | HOUR-AHEAD COP HSL-STWPF > 2% Installed Capacity TARGET 0%
Monthly Average | 11.76% | 22.77% | Monthly Average | 11.76% | 22.77%
2013-02-01 | 0% | 0% | 1 | 14.29% | 32.14%
2013-02-02 | 0% | 0% | 2 | 14.29% | 35.71%
2013-02-03 | 0% | 12.5% | 3 | 17.86% | 32.14%
2013-02-04 | 0% | 12.5% | 4 | 10.71% | 25%
2013-02-05 | 0% | 0% | 5 | 10.71% | 28.57%
2013-02-06 | 0% | 16.67% | 6 | 10.71% | 14.29%
2013-02-07 | 0% | 4.167% | 7 | 14.29% | 14.29%
2013-02-08 | 0% | 0% | 8 | 10.71% | 17.86%
2013-02-09 | 37.5% | 37.5% | 9 | 10.71% | 17.86%
2013-02-10 | 25% | 20.83% | 10 | 3.571% | 14.29%
2013-02-11 | 0% | 16.67% | 11 | 7.143% | 10.71%
2013-02-12 | 0% | 8.333% | 12 | 7.143% | 10.71%
2013-02-13 | 25% | 25% | 13 | 7.143% | 14.29%
2013-02-14 | 4.167% | 20.83% | 14 | 7.143% | 14.29%
2013-02-15 | 16.67% | 8.333% | 15 | 7.143% | 14.29%
2013-02-16 | 12.5% | 16.67% | 16 | 10.71% | 14.29%
2013-02-17 | 58.33% | 75% | 17 | 10.71% | 21.43%
2013-02-18 | 0% | 25% | 18 | 10.71% | 21.43%
2013-02-19 | 12.5% | 37.5% | 19 | 10.71% | 21.43%
2013-02-20 | 79.17% | 95.83% | 20 | 14.29% | 28.57%
2013-02-21 | 20.83% | 29.17% | 21 | 17.86% | 39.29%
2013-02-22 | 0% | 12.5% | 22 | 17.86% | 42.86%
2013-02-23 | 0% | 4.167% | 23 | 17.86% | 35.71%
2013-02-24 | 0% | 8.333% | 24 | 17.86% | 25%
2013-02-25 | 4.167% | 83.33%
2013-02-26 | 25% | 12.5%
2013-02-27 | 8.333% | 20.83%
2013-02-28 | 0% | 33.33%
Formulas:
By Operating Day = [By Operating Day, row above]+1

## DAY-AHEAD BY OUTPUT LEVEL
February 2013
Day-Ahead Aggregated WPF - By Output Level
|  | ERCOT System Load [MW] | Real-Time Mean |  |  | Day-Ahead 1430 Mean | [9 empty] | By Estimated Uncurtailed Output Level | Percent of Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
By Estimated Uncurtailed Output Level | <1000 | 32077.1912 | 631.5868 | 648.2883 | 16.7015 | 1378.325 | 751.5579 | -730.0367 | 7.241% | 140.6% | 1453.2053 | 820.5987 | -804.917 | 7.907% | 152.4% | <1000 | 7.895% | 10.53% | 7.895% | 7.895%
| 1000-2000 | 32639.072 | 1510.1708 | 1530.8191 | 20.6482 | 2323.7074 | 916.4372 | -792.8883 | 8.83% | 60.96% | 2425.9607 | 996.626 | -895.1416 | 9.603% | 66.24% | 1000-2000 | 20.49% | 7.377% | 15.57% | 20.49%
| 2000-3000 | 32332.3171 | 2427.5798 | 2442.9488 | 15.369 | 3029.0579 | 933.342 | -586.1091 | 8.993% | 38.39% | 3105.5958 | 972.6403 | -662.647 | 9.372% | 40.02% | 2000-3000 | 32.63% | 2.105% | 28.42% | 32.63%
| 3000-4000 | 30543.1987 | 3519.6861 | 3542.3124 | 22.6262 | 3792.5175 | 1214.1638 | -250.2052 | 11.7% | 34.29% | 3859.5165 | 1233.1393 | -317.2041 | 11.88% | 34.83% | 3000-4000 | 56.7% | 5.155% | 55.67% | 56.7%
| 4000-5000 | 31170.1862 | 4393.5921 | 4440.5817 | 46.9896 | 4295.5986 | 1317.9579 | 144.9831 | 12.7% | 29.63% | 4378.9324 | 1323.9422 | 61.6493 | 12.76% | 29.74% | 4000-5000 | 53.52% | 11.27% | 49.3% | 53.52%
| 5000-6000 | 31342.9729 | 5368.2685 | 5436.7216 | 68.4531 | 5068.6091 | 1060.8142 | 368.1125 | 10.22% | 19.55% | 5173.1485 | 1101.8359 | 263.5731 | 10.62% | 20.29% | 5000-6000 | 51.52% | 18.18% | 50% | 51.52%
| 6000-7000 | 30299.7146 | 6439.4163 | 6523.6004 | 84.1841 | 5886.3833 | 955.9751 | 637.217 | 9.211% | 14.64% | 6007.07 | 917.7906 | 516.5304 | 8.843% | 14.07% | 6000-7000 | 76.67% | 20% | 73.33% | 76.67%
| >=7000 | 30822.2688 | 7439.716 | 7774.7346 | 335.0186 | 6855.2306 | 979.3602 | 919.504 | 9.436% | 12.84% | 7004.7306 | 889.8336 | 770.004 | 8.574% | 11.68% | >=7000 | 84.71% | 27.06% | 78.82% | 84.71%

## DAY-AHEAD BY HOUR, ON-OFF PEAK
February 2013
Day-Ahead Aggregated WPF - By Operating Hour
|  | ERCOT System Load [MW] | Real-Time Mean |  |  | Day-Ahead 1430 Mean | [9 empty] | Operating Hour |  | Percent of Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
All Hours Average |  | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3897.7277 | 1011.247 | -120.8115 | 9.744% | 45.33% | 3994.0086 | 1031.8357 | -217.0925 | 9.942% | 47.82% | All Hours Average |  | 45.68% | 11.76% | 42.41% | 45.68%
'Off-Peak' Hours (1-6,23-24) |  | 28253.9071 | 4018.2701 | 4112.4485 | 94.1784 | 4363.1938 | 1010.2614 | -250.7452 | 9.734% | 42.7% | 4476.4438 | 1060.2914 | -363.9952 | 10.22% | 46.47% | Off-Peak Hours (1-6,23-24) |  | 38.71% | 12.9% | 35.48% | 38.71%
'On-Peak' Hours (7-22) |  | 33135.7448 | 3547.2548 | 3609.15 | 61.8952 | 3664.9946 | 1011.7398 | -55.8447 | 9.748% | 46.64% | 3752.7911 | 1017.6078 | -143.6411 | 9.805% | 48.49% | On-Peak Hours (7-22) |  | 42.54% | 9.476% | 39.72% | 42.54%
By Operating Hour | 1 | 27667.8458 | 4333.2378 | 4441.3649 | 108.1271 | 4394.9 | 855.3871 | 46.4649 | 8.242% | 34.86% | 4530.2429 | 888.3928 | -88.878 | 8.56% | 37.73% | 1 | Number of Hours when: | 17 | 4 | 13 | 17
| 2 | 26973.9786 | 4200.6242 | 4304.1763 | 103.552 | 4377.65 | 861.6023 | -73.4737 | 8.302% | 33.21% | 4492.7893 | 930.1763 | -188.613 | 8.963% | 37.01% | 2 |  | 11 | 4 | 11 | 11
| 3 | 26727.0852 | 4040.3346 | 4141.0629 | 100.7283 | 4359.0857 | 864.2928 | -218.0228 | 8.328% | 32.37% | 4460.7107 | 941.6821 | -319.6478 | 9.073% | 36.34% | 3 |  | 9 | 5 | 9 | 9
| 4 | 26867.0931 | 3858.59 | 3960.7758 | 102.1859 | 4336.5036 | 1053.043 | -375.7277 | 10.15% | 38.27% | 4438.4679 | 1126.8688 | -477.692 | 10.86% | 42.18% | 4 |  | 10 | 3 | 9 | 10
| 5 | 27632.9234 | 3664.5957 | 3738.5774 | 73.9817 | 4319.2786 | 1111.431 | -580.7012 | 10.71% | 41.43% | 4418.3929 | 1192.7111 | -679.8155 | 11.49% | 45.68% | 5 |  | 10 | 3 | 9 | 10
| 6 | 29773.4606 | 3585.4175 | 3648.2905 | 62.873 | 4297.825 | 1122.9333 | -649.5345 | 10.82% | 42.48% | 4397.1893 | 1196.8904 | -748.8988 | 11.53% | 46.32% | 6 |  | 8 | 3 | 8 | 8
| 7 | 33277.2537 | 3529.235 | 3568.0168 | 38.7818 | 4234.1179 | 1124.616 | -666.101 | 10.84% | 42% | 4342.4857 | 1173.8767 | -774.4689 | 11.31% | 44.83% | 7 |  | 9 | 4 | 9 | 9
| 8 | 34491.8526 | 3539.6341 | 3577.963 | 38.3289 | 4092.9571 | 981.4789 | -514.9942 | 9.457% | 36.93% | 4205.1929 | 1020.4218 | -627.2299 | 9.832% | 39.32% | 8 |  | 8 | 3 | 8 | 8
| 9 | 34156.5464 | 3373.7918 | 3427.0123 | 53.2205 | 3881.7929 | 889.0752 | -454.7806 | 8.567% | 41.95% | 3979.6964 | 937.8133 | -552.6841 | 9.036% | 44.16% | 9 |  | 9 | 3 | 8 | 9
| 10 | 33950.9527 | 3345.8809 | 3432.343 | 86.4621 | 3569.2429 | 855.4945 | -136.8999 | 8.243% | 46.75% | 3650.4464 | 863.6807 | -218.1034 | 8.322% | 48.34% | 10 |  | 14 | 1 | 11 | 14
| 11 | 33634.3941 | 3586.3944 | 3669.9358 | 83.5414 | 3423.4643 | 923.1441 | 246.4715 | 8.895% | 46.39% | 3495.1036 | 907.1962 | 174.8323 | 8.741% | 47.47% | 11 |  | 18 | 2 | 15 | 18
| 12 | 33092.9227 | 3568.646 | 3633.3198 | 64.6737 | 3403.1857 | 998.8599 | 230.1341 | 9.624% | 52.01% | 3468.8857 | 993.4527 | 164.4341 | 9.572% | 53.22% | 12 |  | 15 | 2 | 15 | 15
| 13 | 32554.9016 | 3490.1192 | 3545.0568 | 54.9376 | 3415.7357 | 1058.2473 | 129.3211 | 10.2% | 54.72% | 3483.6429 | 1053.7402 | 61.414 | 10.15% | 55.96% | 13 |  | 14 | 2 | 14 | 14
| 14 | 32176.5925 | 3518.7033 | 3569.5255 | 50.8221 | 3458.9964 | 1061.1787 | 110.529 | 10.22% | 52.9% | 3538.8179 | 1068.7508 | 30.7076 | 10.3% | 54.67% | 14 |  | 13 | 2 | 12 | 13
| 15 | 31790.7457 | 3617.9186 | 3672.2501 | 54.3315 | 3554.4143 | 1105.5507 | 117.8358 | 10.65% | 45.05% | 3628.875 | 1107.5236 | 43.3751 | 10.67% | 46.23% | 15 |  | 13 | 2 | 12 | 13
| 16 | 31564.5667 | 3717.0181 | 3778.3743 | 61.3563 | 3592.8857 | 1077.8526 | 185.4886 | 10.39% | 39.5% | 3659.4714 | 1076.3955 | 118.9029 | 10.37% | 40.09% | 16 |  | 12 | 3 | 12 | 12
| 17 | 31619.3104 | 3702.956 | 3775.8704 | 72.9143 | 3532.9821 | 1080.368 | 242.8882 | 10.41% | 38.65% | 3602.4071 | 1073.4712 | 173.4632 | 10.34% | 38.97% | 17 |  | 16 | 3 | 15 | 16
| 18 | 31999.6914 | 3453.7114 | 3516.5921 | 62.8807 | 3257.0607 | 959.3134 | 259.5314 | 9.243% | 37.64% | 3333.6786 | 927.0571 | 182.9136 | 8.932% | 37.72% | 18 |  | 18 | 3 | 17 | 18
| 19 | 33824.9951 | 3144.9909 | 3199.8666 | 54.8757 | 3333.0607 | 856.3658 | -133.1942 | 8.251% | 49.46% | 3424.3143 | 836.0023 | -224.4477 | 8.055% | 51.06% | 19 |  | 15 | 3 | 14 | 15
| 20 | 34647.642 | 3394.8642 | 3452.4689 | 57.6047 | 3663.1964 | 1002.6711 | -210.7276 | 9.661% | 55.1% | 3763.5 | 1009.4389 | -311.0311 | 9.726% | 58.72% | 20 |  | 12 | 4 | 12 | 12
| 21 | 34225.5582 | 3766.1424 | 3839.4934 | 73.351 | 4020.7893 | 1102.1466 | -181.2959 | 10.62% | 53.1% | 4134.6643 | 1112.5157 | -295.1709 | 10.72% | 56.62% | 21 |  | 13 | 5 | 11 | 13
| 22 | 33163.9914 | 4006.0707 | 4088.3108 | 82.2401 | 4206.0321 | 1111.4744 | -117.7213 | 10.71% | 54.12% | 4333.475 | 1120.3887 | -245.1642 | 10.8% | 58.47% | 22 |  | 12 | 5 | 12 | 12
| 23 | 31234.4151 | 4191.9971 | 4289.0738 | 97.0767 | 4338.2143 | 1101.2383 | -49.1404 | 10.61% | 60.03% | 4466.4679 | 1088.8927 | -177.394 | 10.49% | 63.88% | 23 |  | 16 | 5 | 14 | 16
| 24 | 29154.4552 | 4271.364 | 4376.2665 | 104.9025 | 4482.0929 | 1112.1633 | -105.8264 | 10.72% | 58.96% | 4607.2893 | 1116.7169 | -231.0228 | 10.76% | 62.59% | 24 |  | 15 | 5 | 15 | 15
Operating Hours 23-24, 1-2 |  | 28757.6737 | 4249.3058 | 4352.7204 | 103.4146 | 4398.2143 | 982.5977 | -45.4939 | 9.468% | 46.77% | 4524.1973 | 1006.0447 | -171.477 | 9.694% | 50.3% | Operating Hours 23-24, 1-2 |  | 47.58% | 14.52% | 42.74% | 47.58%
Operating Hours 3-6 |  | 27750.1406 | 3787.2345 | 3872.1767 | 84.9422 | 4328.1732 | 1037.925 | -455.9965 | 10% | 38.64% | 4428.6902 | 1114.5381 | -556.5135 | 10.74% | 42.63% | Operating Hours 3-6 |  | 29.84% | 11.29% | 28.23% | 29.84%
Operating Hours 7-10 |  | 33969.1514 | 3447.1354 | 3501.3338 | 54.1983 | 3944.5277 | 962.6662 | -443.1939 | 9.276% | 41.9% | 4044.4554 | 998.9481 | -543.1216 | 9.625% | 44.16% | Operating Hours 7-10 |  | 32.26% | 8.871% | 29.03% | 32.26%
Operating Hours 11-14 |  | 32864.7027 | 3540.9658 | 3604.4595 | 63.4937 | 3425.3455 | 1010.3575 | 179.1139 | 9.735% | 51.5% | 3496.6125 | 1005.785 | 107.847 | 9.691% | 52.83% | Operating Hours 11-14 |  | 48.39% | 6.452% | 45.16% | 48.39%
Operating Hours 15-18 |  | 31743.5786 | 3622.901 | 3685.7717 | 62.8707 | 3484.3357 | 1055.7712 | 201.436 | 10.17% | 40.21% | 3556.108 | 1046.1118 | 129.6637 | 10.08% | 40.75% | Operating Hours 15-18 |  | 47.58% | 8.871% | 45.16% | 47.58%
Operating Hours 19-22 |  | 33965.5467 | 3578.0171 | 3645.0349 | 67.0179 | 3805.7696 | 1018.1645 | -160.7347 | 9.81% | 52.94% | 3913.9884 | 1019.5864 | -268.9535 | 9.824% | 56.22% | Operating Hours 19-22 |  | 41.94% | 13.71% | 39.52% | 41.94%

## DAY-AHEAD DAILY MEAN
February 2013
Day-Ahead Aggregated WPF - Daily Mean
Operating Day | ERCOT System Load [MW] | Real-Time Daily Mean |  |  | Day-Ahead 1430 Daily Mean | [9 empty] | Operating Day | Percent of Hours when:
|  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[6 empty] | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
Monthly Average | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3897.7277 | 1011.247 | -120.8115 | 9.744% | 45.33% | 3994.0086 | 1031.8357 | -217.0925 | 9.942% | 47.82% |  | 45.68% | 11.76% | 42.41% | 45.68%
2013-02-01 | 32658.7786 | 3639.1257 | 3686.0787 | 46.953 | 3001.8917 | 1137.1798 | 684.187 | 10.96% | 32.3% | 3138.875 | 1117.1965 | 547.2037 | 10.76% | 33.97% | 2013-02-01 | 54.17% | 0% | 54.17% | 54.17%
2013-02-02 | 29393.6932 | 3166.5569 | 3170.2058 | 3.6489 | 2389.9375 | 1164.6865 | 780.2683 | 11.22% | 48.41% | 2406.5875 | 1165.3865 | 763.6183 | 11.23% | 49.02% | 2013-02-02 | 66.67% | 0% | 66.67% | 66.67%
2013-02-03 | 28652.3427 | 3816.8101 | 3818.8872 | 2.0771 | 2794.7625 | 1318.2672 | 1024.1247 | 12.7% | 39.33% | 2846.8792 | 1310.4803 | 972.008 | 12.63% | 41.03% | 2013-02-03 | 62.5% | 0% | 58.33% | 62.5%
2013-02-04 | 30155.1557 | 3028.5372 | 3042.9548 | 14.4176 | 3938.5417 | 902.1396 | -895.5869 | 8.692% | 32.67% | 4013.3417 | 970.3869 | -970.3869 | 9.35% | 35.85% | 2013-02-04 | 4.167% | 0% | 0% | 4.167%
2013-02-05 | 30868.8698 | 1209.3239 | 1219.1493 | 9.8254 | 1226.4125 | 511.3608 | -7.2632 | 4.927% | 91.47% | 1283.375 | 544.0494 | -64.2257 | 5.242% | 99.22% | 2013-02-05 | 37.5% | 0% | 33.33% | 37.5%
2013-02-06 | 30610.9759 | 3071.3932 | 3087.3536 | 15.9605 | 2814.5083 | 566.2435 | 272.8453 | 5.456% | 18.03% | 2816.6 | 560.5852 | 270.7536 | 5.401% | 17.91% | 2013-02-06 | 62.5% | 0% | 62.5% | 62.5%
2013-02-07 | 30500.7563 | 3960.9827 | 4030.1195 | 69.1368 | 3585.4708 | 688.2522 | 444.6487 | 6.632% | 17.32% | 3613.475 | 667.5406 | 416.6445 | 6.432% | 16.72% | 2013-02-07 | 66.67% | 0% | 70.83% | 66.67%
2013-02-08 | 30132.8696 | 3089.5321 | 3101.1631 | 11.631 | 3075.175 | 321.2078 | 25.9881 | 3.095% | 11.65% | 3161.8833 | 315.6219 | -60.7202 | 3.041% | 12.13% | 2013-02-08 | 45.83% | 0% | 33.33% | 45.83%
2013-02-09 | 30165.599 | 7634.0866 | 7731.2296 | 97.143 | 6795.275 | 935.9546 | 935.9546 | 9.018% | 11.81% | 6994.8917 | 736.6597 | 736.3379 | 7.098% | 9.241% | 2013-02-09 | 100% | 37.5% | 95.83% | 100%
2013-02-10 | 28415.358 | 3871.6319 | 3895.4641 | 23.8322 | 5391.5625 | 1496.0984 | -1496.0984 | 14.42% | 124.5% | 5532.0583 | 1636.5942 | -1636.5942 | 15.77% | 135.5% | 2013-02-10 | 0% | 25% | 0% | 0%
2013-02-11 | 31730.6495 | 2519.4337 | 2523.6832 | 4.2495 | 4192.7583 | 1669.0751 | -1669.0751 | 16.08% | 91.99% | 4239.675 | 1715.9918 | -1715.9918 | 16.53% | 95.14% | 2013-02-11 | 0% | 0% | 0% | 0%
2013-02-12 | 32576.8689 | 2978.9997 | 3023.9627 | 44.963 | 4063.1792 | 1422.195 | -1039.2164 | 13.7% | 74.87% | 4114.7 | 1465.0158 | -1090.7373 | 14.12% | 77.67% | 2013-02-12 | 20.83% | 0% | 20.83% | 20.83%
2013-02-13 | 33027.1346 | 1223.7074 | 1235.8274 | 12.1199 | 2065.3333 | 840.113 | -829.506 | 8.095% | 82.38% | 2198.2083 | 967.5297 | -962.381 | 9.322% | 93.59% | 2013-02-13 | 4.167% | 25% | 4.167% | 4.167%
2013-02-14 | 32693.8388 | 2526.1252 | 2541.6121 | 15.4868 | 2078.2958 | 709.2604 | 463.3162 | 6.834% | 31.2% | 2123.6792 | 710.7271 | 417.9329 | 6.848% | 31.51% | 2013-02-14 | 83.33% | 4.167% | 83.33% | 83.33%
2013-02-15 | 33125.5147 | 3889.0233 | 3936.5723 | 47.5491 | 2836.3417 | 1419.1891 | 1100.2307 | 13.67% | 51.81% | 2918.3417 | 1440.5641 | 1018.2307 | 13.88% | 58.59% | 2013-02-15 | 79.17% | 16.67% | 79.17% | 79.17%
2013-02-16 | 32395.7082 | 2135.8694 | 2153.6275 | 17.7581 | 3455.625 | 1337.8847 | -1301.9975 | 12.89% | 86.84% | 3540.275 | 1410.6597 | -1386.6475 | 13.59% | 91.45% | 2013-02-16 | 8.333% | 12.5% | 8.333% | 8.333%
2013-02-17 | 30223.127 | 7110.4923 | 7449.0893 | 338.5969 | 6408.3167 | 1054.6472 | 1040.7726 | 10.16% | 14.44% | 6595.1833 | 936.3695 | 853.9059 | 9.022% | 12.75% | 2013-02-17 | 87.5% | 58.33% | 83.33% | 87.5%
2013-02-18 | 30425.9863 | 5793.6812 | 6120.5499 | 326.8687 | 5521.925 | 779.8528 | 598.6249 | 7.514% | 13.27% | 5624.0792 | 814.9678 | 496.4708 | 7.852% | 13.62% | 2013-02-18 | 62.5% | 0% | 54.17% | 62.5%
2013-02-19 | 31196.6078 | 4271.3681 | 4303.2326 | 31.8645 | 5370.7583 | 1349.7995 | -1067.5258 | 13.01% | 37.79% | 5494.35 | 1420.9553 | -1191.1174 | 13.69% | 40.13% | 2013-02-19 | 29.17% | 12.5% | 25% | 29.17%
2013-02-20 | 33461.2597 | 5187.0068 | 5300.5495 | 113.5427 | 6211.45 | 1083.9492 | -910.9005 | 10.44% | 27.32% | 6466.9458 | 1198.1451 | -1166.3963 | 11.54% | 30.3% | 2013-02-20 | 25% | 79.17% | 16.67% | 25%
2013-02-21 | 32340.0881 | 4863.3988 | 4951.5059 | 88.1072 | 6844.5333 | 1973.0192 | -1893.0274 | 19.01% | 59.97% | 6990.1583 | 2109.2775 | -2038.6524 | 20.32% | 63.55% | 2013-02-21 | 12.5% | 20.83% | 12.5% | 12.5%
2013-02-22 | 33092.0778 | 2078.6557 | 2088.5159 | 9.8602 | 1904.9958 | 550.6133 | 183.5201 | 5.305% | 28.64% | 1999.7292 | 551.4901 | 88.7867 | 5.314% | 29.84% | 2013-02-22 | 54.17% | 0% | 50% | 54.17%
2013-02-23 | 31344.6674 | 2287.3555 | 2320.7534 | 33.3979 | 2418.4875 | 766.4815 | -97.7341 | 7.385% | 36.61% | 2491.15 | 786.9498 | -170.3966 | 7.582% | 38.75% | 2013-02-23 | 33.33% | 0% | 29.17% | 33.33%
2013-02-24 | 29651.5147 | 5736.3765 | 5828.893 | 92.5165 | 5673.7208 | 1092.7822 | 155.1722 | 10.53% | 22.01% | 5762.0917 | 1070.9883 | 66.8013 | 10.32% | 21.9% | 2013-02-24 | 66.67% | 0% | 58.33% | 66.67%
2013-02-25 | 31724.1458 | 6520.2212 | 6861.0907 | 340.8696 | 6996.5 | 919.7619 | -135.4093 | 8.862% | 19.29% | 7088.0042 | 910.7002 | -226.9134 | 8.775% | 19.43% | 2013-02-25 | 62.5% | 4.167% | 58.33% | 62.5%
2013-02-26 | 33871.3596 | 2558.8567 | 2614.6232 | 55.7665 | 3047.1833 | 1126.5964 | -432.5602 | 10.86% | 106.5% | 3146.4875 | 1199.3344 | -531.8643 | 11.56% | 110.4% | 2013-02-26 | 29.17% | 25% | 25% | 29.17%
2013-02-27 | 33285.0804 | 4270.726 | 4381.2587 | 110.5327 | 3515.8625 | 873.3044 | 865.3962 | 8.415% | 19.7% | 3607.3333 | 790.0559 | 773.9254 | 7.612% | 17.48% | 2013-02-27 | 91.67% | 8.333% | 87.5% | 91.67%
2013-02-28 | 34517.0085 | 1279.9999 | 1335.6992 | 55.6992 | 1517.5708 | 305.0009 | -181.8717 | 2.939% | 37.01% | 1623.8833 | 367.1762 | -288.1842 | 3.538% | 42.08% | 2013-02-28 | 29.17% | 0% | 16.67% | 29.17%
Formulas:
Operating Day = [Operating Day]

## DAY-AHEAD HOURLY MEAN
February 2013
Day-Ahead Aggregated WPF - Hourly Mean
Operating Day | Operating Hour | ERCOT System Load [MW] | Real-Time |  |  | Day-Ahead 1430 | [9 empty] | Operating Hour | Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
Monthly Average |  | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3897.7277 | 1011.247 | -120.8115 | 9.744% | 45.33% | 3994.0086 | 1031.8357 | -217.0925 | 9.942% | 47.82% | Average | 45.68% | 11.76% | 42.41% | 45.68%
Monthly Standard Deviation |  | 3458.3871 | 2243.6544 | 2325.6638 | 176.1796 | 2072.1694 | 800.822 | 1284.8515 | 7.716% | 63.17% | 2103.2162 | 815.0144 | 1297.4285 | 7.853% | 67.63% | St. Deviation
Monthly Maximum |  | 40736.9259 | 8526.8431 | 8854.9324 | 1574.3329 | 8885.1 | 4208.503 | 3118.5343 | 40.55% | 655.7% | 9108 | 4379.003 | 3109.0343 | 42.19% | 713.4% | Max.
Monthly Minimum |  | 23611.8924 | 135.1685 | 143.8527 | -42.961 | 642.3 | 4.2293 | -4208.503 | 0.00040751 | 0.00087392 | 667.9 | 3.8611 | -4379.003 | 0.0372% | 0.05805%
2013-02-01 | 1 | 28903.2237 | 3176.1174 | 3185.6333 | 9.5159 | 2847.9 | 337.7333 | 337.7333 | 3.254% | 10.6% | 3034.7 | 150.9333 | 150.9333 | 1.454% | 4.738% | 1 | 1 | 0 | 1 | 1
2013-02-01 | 2 | 28565.4173 | 2903.9421 | 2912.5707 | 8.6286 | 2916.8 | 4.2293 | -4.2293 | 0.04075% | 0.1452% | 3059.9 | 147.3293 | -147.3293 | 1.42% | 5.058% | 2 | 0 | 0 | 0 | 0
2013-02-01 | 3 | 28719.4526 | 2296.8456 | 2300.1776 | 3.332 | 2785 | 484.8224 | -484.8224 | 4.671% | 21.08% | 2913.4 | 613.2224 | -613.2224 | 5.909% | 26.66% | 3 | 0 | 0 | 0 | 0
2013-02-01 | 4 | 29209.5197 | 2107.0549 | 2112.7068 | 5.6519 | 2458.8 | 346.0932 | -346.0932 | 3.335% | 16.38% | 2592.3 | 479.5932 | -479.5932 | 4.621% | 22.7% | 4 | 0 | 0 | 0 | 0
2013-02-01 | 5 | 30503.9308 | 1861.1293 | 1872.3455 | 11.2162 | 2270.1 | 397.7545 | -397.7545 | 3.832% | 21.24% | 2431.6 | 559.2545 | -559.2545 | 5.389% | 29.87% | 5 | 0 | 0 | 0 | 0
2013-02-01 | 6 | 33457.6174 | 1842.8186 | 1855.7023 | 12.8837 | 2317.2 | 461.4977 | -461.4977 | 4.447% | 24.87% | 2476.3 | 620.5977 | -620.5977 | 5.98% | 33.44% | 6 | 0 | 0 | 0 | 0
2013-02-01 | 7 | 38169.9799 | 1842.1573 | 1856.1608 | 14.0035 | 2248.4 | 392.2392 | -392.2392 | 3.779% | 21.13% | 2408.9 | 552.7392 | -552.7392 | 5.326% | 29.78% | 7 | 0 | 0 | 0 | 0
2013-02-01 | 8 | 39596.6815 | 1771.4323 | 1796.1919 | 24.7596 | 2311.5 | 515.3081 | -515.3081 | 4.965% | 28.69% | 2484.4 | 688.2081 | -688.2081 | 6.631% | 38.31% | 8 | 0 | 0 | 0 | 0
2013-02-01 | 9 | 38139.0816 | 1546.2695 | 1563.9631 | 17.6936 | 2498.2 | 934.2369 | -934.2369 | 9.002% | 59.74% | 2608.4 | 1044.4369 | -1044.4369 | 10.06% | 66.78% | 9 | 0 | 0 | 0 | 0
2013-02-01 | 10 | 36747.1527 | 974.4528 | 982.002 | 7.5492 | 1952.8 | 970.798 | -970.798 | 9.354% | 98.86% | 2023.3 | 1041.298 | -1041.298 | 10.03% | 106% | 10 | 0 | 0 | 0 | 0
2013-02-01 | 11 | 35470.6573 | 1167.7999 | 1174.3049 | 6.505 | 1840.4 | 666.0951 | -666.0951 | 6.418% | 56.72% | 1918.4 | 744.0951 | -744.0951 | 7.17% | 63.36% | 11 | 0 | 0 | 0 | 0
2013-02-01 | 12 | 34103.5191 | 1701.6092 | 1698.8609 | -2.7483 | 1961.7 | 262.8391 | -262.8391 | 2.533% | 15.47% | 2048 | 349.1391 | -349.1391 | 3.364% | 20.55% | 12 | 0 | 0 | 0 | 0
2013-02-01 | 13 | 32920.1769 | 2650.61 | 2646.5781 | -4.0319 | 2233.9 | 412.6781 | 412.6781 | 3.976% | 15.59% | 2330 | 316.5781 | 316.5781 | 3.05% | 11.96% | 13 | 1 | 0 | 1 | 1
2013-02-01 | 14 | 32258.5193 | 3791.3046 | 3784.776 | -6.5286 | 2453.5 | 1331.276 | 1331.276 | 12.83% | 35.17% | 2563.8 | 1220.976 | 1220.976 | 11.76% | 32.26% | 14 | 1 | 0 | 1 | 1
2013-02-01 | 15 | 31634.0832 | 4793.1525 | 4785.2925 | -7.8599 | 2808.4 | 1976.8925 | 1976.8925 | 19.05% | 41.31% | 2927.9 | 1857.3925 | 1857.3925 | 17.9% | 38.81% | 15 | 1 | 0 | 1 | 1
2013-02-01 | 16 | 31086.6036 | 4821.9216 | 4818.3999 | -3.5217 | 2933.3 | 1885.0999 | 1885.0999 | 18.16% | 39.12% | 3051.8 | 1766.5999 | 1766.5999 | 17.02% | 36.66% | 16 | 1 | 0 | 1 | 1
2013-02-01 | 17 | 30819.4854 | 5391.8369 | 5394.7412 | 2.9043 | 2725.3 | 2669.4412 | 2669.4412 | 25.72% | 49.48% | 2850.2 | 2544.5412 | 2544.5412 | 24.52% | 47.17% | 17 | 1 | 0 | 1 | 1
2013-02-01 | 18 | 31053.0181 | 4874.8601 | 4881.562 | 6.7019 | 2432.8 | 2448.762 | 2448.762 | 23.59% | 50.16% | 2558.8 | 2322.762 | 2322.762 | 22.38% | 47.58% | 18 | 1 | 0 | 1 | 1
2013-02-01 | 19 | 33039.3482 | 4407.9627 | 4420.8684 | 12.9057 | 2980.9 | 1439.9684 | 1439.9684 | 13.87% | 32.57% | 3135.4 | 1285.4684 | 1285.4684 | 12.39% | 29.08% | 19 | 1 | 0 | 1 | 1
2013-02-01 | 20 | 33403.3872 | 5905.9255 | 5975.0626 | 69.137 | 3922.4 | 2052.6626 | 2052.6626 | 19.78% | 34.35% | 4099.1 | 1875.9626 | 1875.9626 | 18.08% | 31.4% | 20 | 1 | 0 | 1 | 1
2013-02-01 | 21 | 33109.2029 | 6660.6719 | 6850.3465 | 189.6746 | 4890.7 | 1959.6465 | 1959.6465 | 18.88% | 28.61% | 5084.7 | 1765.6465 | 1765.6465 | 17.01% | 25.77% | 21 | 1 | 0 | 1 | 1
2013-02-01 | 22 | 32452.2227 | 6984.9051 | 7292.1243 | 307.2191 | 5304.2 | 1987.9243 | 1987.9243 | 19.15% | 27.26% | 5484.2 | 1807.9243 | 1807.9243 | 17.42% | 24.79% | 22 | 1 | 0 | 1 | 1
2013-02-01 | 23 | 31061.5721 | 7017.4619 | 7402.0304 | 384.5685 | 5488 | 1914.0304 | 1914.0304 | 18.44% | 25.86% | 5645.7 | 1756.3304 | 1756.3304 | 16.92% | 23.73% | 23 | 1 | 0 | 1 | 1
2013-02-01 | 24 | 29386.8325 | 6846.7748 | 6903.4861 | 56.7113 | 5463.2 | 1440.2861 | 1440.2861 | 13.88% | 20.86% | 5601.8 | 1301.6861 | 1301.6861 | 12.54% | 18.86% | 24 | 1 | 0 | 1 | 1
2013-02-02 | 1 | 27878.9467 | 6490.5691 | 6490.108 | -0.46103 | 5235.4 | 1254.708 | 1254.708 | 12.09% | 19.33% | 5255.1 | 1235.008 | 1235.008 | 11.9% | 19.03% | 1 | 1 | 0 | 1 | 1
2013-02-02 | 2 | 27069.7084 | 6133.4399 | 6143.7593 | 10.3193 | 5024.9 | 1118.8593 | 1118.8593 | 10.78% | 18.21% | 5028.7 | 1115.0593 | 1115.0593 | 10.74% | 18.15% | 2 | 1 | 0 | 1 | 1
2013-02-02 | 3 | 26605.6481 | 5566.7216 | 5571.0564 | 4.3348 | 4803.2 | 767.8564 | 767.8564 | 7.399% | 13.78% | 4779.2 | 791.8564 | 791.8564 | 7.63% | 14.21% | 3 | 1 | 0 | 1 | 1
2013-02-02 | 4 | 26544.8923 | 5032.4626 | 5046.3782 | 13.9156 | 4558.2 | 488.1782 | 488.1782 | 4.704% | 9.674% | 4544.8 | 501.5782 | 501.5782 | 4.833% | 9.939% | 4 | 1 | 0 | 1 | 1
2013-02-02 | 5 | 26879.1872 | 4176.7663 | 4186.2765 | 9.5101 | 4013.8 | 172.4765 | 172.4765 | 1.662% | 4.12% | 4028.6 | 157.6765 | 157.6765 | 1.519% | 3.767% | 5 | 1 | 0 | 1 | 1
2013-02-02 | 6 | 28071.9553 | 3420.9208 | 3429.8217 | 8.9009 | 3599.3 | 169.4783 | -169.4783 | 1.633% | 4.941% | 3602.3 | 172.4783 | -172.4783 | 1.662% | 5.029% | 6 | 0 | 0 | 0 | 0
2013-02-02 | 7 | 29641.7545 | 2482.8561 | 2492.9852 | 10.1291 | 3220.9 | 727.9148 | -727.9148 | 7.014% | 29.2% | 3230.9 | 737.9148 | -737.9148 | 7.11% | 29.6% | 7 | 0 | 0 | 0 | 0
2013-02-02 | 8 | 30885.7539 | 2436.9042 | 2446.5822 | 9.6781 | 2577.5 | 130.9178 | -130.9178 | 1.261% | 5.351% | 2609.5 | 162.9178 | -162.9178 | 1.57% | 6.659% | 8 | 0 | 0 | 0 | 0
2013-02-02 | 9 | 31622.2274 | 3032.7336 | 3040.6248 | 7.8912 | 2025.4 | 1015.2248 | 1015.2248 | 9.782% | 33.39% | 2065.6 | 975.0248 | 975.0248 | 9.395% | 32.07% | 9 | 1 | 0 | 1 | 1
2013-02-02 | 10 | 31543.065 | 3467.4311 | 3466.3619 | -1.0692 | 1670.8 | 1795.5619 | 1795.5619 | 17.3% | 51.8% | 1696.8 | 1769.5619 | 1769.5619 | 17.05% | 51.05% | 10 | 1 | 0 | 1 | 1
2013-02-02 | 11 | 31173.0258 | 4456.7679 | 4456.9822 | 0.21428 | 1664.5 | 2792.4822 | 2792.4822 | 26.91% | 62.65% | 1680.6 | 2776.3822 | 2776.3822 | 26.75% | 62.29% | 11 | 1 | 0 | 1 | 1
2013-02-02 | 12 | 30601.4203 | 4693.9226 | 4695.3365 | 1.4139 | 1706.3 | 2989.0365 | 2989.0365 | 28.8% | 63.66% | 1710.1 | 2985.2365 | 2985.2365 | 28.76% | 63.58% | 12 | 1 | 0 | 1 | 1
2013-02-02 | 13 | 30036.3124 | 3998.8734 | 4001.6153 | 2.7419 | 1689.3 | 2312.3153 | 2312.3153 | 22.28% | 57.78% | 1682 | 2319.6153 | 2319.6153 | 22.35% | 57.97% | 13 | 1 | 0 | 1 | 1
2013-02-02 | 14 | 29517.5566 | 3550.2428 | 3553.0769 | 2.8341 | 1652.7 | 1900.3769 | 1900.3769 | 18.31% | 53.49% | 1649 | 1904.0769 | 1904.0769 | 18.35% | 53.59% | 14 | 1 | 0 | 1 | 1
2013-02-02 | 15 | 29229.8271 | 3449.0174 | 3440.5 | -8.5174 | 1462.9 | 1977.6 | 1977.6 | 19.05% | 57.48% | 1473.4 | 1967.1 | 1967.1 | 18.95% | 57.17% | 15 | 1 | 0 | 1 | 1
2013-02-02 | 16 | 29131.8985 | 3477.2609 | 3448.7004 | -28.5605 | 1329.1 | 2119.6004 | 2119.6004 | 20.42% | 61.46% | 1346.4 | 2102.3004 | 2102.3004 | 20.26% | 60.96% | 16 | 1 | 0 | 1 | 1
2013-02-02 | 17 | 29208.9046 | 2814.1586 | 2813.8832 | -0.27537 | 1213.9 | 1599.9832 | 1599.9832 | 15.42% | 56.86% | 1239.3 | 1574.5832 | 1574.5832 | 15.17% | 55.96% | 17 | 1 | 0 | 1 | 1
2013-02-02 | 18 | 29489.3291 | 1974.0312 | 1977.6161 | 3.5849 | 1126.2 | 851.4161 | 851.4161 | 8.204% | 43.05% | 1155.6 | 822.0161 | 822.0161 | 7.92% | 41.57% | 18 | 1 | 0 | 1 | 1
2013-02-02 | 19 | 31246.7644 | 1401.0812 | 1408.0817 | 7.0004 | 1224.3 | 183.7817 | 183.7817 | 1.771% | 13.05% | 1257.1 | 150.9817 | 150.9817 | 1.455% | 10.72% | 19 | 1 | 0 | 1 | 1
2013-02-02 | 20 | 31544.0224 | 1097.3471 | 1098.7455 | 1.3984 | 1288.7 | 189.9545 | -189.9545 | 1.83% | 17.29% | 1331.9 | 233.1545 | -233.1545 | 2.247% | 21.22% | 20 | 0 | 0 | 0 | 0
2013-02-02 | 21 | 31005.7798 | 835.8227 | 839.0936 | 3.2708 | 1393.2 | 554.1064 | -554.1064 | 5.339% | 66.04% | 1433 | 593.9064 | -593.9064 | 5.722% | 70.78% | 21 | 0 | 0 | 0 | 0
2013-02-02 | 22 | 30196.05 | 693.6634 | 701.5625 | 7.8991 | 1498.2 | 796.6375 | -796.6375 | 7.676% | 113.6% | 1530.4 | 828.8375 | -828.8375 | 7.986% | 118.1% | 22 | 0 | 0 | 0 | 0
2013-02-02 | 23 | 28915.9602 | 636.967 | 651.7683 | 14.8014 | 1611.4 | 959.6317 | -959.6317 | 9.246% | 147.2% | 1637.7 | 985.9317 | -985.9317 | 9.5% | 151.3% | 23 | 0 | 0 | 0 | 0
2013-02-02 | 24 | 27408.647 | 677.4041 | 684.0232 | 6.6192 | 1768.4 | 1084.3768 | -1084.3768 | 10.45% | 158.5% | 1790.1 | 1106.0768 | -1106.0768 | 10.66% | 161.7% | 24 | 0 | 0 | 0 | 0
2013-02-03 | 1 | 26305.8048 | 680.0233 | 684.6273 | 4.604 | 1140.9 | 456.2727 | -456.2727 | 4.396% | 66.65% | 1212.5 | 527.8727 | -527.8727 | 5.086% | 77.1% | 1 | 0 | 0 | 0 | 0
2013-02-03 | 2 | 25654.4219 | 659.7585 | 671.6533 | 11.8948 | 1210.1 | 538.4467 | -538.4467 | 5.188% | 80.17% | 1271.2 | 599.5467 | -599.5467 | 5.777% | 89.26% | 2 | 0 | 0 | 0 | 0
2013-02-03 | 3 | 25413.7978 | 596.6463 | 601.5307 | 4.8843 | 1240.7 | 639.1693 | -639.1693 | 6.159% | 106.3% | 1298.3 | 696.7693 | -696.7693 | 6.714% | 115.8% | 3 | 0 | 0 | 0 | 0
2013-02-03 | 4 | 25479.8261 | 808.467 | 811.0769 | 2.6099 | 1335.2 | 524.1231 | -524.1231 | 5.05% | 64.62% | 1384.5 | 573.4231 | -573.4231 | 5.525% | 70.7% | 4 | 0 | 0 | 0 | 0
2013-02-03 | 5 | 25860.1781 | 1067.5778 | 1068.5545 | 0.97676 | 1535.8 | 467.2455 | -467.2455 | 4.502% | 43.73% | 1583.2 | 514.6455 | -514.6455 | 4.959% | 48.16% | 5 | 0 | 0 | 0 | 0
2013-02-03 | 6 | 26777.7699 | 1310.0743 | 1316.4932 | 6.4189 | 1705.5 | 389.0068 | -389.0068 | 3.748% | 29.55% | 1762.7 | 446.2068 | -446.2068 | 4.299% | 33.89% | 6 | 0 | 0 | 0 | 0
2013-02-03 | 7 | 28163.6435 | 1646.2459 | 1648.5286 | 2.2827 | 1934 | 285.4714 | -285.4714 | 2.751% | 17.32% | 2002.4 | 353.8714 | -353.8714 | 3.41% | 21.47% | 7 | 0 | 0 | 0 | 0
2013-02-03 | 8 | 29405.3214 | 2003.5307 | 2005.316 | 1.7853 | 2229.1 | 223.784 | -223.784 | 2.156% | 11.16% | 2268.1 | 262.784 | -262.784 | 2.532% | 13.1% | 8 | 0 | 0 | 0 | 0
2013-02-03 | 9 | 30479.5242 | 2300.0943 | 2302.4091 | 2.3148 | 2308.6 | 6.1909 | -6.1909 | 0.05965% | 0.2689% | 2359.9 | 57.4909 | -57.4909 | 0.5539% | 2.497% | 9 | 0 | 0 | 0 | 0
2013-02-03 | 10 | 30581.6688 | 2156.117 | 2162.6435 | 6.5265 | 2145.1 | 17.5435 | 17.5435 | 0.169% | 0.8112% | 2191.7 | 29.0565 | -29.0565 | 0.28% | 1.344% | 10 | 1 | 0 | 0 | 1
2013-02-03 | 11 | 30015.6169 | 3107.1968 | 3113.3459 | 6.1491 | 1989.4 | 1123.9459 | 1123.9459 | 10.83% | 36.1% | 2015.4 | 1097.9459 | 1097.9459 | 10.58% | 35.27% | 11 | 1 | 0 | 1 | 1
2013-02-03 | 12 | 29536.7907 | 4616.2409 | 4617.2281 | 0.9872 | 2144.1 | 2473.1281 | 2473.1281 | 23.83% | 53.56% | 2165.5 | 2451.7281 | 2451.7281 | 23.62% | 53.1% | 12 | 1 | 0 | 1 | 1
2013-02-03 | 13 | 29325.8769 | 5362.4148 | 5354.1343 | -8.2805 | 2235.6 | 3118.5343 | 3118.5343 | 30.05% | 58.25% | 2245.1 | 3109.0343 | 3109.0343 | 29.96% | 58.07% | 13 | 1 | 0 | 1 | 1
2013-02-03 | 14 | 29083.2635 | 5162.1937 | 5139.3084 | -22.8853 | 2339.4 | 2799.9084 | 2799.9084 | 26.98% | 54.48% | 2354.6 | 2784.7084 | 2784.7084 | 26.83% | 54.18% | 14 | 1 | 0 | 1 | 1
2013-02-03 | 15 | 29140.2239 | 5281.8599 | 5263.7545 | -18.1054 | 2574.8 | 2688.9545 | 2688.9545 | 25.91% | 51.08% | 2602.6 | 2661.1545 | 2661.1545 | 25.64% | 50.56% | 15 | 1 | 0 | 1 | 1
2013-02-03 | 16 | 29237.0841 | 5796.9883 | 5794.7537 | -2.2345 | 2917.2 | 2877.5537 | 2877.5537 | 27.73% | 49.66% | 2950 | 2844.7537 | 2844.7537 | 27.41% | 49.09% | 16 | 1 | 0 | 1 | 1
2013-02-03 | 17 | 29330.7828 | 5789.0055 | 5814.9711 | 25.9656 | 3051.7 | 2763.2711 | 2763.2711 | 26.62% | 47.52% | 3093.5 | 2721.4711 | 2721.4711 | 26.22% | 46.8% | 17 | 1 | 0 | 1 | 1
2013-02-03 | 18 | 29421.7777 | 4854.2721 | 4860.8497 | 6.5776 | 2894.6 | 1966.2497 | 1966.2497 | 18.95% | 40.45% | 2950.4 | 1910.4497 | 1910.4497 | 18.41% | 39.3% | 18 | 1 | 0 | 1 | 1
2013-02-03 | 19 | 30801.081 | 4644.675 | 4650.7126 | 6.0376 | 3317.7 | 1333.0126 | 1333.0126 | 12.84% | 28.66% | 3366.7 | 1284.0126 | 1284.0126 | 12.37% | 27.61% | 19 | 1 | 0 | 1 | 1
2013-02-03 | 20 | 31124.222 | 5800.7068 | 5798.0338 | -2.673 | 4051 | 1747.0338 | 1747.0338 | 16.83% | 30.13% | 4120.6 | 1677.4338 | 1677.4338 | 16.16% | 28.93% | 20 | 1 | 0 | 1 | 1
2013-02-03 | 21 | 30906.9563 | 6910.91 | 6913.7396 | 2.8296 | 5068.8 | 1844.9396 | 1844.9396 | 17.78% | 26.69% | 5152.2 | 1761.5396 | 1761.5396 | 16.97% | 25.48% | 21 | 1 | 0 | 1 | 1
2013-02-03 | 22 | 29938.1846 | 7344.414 | 7346.0854 | 1.6715 | 5675 | 1671.0854 | 1671.0854 | 16.1% | 22.75% | 5755.9 | 1590.1854 | 1590.1854 | 15.32% | 21.65% | 22 | 1 | 0 | 1 | 1
2013-02-03 | 23 | 29057.3629 | 7131.7504 | 7138.5474 | 6.797 | 5943.7 | 1194.8474 | 1194.8474 | 11.51% | 16.74% | 6043.4 | 1095.1474 | 1095.1474 | 10.55% | 15.34% | 23 | 1 | 0 | 1 | 1
2013-02-03 | 24 | 26615.0456 | 6572.2799 | 6574.9948 | 2.7149 | 6086.3 | 488.6948 | 488.6948 | 4.709% | 7.433% | 6174.7 | 400.2948 | 400.2948 | 3.857% | 6.088% | 24 | 1 | 0 | 1 | 1
2013-02-04 | 1 | 24890.9166 | 5908.5078 | 5910.9356 | 2.4277 | 6759.1 | 848.1644 | -848.1644 | 8.172% | 14.35% | 6795.4 | 884.4644 | -884.4644 | 8.522% | 14.96% | 1 | 0 | 0 | 0 | 0
2013-02-04 | 2 | 23937.541 | 5354.5929 | 5357.8685 | 3.2755 | 6392.8 | 1034.9315 | -1034.9315 | 9.972% | 19.32% | 6404.7 | 1046.8315 | -1046.8315 | 10.09% | 19.54% | 2 | 0 | 0 | 0 | 0
2013-02-04 | 3 | 23611.8924 | 5035.0563 | 5041.0477 | 5.9914 | 6380 | 1338.9523 | -1338.9523 | 12.9% | 26.56% | 6387.4 | 1346.3523 | -1346.3523 | 12.97% | 26.71% | 3 | 0 | 0 | 0 | 0
2013-02-04 | 4 | 23668.521 | 4592.5687 | 4601.1593 | 8.5906 | 6512.2 | 1911.0407 | -1911.0407 | 18.41% | 41.53% | 6529.1 | 1927.9407 | -1927.9407 | 18.58% | 41.9% | 4 | 0 | 0 | 0 | 0
2013-02-04 | 5 | 24382.2297 | 4180.3616 | 4194.3853 | 14.0238 | 5836.4 | 1642.0147 | -1642.0147 | 15.82% | 39.15% | 5864.9 | 1670.5147 | -1670.5147 | 16.1% | 39.83% | 5 | 0 | 0 | 0 | 0
2013-02-04 | 6 | 26667.8482 | 4287.4076 | 4302.0949 | 14.6873 | 5564.7 | 1262.6051 | -1262.6051 | 12.17% | 29.35% | 5588.9 | 1286.8051 | -1286.8051 | 12.4% | 29.91% | 6 | 0 | 0 | 0 | 0
2013-02-04 | 7 | 30636.634 | 4012.1782 | 4010.3017 | -1.8765 | 5290.4 | 1280.0983 | -1280.0983 | 12.33% | 31.92% | 5303.1 | 1292.7983 | -1292.7983 | 12.46% | 32.24% | 7 | 0 | 0 | 0 | 0
2013-02-04 | 8 | 32207.8746 | 3839.748 | 3843.5795 | 3.8316 | 4880.3 | 1036.7205 | -1036.7205 | 9.989% | 26.97% | 4846.8 | 1003.2205 | -1003.2205 | 9.666% | 26.1% | 8 | 0 | 0 | 0 | 0
2013-02-04 | 9 | 31741.641 | 3311.7498 | 3318.4081 | 6.6583 | 4149.4 | 830.9919 | -830.9919 | 8.007% | 25.04% | 4190.3 | 871.8919 | -871.8919 | 8.401% | 26.27% | 9 | 0 | 0 | 0 | 0
2013-02-04 | 10 | 32060.5536 | 2790.7125 | 2797.035 | 6.3225 | 3359.1 | 562.065 | -562.065 | 5.416% | 20.1% | 3483.3 | 686.265 | -686.265 | 6.612% | 24.54% | 10 | 0 | 0 | 0 | 0
2013-02-04 | 11 | 32202.06 | 2782.5156 | 2834.0324 | 51.5168 | 2755.4 | 78.6324 | 78.6324 | 0.7576% | 2.775% | 2907.4 | 73.3676 | -73.3676 | 0.7069% | 2.589% | 11 | 1 | 0 | 0 | 1
2013-02-04 | 12 | 32255.2395 | 1956.0868 | 2031.4368 | 75.3499 | 2535.7 | 504.2632 | -504.2632 | 4.859% | 24.82% | 2698.8 | 667.3632 | -667.3632 | 6.43% | 32.85% | 12 | 0 | 0 | 0 | 0
2013-02-04 | 13 | 32231.2884 | 1689.8074 | 1749.8047 | 59.9973 | 2543.9 | 794.0953 | -794.0953 | 7.651% | 45.38% | 2704.9 | 955.0953 | -955.0953 | 9.203% | 54.58% | 13 | 0 | 0 | 0 | 0
2013-02-04 | 14 | 32268.1277 | 2084.1914 | 2097.2131 | 13.0217 | 2591.2 | 493.9869 | -493.9869 | 4.76% | 23.55% | 2753.6 | 656.3869 | -656.3869 | 6.324% | 31.3% | 14 | 0 | 0 | 0 | 0
2013-02-04 | 15 | 32255.3367 | 2424.6632 | 2450.5385 | 25.8753 | 2985.5 | 534.9615 | -534.9615 | 5.155% | 21.83% | 3090.2 | 639.6615 | -639.6615 | 6.163% | 26.1% | 15 | 0 | 0 | 0 | 0
2013-02-04 | 16 | 32277.3375 | 2613.4128 | 2621.623 | 8.2102 | 2930 | 308.377 | -308.377 | 2.971% | 11.76% | 3004.5 | 382.877 | -382.877 | 3.689% | 14.6% | 16 | 0 | 0 | 0 | 0
2013-02-04 | 17 | 32390.3207 | 2421.7103 | 2414.89 | -6.8203 | 2834 | 419.11 | -419.11 | 4.038% | 17.36% | 2894.7 | 479.81 | -479.81 | 4.623% | 19.87% | 17 | 0 | 0 | 0 | 0
2013-02-04 | 18 | 32621.8877 | 2216.5702 | 2216.8676 | 0.29735 | 2670.1 | 453.2324 | -453.2324 | 4.367% | 20.44% | 2737.9 | 521.0324 | -521.0324 | 5.02% | 23.5% | 18 | 0 | 0 | 0 | 0
2013-02-04 | 19 | 34330.5697 | 1942.7284 | 1947.8911 | 5.1627 | 2628 | 680.1089 | -680.1089 | 6.553% | 34.92% | 2725.9 | 778.0089 | -778.0089 | 7.496% | 39.94% | 19 | 0 | 0 | 0 | 0
2013-02-04 | 20 | 34664.6416 | 1942.1996 | 1958.785 | 16.5853 | 2764.9 | 806.115 | -806.115 | 7.767% | 41.15% | 2855.9 | 897.115 | -897.115 | 8.644% | 45.8% | 20 | 0 | 0 | 0 | 0
2013-02-04 | 21 | 33758.0269 | 1858.6212 | 1875.6864 | 17.0652 | 3008.2 | 1132.5136 | -1132.5136 | 10.91% | 60.38% | 3087.5 | 1211.8136 | -1211.8136 | 11.68% | 64.61% | 21 | 0 | 0 | 0 | 0
2013-02-04 | 22 | 32192.5779 | 1692.4282 | 1703.7297 | 11.3015 | 3122.8 | 1419.0703 | -1419.0703 | 13.67% | 83.29% | 3213.6 | 1509.8703 | -1509.8703 | 14.55% | 88.62% | 22 | 0 | 0 | 0 | 0
2013-02-04 | 23 | 29499.635 | 1798.4626 | 1804.795 | 6.3324 | 3074.2 | 1269.405 | -1269.405 | 12.23% | 70.34% | 3186.7 | 1381.905 | -1381.905 | 13.32% | 76.57% | 23 | 0 | 0 | 0 | 0
2013-02-04 | 24 | 26971.0347 | 1948.6111 | 1946.8059 | -1.8052 | 2956.7 | 1009.8941 | -1009.8941 | 9.731% | 51.87% | 3064.7 | 1117.8941 | -1117.8941 | 10.77% | 57.42% | 24 | 0 | 0 | 0 | 0
2013-02-05 | 1 | 25242.3479 | 1789.8665 | 1787.1869 | -2.6796 | 1756.2 | 30.9869 | 30.9869 | 0.2986% | 1.734% | 1943.1 | 155.9131 | -155.9131 | 1.502% | 8.724% | 1 | 1 | 0 | 0 | 1
2013-02-05 | 2 | 24361.1331 | 1274.8193 | 1278.3024 | 3.4831 | 1461.2 | 182.8976 | -182.8976 | 1.762% | 14.31% | 1620.3 | 341.9976 | -341.9976 | 3.295% | 26.75% | 2 | 0 | 0 | 0 | 0
2013-02-05 | 3 | 23958.4144 | 840.7356 | 844.0309 | 3.2954 | 1181.7 | 337.6691 | -337.6691 | 3.254% | 40.01% | 1337.7 | 493.6691 | -493.6691 | 4.757% | 58.49% | 3 | 0 | 0 | 0 | 0
2013-02-05 | 4 | 23934.8524 | 546.9935 | 549.1649 | 2.1714 | 942.1 | 392.9351 | -392.9351 | 3.786% | 71.55% | 1078.3 | 529.1351 | -529.1351 | 5.098% | 96.35% | 4 | 0 | 0 | 0 | 0
2013-02-05 | 5 | 24570.2447 | 390.4942 | 393.6511 | 3.1569 | 839.9 | 446.2489 | -446.2489 | 4.3% | 113.4% | 944 | 550.3489 | -550.3489 | 5.303% | 139.8% | 5 | 0 | 0 | 0 | 0
2013-02-05 | 6 | 26826.795 | 356.8095 | 365.7525 | 8.943 | 816.9 | 451.1475 | -451.1475 | 4.347% | 123.3% | 894.3 | 528.5475 | -528.5475 | 5.093% | 144.5% | 6 | 0 | 0 | 0 | 0
2013-02-05 | 7 | 30875.4234 | 467.8347 | 480.4111 | 12.5763 | 836.9 | 356.4889 | -356.4889 | 3.435% | 74.2% | 889.5 | 409.0889 | -409.0889 | 3.942% | 85.15% | 7 | 0 | 0 | 0 | 0
2013-02-05 | 8 | 32312.7929 | 538.6193 | 555.4865 | 16.8673 | 911.9 | 356.4135 | -356.4135 | 3.434% | 64.16% | 959.2 | 403.7135 | -403.7135 | 3.89% | 72.68% | 8 | 0 | 0 | 0 | 0
2013-02-05 | 9 | 31905.7771 | 468.7664 | 483.2921 | 14.5256 | 1053.1 | 569.8079 | -569.8079 | 5.49% | 117.9% | 1083.8 | 600.5079 | -600.5079 | 5.786% | 124.3% | 9 | 0 | 0 | 0 | 0
2013-02-05 | 10 | 32079.6836 | 481.8668 | 496.9967 | 15.1299 | 1044.5 | 547.5033 | -547.5033 | 5.275% | 110.2% | 1062 | 565.0033 | -565.0033 | 5.444% | 113.7% | 10 | 0 | 0 | 0 | 0
2013-02-05 | 11 | 32546.3122 | 315.0159 | 326.932 | 11.916 | 813.7 | 486.768 | -486.768 | 4.69% | 148.9% | 835.7 | 508.768 | -508.768 | 4.902% | 155.6% | 11 | 0 | 0 | 0 | 0
2013-02-05 | 12 | 32851.1331 | 212.7565 | 216.1149 | 3.3584 | 746.2 | 530.0851 | -530.0851 | 5.108% | 245.3% | 769.5 | 553.3851 | -553.3851 | 5.332% | 256.1% | 12 | 0 | 0 | 0 | 0
2013-02-05 | 13 | 33166.4823 | 155.6117 | 162.9123 | 7.3006 | 694.6 | 531.6877 | -531.6877 | 5.123% | 326.4% | 717.9 | 554.9877 | -554.9877 | 5.347% | 340.7% | 13 | 0 | 0 | 0 | 0
2013-02-05 | 14 | 33562.6492 | 135.1685 | 143.8527 | 8.6842 | 662.1 | 518.2473 | -518.2473 | 4.993% | 360.3% | 686.7 | 542.8473 | -542.8473 | 5.23% | 377.4% | 14 | 0 | 0 | 0 | 0
2013-02-05 | 15 | 33750.5329 | 276.9715 | 269.9006 | -7.0709 | 662.7 | 392.7994 | -392.7994 | 3.785% | 145.5% | 682.1 | 412.1994 | -412.1994 | 3.972% | 152.7% | 15 | 0 | 0 | 0 | 0
2013-02-05 | 16 | 33949.7471 | 528.7421 | 531.4117 | 2.6695 | 654.2 | 122.7883 | -122.7883 | 1.183% | 23.11% | 680.6 | 149.1883 | -149.1883 | 1.437% | 28.07% | 16 | 0 | 0 | 0 | 0
2013-02-05 | 17 | 34025.0913 | 770.9189 | 782.0844 | 11.1655 | 642.3 | 139.7844 | 139.7844 | 1.347% | 17.87% | 667.9 | 114.1844 | 114.1844 | 1.1% | 14.6% | 17 | 1 | 0 | 1 | 1
2013-02-05 | 18 | 33963.1682 | 788.2129 | 799.2726 | 11.0597 | 657 | 142.2726 | 142.2726 | 1.371% | 17.8% | 684.4 | 114.8726 | 114.8726 | 1.107% | 14.37% | 18 | 1 | 0 | 1 | 1
2013-02-05 | 19 | 35337.276 | 1154.2942 | 1157.4004 | 3.1062 | 930.2 | 227.2004 | 227.2004 | 2.189% | 19.63% | 962.8 | 194.6004 | 194.6004 | 1.875% | 16.81% | 19 | 1 | 0 | 1 | 1
2013-02-05 | 20 | 35542.6911 | 2152.116 | 2164.4325 | 12.3166 | 1423.3 | 741.1325 | 741.1325 | 7.141% | 34.24% | 1454.7 | 709.7325 | 709.7325 | 6.838% | 32.79% | 20 | 1 | 0 | 1 | 1
2013-02-05 | 21 | 34737.8211 | 3171.564 | 3206.8321 | 35.2681 | 1944.4 | 1262.4321 | 1262.4321 | 12.16% | 39.37% | 1982.6 | 1224.2321 | 1224.2321 | 11.8% | 38.18% | 21 | 1 | 0 | 1 | 1
2013-02-05 | 22 | 33078.8062 | 3944.2496 | 3992.0898 | 47.8402 | 2395.4 | 1596.6898 | 1596.6898 | 15.38% | 40% | 2420.1 | 1571.9898 | 1571.9898 | 15.15% | 39.38% | 22 | 1 | 0 | 1 | 1
2013-02-05 | 23 | 30498.1686 | 4116.3935 | 4124.8779 | 8.4844 | 2912.1 | 1212.7779 | 1212.7779 | 11.69% | 29.4% | 2945.8 | 1179.0779 | 1179.0779 | 11.36% | 28.58% | 23 | 1 | 0 | 1 | 1
2013-02-05 | 24 | 27775.5302 | 4144.9534 | 4147.1953 | 2.2419 | 3451.3 | 695.8953 | 695.8953 | 6.705% | 16.78% | 3498 | 649.1953 | 649.1953 | 6.255% | 15.65% | 24 | 1 | 0 | 1 | 1
2013-02-06 | 1 | 25925.042 | 3623.6332 | 3627.5148 | 3.8816 | 3235 | 392.5148 | 392.5148 | 3.782% | 10.82% | 3203.3 | 424.2148 | 424.2148 | 4.087% | 11.69% | 1 | 1 | 0 | 1 | 1
2013-02-06 | 2 | 24927.7028 | 3743.8942 | 3746.3413 | 2.4472 | 3307.7 | 438.6413 | 438.6413 | 4.226% | 11.71% | 3301 | 445.3413 | 445.3413 | 4.291% | 11.89% | 2 | 1 | 0 | 1 | 1
2013-02-06 | 3 | 24419.9018 | 3671.444 | 3673.9111 | 2.467 | 3178.6 | 495.3111 | 495.3111 | 4.772% | 13.48% | 3162.8 | 511.1111 | 511.1111 | 4.925% | 13.91% | 3 | 1 | 0 | 1 | 1
2013-02-06 | 4 | 24304.2386 | 3836.9741 | 3837.4178 | 0.44379 | 2697.9 | 1139.5178 | 1139.5178 | 10.98% | 29.69% | 2745.4 | 1092.0178 | 1092.0178 | 10.52% | 28.46% | 4 | 1 | 0 | 1 | 1
2013-02-06 | 5 | 24860.8766 | 4047.776 | 4052.1918 | 4.4158 | 2548.6 | 1503.5918 | 1503.5918 | 14.49% | 37.11% | 2596.9 | 1455.2918 | 1455.2918 | 14.02% | 35.91% | 5 | 1 | 0 | 1 | 1
2013-02-06 | 6 | 26954.9423 | 3773.459 | 3785.396 | 11.937 | 2722.2 | 1063.196 | 1063.196 | 10.24% | 28.09% | 2723.8 | 1061.596 | 1061.596 | 10.23% | 28.04% | 6 | 1 | 0 | 1 | 1
2013-02-06 | 7 | 30913.6438 | 3436.406 | 3448.4954 | 12.0894 | 2710.6 | 737.8954 | 737.8954 | 7.11% | 21.4% | 2705.5 | 742.9954 | 742.9954 | 7.159% | 21.55% | 7 | 1 | 0 | 1 | 1
2013-02-06 | 8 | 32448.8541 | 3097.205 | 3092.6042 | -4.6009 | 3179.7 | 87.0958 | -87.0958 | 0.8392% | 2.816% | 3099.2 | 6.5958 | -6.5958 | 0.06355% | 0.2133% | 8 | 0 | 0 | 0 | 0
2013-02-06 | 9 | 32079.9853 | 2677.4008 | 2676.4785 | -0.92223 | 3066.3 | 389.8215 | -389.8215 | 3.756% | 14.56% | 2998.1 | 321.6215 | -321.6215 | 3.099% | 12.02% | 9 | 0 | 0 | 0 | 0
2013-02-06 | 10 | 32381.66 | 2396.0519 | 2400.7922 | 4.7403 | 2967 | 566.2078 | -566.2078 | 5.456% | 23.58% | 2899.8 | 499.0078 | -499.0078 | 4.808% | 20.79% | 10 | 0 | 0 | 0 | 0
2013-02-06 | 11 | 32746.0646 | 3053.8407 | 3060.6141 | 6.7733 | 2739.2 | 321.4141 | 321.4141 | 3.097% | 10.5% | 2687.1 | 373.5141 | 373.5141 | 3.599% | 12.2% | 11 | 1 | 0 | 1 | 1
2013-02-06 | 12 | 32879.0259 | 2823.2963 | 2843.5418 | 20.2455 | 2764.5 | 79.0418 | 79.0418 | 0.7616% | 2.78% | 2725.5 | 118.0418 | 118.0418 | 1.137% | 4.151% | 12 | 1 | 0 | 1 | 1
2013-02-06 | 13 | 32907.044 | 2288.921 | 2299.3689 | 10.4479 | 2621.6 | 322.2311 | -322.2311 | 3.105% | 14.01% | 2633.6 | 334.2311 | -334.2311 | 3.22% | 14.54% | 13 | 0 | 0 | 0 | 0
2013-02-06 | 14 | 33075.5516 | 2041.1339 | 2053.2321 | 12.0981 | 2464.8 | 411.5679 | -411.5679 | 3.966% | 20.04% | 2501.3 | 448.0679 | -448.0679 | 4.317% | 21.82% | 14 | 0 | 0 | 0 | 0
2013-02-06 | 15 | 32979.2423 | 2631.6168 | 2644.109 | 12.4922 | 2368.1 | 276.009 | 276.009 | 2.659% | 10.44% | 2410.2 | 233.909 | 233.909 | 2.254% | 8.846% | 15 | 1 | 0 | 1 | 1
2013-02-06 | 16 | 32930.4021 | 3316.2815 | 3311.2319 | -5.0496 | 2340.7 | 970.5319 | 970.5319 | 9.351% | 29.31% | 2358.7 | 952.5319 | 952.5319 | 9.178% | 28.77% | 16 | 1 | 0 | 1 | 1
2013-02-06 | 17 | 32819.386 | 3321.451 | 3326.706 | 5.255 | 2314.8 | 1011.906 | 1011.906 | 9.75% | 30.42% | 2329.9 | 996.806 | 996.806 | 9.605% | 29.96% | 17 | 1 | 0 | 1 | 1
2013-02-06 | 18 | 32955.4063 | 2779.9706 | 2786.6249 | 6.6544 | 2093.4 | 693.2249 | 693.2249 | 6.679% | 24.88% | 2111.5 | 675.1249 | 675.1249 | 6.505% | 24.23% | 18 | 1 | 0 | 1 | 1
2013-02-06 | 19 | 34467.0357 | 2119.8275 | 2132.1187 | 12.2912 | 2257.8 | 125.6813 | -125.6813 | 1.211% | 5.895% | 2283.9 | 151.7813 | -151.7813 | 1.462% | 7.119% | 19 | 0 | 0 | 0 | 0
2013-02-06 | 20 | 34642.0874 | 2063.6154 | 2066.5492 | 2.9337 | 2655.7 | 589.1508 | -589.1508 | 5.677% | 28.51% | 2686.5 | 619.9508 | -619.9508 | 5.973% | 30% | 20 | 0 | 0 | 0 | 0
2013-02-06 | 21 | 33795.0075 | 2370.3551 | 2394.1367 | 23.7817 | 3016.4 | 622.2633 | -622.2633 | 5.996% | 25.99% | 3043.2 | 649.0633 | -649.0633 | 6.254% | 27.11% | 21 | 0 | 0 | 0 | 0
2013-02-06 | 22 | 32355.1999 | 2750.0626 | 2831.6407 | 81.5781 | 3238.4 | 406.7593 | -406.7593 | 3.919% | 14.36% | 3279.3 | 447.6593 | -447.6593 | 4.313% | 15.81% | 22 | 0 | 0 | 0 | 0
2013-02-06 | 23 | 29752.8892 | 3479.9252 | 3553.6746 | 73.7494 | 3385.7 | 167.9746 | 167.9746 | 1.618% | 4.727% | 3423.4 | 130.2746 | 130.2746 | 1.255% | 3.666% | 23 | 1 | 0 | 1 | 1
2013-02-06 | 24 | 27142.2329 | 4368.8941 | 4451.7952 | 82.9012 | 3673.5 | 778.2952 | 778.2952 | 7.499% | 17.48% | 3688.5 | 763.2952 | 763.2952 | 7.355% | 17.15% | 24 | 1 | 0 | 1 | 1
2013-02-07 | 1 | 25347.8937 | 4870.5205 | 5062.8643 | 192.3438 | 4691.2 | 371.6643 | 371.6643 | 3.581% | 7.341% | 4771.2 | 291.6643 | 291.6643 | 2.81% | 5.761% | 1 | 1 | 0 | 1 | 1
2013-02-07 | 2 | 24457.3209 | 4893.5587 | 5021.3118 | 127.7531 | 5025.7 | 4.3882 | -4.3882 | 0.04228% | 0.08739% | 4993.7 | 27.6118 | 27.6118 | 0.266% | 0.5499% | 2 | 0 | 0 | 1 | 0
2013-02-07 | 3 | 23984.2033 | 4810.5782 | 4868.0297 | 57.4514 | 5269.2 | 401.1703 | -401.1703 | 3.865% | 8.241% | 5225.8 | 357.7703 | -357.7703 | 3.447% | 7.349% | 3 | 0 | 0 | 0 | 0
2013-02-07 | 4 | 23917.7483 | 4777.0694 | 4859.0503 | 81.9809 | 5197.5 | 338.4497 | -338.4497 | 3.261% | 6.965% | 5237.3 | 378.2497 | -378.2497 | 3.645% | 7.784% | 4 | 0 | 0 | 0 | 0
2013-02-07 | 5 | 24452.3871 | 4608.8987 | 4698.2457 | 89.3471 | 5173.2 | 474.9543 | -474.9543 | 4.576% | 10.11% | 5231.4 | 533.1543 | -533.1543 | 5.137% | 11.35% | 5 | 0 | 0 | 0 | 0
2013-02-07 | 6 | 26437.4943 | 4359.0832 | 4447.6651 | 88.5819 | 5170.6 | 722.9349 | -722.9349 | 6.966% | 16.25% | 5202.4 | 754.7349 | -754.7349 | 7.272% | 16.97% | 6 | 0 | 0 | 0 | 0
2013-02-07 | 7 | 30348.1355 | 4305.5332 | 4383.7069 | 78.1737 | 4974.6 | 590.8931 | -590.8931 | 5.693% | 13.48% | 4975.4 | 591.6931 | -591.6931 | 5.701% | 13.5% | 7 | 0 | 0 | 0 | 0
2013-02-07 | 8 | 31703.7274 | 4209.2005 | 4298.8149 | 89.6144 | 4668.4 | 369.5851 | -369.5851 | 3.561% | 8.597% | 4635.9 | 337.0851 | -337.0851 | 3.248% | 7.841% | 8 | 0 | 0 | 0 | 0
2013-02-07 | 9 | 31438.4421 | 3672.2759 | 3761.0341 | 88.7582 | 3781.9 | 20.8659 | -20.8659 | 0.201% | 0.5548% | 3819.1 | 58.0659 | -58.0659 | 0.5595% | 1.544% | 9 | 0 | 0 | 0 | 0
2013-02-07 | 10 | 31789.2742 | 3586.8986 | 3668.6201 | 81.7215 | 2901.7 | 766.9201 | 766.9201 | 7.39% | 20.9% | 2963 | 705.6201 | 705.6201 | 6.799% | 19.23% | 10 | 1 | 0 | 1 | 1
2013-02-07 | 11 | 32372.5942 | 3949.3464 | 4049.6241 | 100.2777 | 2561.1 | 1488.5241 | 1488.5241 | 14.34% | 36.76% | 2621.5 | 1428.1241 | 1428.1241 | 13.76% | 35.27% | 11 | 1 | 0 | 1 | 1
2013-02-07 | 12 | 32591.5782 | 3309.3661 | 3413.9416 | 104.5755 | 2576.8 | 837.1416 | 837.1416 | 8.066% | 24.52% | 2568.4 | 845.5416 | 845.5416 | 8.147% | 24.77% | 12 | 1 | 0 | 1 | 1
2013-02-07 | 13 | 32822.9764 | 3784.9037 | 3888.8584 | 103.9547 | 2709.3 | 1179.5584 | 1179.5584 | 11.37% | 30.33% | 2693.9 | 1194.9584 | 1194.9584 | 11.51% | 30.73% | 13 | 1 | 0 | 1 | 1
2013-02-07 | 14 | 33307.7706 | 4207.1987 | 4296.7575 | 89.5588 | 2792.4 | 1504.3575 | 1504.3575 | 14.49% | 35.01% | 2800.5 | 1496.2575 | 1496.2575 | 14.42% | 34.82% | 14 | 1 | 0 | 1 | 1
2013-02-07 | 15 | 33402.322 | 3974.435 | 4056.0885 | 81.6534 | 2905 | 1151.0885 | 1151.0885 | 11.09% | 28.38% | 2892.1 | 1163.9885 | 1163.9885 | 11.22% | 28.7% | 15 | 1 | 0 | 1 | 1
2013-02-07 | 16 | 33431.5088 | 4149.6482 | 4231.363 | 81.7149 | 2895.2 | 1336.163 | 1336.163 | 12.87% | 31.58% | 2894.7 | 1336.663 | 1336.663 | 12.88% | 31.59% | 16 | 1 | 0 | 1 | 1
2013-02-07 | 17 | 33414.5693 | 4207.1025 | 4271.7606 | 64.6581 | 2816.7 | 1455.0606 | 1455.0606 | 14.02% | 34.06% | 2859.3 | 1412.4606 | 1412.4606 | 13.61% | 33.07% | 17 | 1 | 0 | 1 | 1
2013-02-07 | 18 | 33233.515 | 3731.6461 | 3772.2384 | 40.5923 | 2600.9 | 1171.3384 | 1171.3384 | 11.29% | 31.05% | 2667.7 | 1104.5384 | 1104.5384 | 10.64% | 29.28% | 18 | 1 | 0 | 1 | 1
2013-02-07 | 19 | 34487.0449 | 2986.5092 | 2995.6444 | 9.1353 | 2568.6 | 427.0444 | 427.0444 | 4.115% | 14.26% | 2648.4 | 347.2444 | 347.2444 | 3.346% | 11.59% | 19 | 1 | 0 | 1 | 1
2013-02-07 | 20 | 34883.5663 | 3119.3448 | 3123.6187 | 4.274 | 2679.9 | 443.7187 | 443.7187 | 4.275% | 14.21% | 2739.7 | 383.9187 | 383.9187 | 3.699% | 12.29% | 20 | 1 | 0 | 1 | 1
2013-02-07 | 21 | 34175.7921 | 3453.1871 | 3453.8543 | 0.66726 | 2842.6 | 611.2543 | 611.2543 | 5.89% | 17.7% | 2935.4 | 518.4543 | 518.4543 | 4.995% | 15.01% | 21 | 1 | 0 | 1 | 1
2013-02-07 | 22 | 32625.4483 | 3357.6651 | 3357.9996 | 0.33451 | 2999.8 | 358.1996 | 358.1996 | 3.451% | 10.67% | 3067.8 | 290.1996 | 290.1996 | 2.796% | 8.642% | 22 | 1 | 0 | 1 | 1
2013-02-07 | 23 | 30024.5661 | 3370.737 | 3370.7546 | 0.017577 | 3083.9 | 286.8546 | 286.8546 | 2.764% | 8.51% | 3117.2 | 253.5546 | 253.5546 | 2.443% | 7.522% | 23 | 1 | 0 | 1 | 1
2013-02-07 | 24 | 27368.2718 | 3368.8791 | 3371.022 | 2.1429 | 3165.1 | 205.922 | 205.922 | 1.984% | 6.109% | 3161.6 | 209.422 | 209.422 | 2.018% | 6.212% | 24 | 1 | 0 | 1 | 1
2013-02-08 | 1 | 25652.9017 | 3478.7096 | 3479.1849 | 0.47532 | 3938.3 | 459.1151 | -459.1151 | 4.424% | 13.2% | 4055.2 | 576.0151 | -576.0151 | 5.55% | 16.56% | 1 | 0 | 0 | 0 | 0
2013-02-08 | 2 | 24683.7991 | 3561.7203 | 3561.8071 | 0.08677 | 3930.3 | 368.4929 | -368.4929 | 3.551% | 10.35% | 4041.9 | 480.0929 | -480.0929 | 4.626% | 13.48% | 2 | 0 | 0 | 0 | 0
2013-02-08 | 3 | 24299.721 | 3797.6023 | 3798.8661 | 1.2639 | 3977.4 | 178.5339 | -178.5339 | 1.72% | 4.7% | 4092.5 | 293.6339 | -293.6339 | 2.829% | 7.73% | 3 | 0 | 0 | 0 | 0
2013-02-08 | 4 | 24324.7217 | 3944.3567 | 3947.5387 | 3.182 | 3869.9 | 77.6387 | 77.6387 | 0.7481% | 1.967% | 3995 | 47.4613 | -47.4613 | 0.4573% | 1.202% | 4 | 1 | 0 | 0 | 1
2013-02-08 | 5 | 25032.3177 | 3969.6774 | 3969.9061 | 0.22873 | 3635.6 | 334.3061 | 334.3061 | 3.221% | 8.421% | 3748.6 | 221.3061 | 221.3061 | 2.132% | 5.575% | 5 | 1 | 0 | 1 | 1
2013-02-08 | 6 | 27370.2614 | 3792.7036 | 3799.5622 | 6.8587 | 3380.4 | 419.1622 | 419.1622 | 4.039% | 11.03% | 3540.3 | 259.2622 | 259.2622 | 2.498% | 6.823% | 6 | 1 | 0 | 1 | 1
2013-02-08 | 7 | 31760.9368 | 3734.3304 | 3743.4438 | 9.1134 | 3044.6 | 698.8438 | 698.8438 | 6.734% | 18.67% | 3221.2 | 522.2438 | 522.2438 | 5.032% | 13.95% | 7 | 1 | 0 | 1 | 1
2013-02-08 | 8 | 33241.7953 | 3385.5765 | 3375.0727 | -10.5038 | 2564.3 | 810.7727 | 810.7727 | 7.812% | 24.02% | 2737.3 | 637.7727 | 637.7727 | 6.145% | 18.9% | 8 | 1 | 0 | 1 | 1
2013-02-08 | 9 | 32861.3686 | 2484.923 | 2464.2731 | -20.6499 | 2037.4 | 426.8731 | 426.8731 | 4.113% | 17.32% | 2202.1 | 262.1731 | 262.1731 | 2.526% | 10.64% | 9 | 1 | 0 | 1 | 1
2013-02-08 | 10 | 32809.2171 | 1705.7463 | 1702.735 | -3.0113 | 1675.2 | 27.535 | 27.535 | 0.2653% | 1.617% | 1816.7 | 113.965 | -113.965 | 1.098% | 6.693% | 10 | 1 | 0 | 0 | 1
2013-02-08 | 11 | 32650.4938 | 1606.9479 | 1599.1577 | -7.7902 | 1570.2 | 28.9577 | 28.9577 | 0.279% | 1.811% | 1670.1 | 70.9423 | -70.9423 | 0.6836% | 4.436% | 11 | 1 | 0 | 0 | 1
2013-02-08 | 12 | 32294.5245 | 1460.7497 | 1453.9253 | -6.8244 | 1509.2 | 55.2747 | -55.2747 | 0.5326% | 3.802% | 1574.6 | 120.6747 | -120.6747 | 1.163% | 8.3% | 12 | 0 | 0 | 0 | 0
2013-02-08 | 13 | 31818.1137 | 1270.2105 | 1268.9152 | -1.2952 | 1471.1 | 202.1848 | -202.1848 | 1.948% | 15.93% | 1529.8 | 260.8848 | -260.8848 | 2.514% | 20.56% | 13 | 0 | 0 | 0 | 0
2013-02-08 | 14 | 31803.0493 | 1179.2044 | 1193.0865 | 13.8821 | 1544 | 350.9135 | -350.9135 | 3.381% | 29.41% | 1584.6 | 391.5135 | -391.5135 | 3.772% | 32.82% | 14 | 0 | 0 | 0 | 0
2013-02-08 | 15 | 31645.9608 | 1296.2292 | 1311.0909 | 14.8617 | 1748.3 | 437.2091 | -437.2091 | 4.213% | 33.35% | 1781.6 | 470.5091 | -470.5091 | 4.533% | 35.89% | 15 | 0 | 0 | 0 | 0
2013-02-08 | 16 | 31433.4554 | 1610.1605 | 1609.3756 | -0.78484 | 1995.4 | 386.0244 | -386.0244 | 3.719% | 23.99% | 2025 | 415.6244 | -415.6244 | 4.005% | 25.83% | 16 | 0 | 0 | 0 | 0
2013-02-08 | 17 | 31310.2462 | 2186.6664 | 2188.2553 | 1.5889 | 2312.3 | 124.0447 | -124.0447 | 1.195% | 5.669% | 2340.2 | 151.9447 | -151.9447 | 1.464% | 6.944% | 17 | 0 | 0 | 0 | 0
2013-02-08 | 18 | 31164.1501 | 2609.4316 | 2610.215 | 0.78338 | 2473.2 | 137.015 | 137.015 | 1.32% | 5.249% | 2505.6 | 104.615 | 104.615 | 1.008% | 4.008% | 18 | 1 | 0 | 1 | 1
2013-02-08 | 19 | 32539.0751 | 2565.4722 | 2568.5242 | 3.052 | 2788.2 | 219.6758 | -219.6758 | 2.117% | 8.553% | 2823 | 254.4758 | -254.4758 | 2.452% | 9.907% | 19 | 0 | 0 | 0 | 0
2013-02-08 | 20 | 32794.6821 | 3069.92 | 3076.3646 | 6.4446 | 3479 | 402.6354 | -402.6354 | 3.88% | 13.09% | 3523.8 | 447.4354 | -447.4354 | 4.311% | 14.54% | 20 | 0 | 0 | 0 | 0
2013-02-08 | 21 | 32238.5375 | 4125.6482 | 4162.4754 | 36.8272 | 4471.5 | 309.0246 | -309.0246 | 2.978% | 7.424% | 4495.3 | 332.8246 | -332.8246 | 3.207% | 7.996% | 21 | 0 | 0 | 0 | 0
2013-02-08 | 22 | 31371.2466 | 4921.1336 | 5007.392 | 86.2583 | 5056.9 | 49.508 | -49.508 | 0.477% | 0.9887% | 5095.5 | 88.108 | -88.108 | 0.8489% | 1.76% | 22 | 0 | 0 | 0 | 0
2013-02-08 | 23 | 29931.9508 | 5831.402 | 5912.9687 | 81.5667 | 5481.8 | 431.1687 | 431.1687 | 4.154% | 7.292% | 5546.4 | 366.5687 | 366.5687 | 3.532% | 6.199% | 23 | 1 | 0 | 1 | 1
2013-02-08 | 24 | 28156.3442 | 6560.2477 | 6623.7785 | 63.5308 | 5849.7 | 774.0785 | 774.0785 | 7.458% | 11.69% | 5938.9 | 684.8785 | 684.8785 | 6.599% | 10.34% | 24 | 1 | 0 | 1 | 1
2013-02-09 | 1 | 26746.2565 | 6498.6347 | 6576.8002 | 78.1655 | 5884.5 | 692.3002 | 692.3002 | 6.671% | 10.53% | 5954.1 | 622.7002 | 622.7002 | 6% | 9.468% | 1 | 1 | 0 | 1 | 1
2013-02-09 | 2 | 25916.2932 | 6734.0204 | 6825.5516 | 91.5312 | 6068.7 | 756.8516 | 756.8516 | 7.292% | 11.09% | 6168 | 657.5516 | 657.5516 | 6.336% | 9.634% | 2 | 1 | 0 | 1 | 1
2013-02-09 | 3 | 25481.2976 | 6966.4739 | 7129.0606 | 162.5867 | 6340.1 | 788.9606 | 788.9606 | 7.602% | 11.07% | 6414.9 | 714.1606 | 714.1606 | 6.881% | 10.02% | 3 | 1 | 0 | 1 | 1
2013-02-09 | 4 | 25275.6193 | 6971.464 | 7209.1939 | 237.7299 | 6504.2 | 704.9939 | 704.9939 | 6.793% | 9.779% | 6558.9 | 650.2939 | 650.2939 | 6.266% | 9.02% | 4 | 1 | 0 | 1 | 1
2013-02-09 | 5 | 25472.0603 | 7129.6311 | 7182.4698 | 52.8386 | 6607.8 | 574.6698 | 574.6698 | 5.537% | 8.001% | 6662.8 | 519.6698 | 519.6698 | 5.007% | 7.235% | 5 | 1 | 0 | 1 | 1
2013-02-09 | 6 | 26332.4562 | 7211.3343 | 7308.2703 | 96.936 | 6650.6 | 657.6703 | 657.6703 | 6.337% | 8.999% | 6718.3 | 589.9703 | 589.9703 | 5.685% | 8.073% | 6 | 1 | 0 | 1 | 1
2013-02-09 | 7 | 27852.6056 | 7313.9236 | 7408.5101 | 94.5864 | 6716.9 | 691.6101 | 691.6101 | 6.664% | 9.335% | 6841 | 567.5101 | 567.5101 | 5.468% | 7.66% | 7 | 1 | 0 | 1 | 1
2013-02-09 | 8 | 29232.4853 | 7373.215 | 7451.5629 | 78.3479 | 6886.4 | 565.1629 | 565.1629 | 5.446% | 7.584% | 7015.9 | 435.6629 | 435.6629 | 4.198% | 5.847% | 8 | 1 | 0 | 1 | 1
2013-02-09 | 9 | 30753.0811 | 7495.6746 | 7545.9575 | 50.2829 | 7252 | 293.9575 | 293.9575 | 2.832% | 3.896% | 7337.7 | 208.2575 | 208.2575 | 2.007% | 2.76% | 9 | 1 | 0 | 1 | 1
2013-02-09 | 10 | 32056.2716 | 7719.0917 | 7755.5476 | 36.4559 | 7396.7 | 358.8476 | 358.8476 | 3.458% | 4.627% | 7490.5 | 265.0476 | 265.0476 | 2.554% | 3.418% | 10 | 1 | 0 | 1 | 1
2013-02-09 | 11 | 32751.4603 | 7958.8734 | 7992.3402 | 33.4667 | 7383.1 | 609.2402 | 609.2402 | 5.87% | 7.623% | 7525 | 467.3402 | 467.3402 | 4.503% | 5.847% | 11 | 1 | 0 | 1 | 1
2013-02-09 | 12 | 32822.7783 | 8143.3364 | 8253.9319 | 110.5956 | 7359.1 | 894.8319 | 894.8319 | 8.622% | 10.84% | 7539.7 | 714.2319 | 714.2319 | 6.882% | 8.653% | 12 | 1 | 0 | 1 | 1
2013-02-09 | 13 | 32520.2619 | 8175.6932 | 8370.7173 | 195.0241 | 7351.3 | 1019.4173 | 1019.4173 | 9.822% | 12.18% | 7523.7 | 847.0173 | 847.0173 | 8.161% | 10.12% | 13 | 1 | 0 | 1 | 1
2013-02-09 | 14 | 32012.2157 | 8336.0705 | 8496.8283 | 160.7578 | 7377.2 | 1119.6283 | 1119.6283 | 10.79% | 13.18% | 7547.4 | 949.4283 | 949.4283 | 9.148% | 11.17% | 14 | 1 | 0 | 1 | 1
2013-02-09 | 15 | 31745.1077 | 8342.6684 | 8521.2482 | 178.5798 | 7444.1 | 1077.1482 | 1077.1482 | 10.38% | 12.64% | 7633.2 | 888.0482 | 888.0482 | 8.557% | 10.42% | 15 | 1 | 0 | 1 | 1
2013-02-09 | 16 | 31624.1969 | 8294.173 | 8475.1879 | 181.0148 | 7503.6 | 971.5879 | 971.5879 | 9.362% | 11.46% | 7712.5 | 762.6879 | 762.6879 | 7.349% | 8.999% | 16 | 1 | 1 | 1 | 1
2013-02-09 | 17 | 31888.0463 | 8385.0973 | 8524.2439 | 139.1465 | 7237.2 | 1287.0439 | 1287.0439 | 12.4% | 15.1% | 7479.7 | 1044.5439 | 1044.5439 | 10.06% | 12.25% | 17 | 1 | 1 | 1 | 1
2013-02-09 | 18 | 32599.5027 | 8421.9493 | 8489.4419 | 67.4926 | 6404.7 | 2084.7419 | 2084.7419 | 20.09% | 24.56% | 6714.2 | 1775.2419 | 1775.2419 | 17.1% | 20.91% | 18 | 1 | 1 | 1 | 1
2013-02-09 | 19 | 33865.5417 | 8407.6902 | 8462.8834 | 55.1932 | 6355.1 | 2107.7834 | 2107.7834 | 20.31% | 24.91% | 6706.4 | 1756.4834 | 1756.4834 | 16.92% | 20.76% | 19 | 1 | 1 | 1 | 1
2013-02-09 | 20 | 33739.6155 | 8526.8431 | 8594.4452 | 67.6021 | 6659.1 | 1935.3452 | 1935.3452 | 18.65% | 22.52% | 7032 | 1562.4452 | 1562.4452 | 15.05% | 18.18% | 20 | 1 | 1 | 1 | 1
2013-02-09 | 21 | 32953.6341 | 8241.2146 | 8299.4275 | 58.2128 | 6898.1 | 1401.3275 | 1401.3275 | 13.5% | 16.88% | 7264.3 | 1035.1275 | 1035.1275 | 9.974% | 12.47% | 21 | 1 | 1 | 1 | 1
2013-02-09 | 22 | 31836.251 | 7346.7211 | 7379.3771 | 32.656 | 6416.3 | 963.0771 | 963.0771 | 9.28% | 13.05% | 6809.8 | 569.5771 | 569.5771 | 5.488% | 7.718% | 22 | 1 | 1 | 1 | 1
2013-02-09 | 23 | 30186.2783 | 6623.5242 | 6651.7389 | 28.2148 | 6205.5 | 446.2389 | 446.2389 | 4.3% | 6.709% | 6655.6 | 3.8611 | -3.8611 | 0.0372% | 0.05805% | 23 | 1 | 1 | 0 | 1
2013-02-09 | 24 | 28311.0593 | 6600.7607 | 6644.7739 | 44.0133 | 6184.3 | 460.4739 | 460.4739 | 4.437% | 6.93% | 6571.8 | 72.9739 | 72.9739 | 0.7031% | 1.098% | 24 | 1 | 1 | 1 | 1
2013-02-10 | 1 | 26712.4644 | 6869.3889 | 6900.8414 | 31.4525 | 7283.7 | 382.8586 | -382.8586 | 3.689% | 5.548% | 7463.1 | 562.2586 | -562.2586 | 5.418% | 8.148% | 1 | 0 | 0 | 0 | 0
2013-02-10 | 2 | 25516.4264 | 6450.4008 | 6504.636 | 54.2351 | 7135.8 | 631.164 | -631.164 | 6.081% | 9.703% | 7285.3 | 780.664 | -780.664 | 7.522% | 12% | 2 | 0 | 0 | 0 | 0
2013-02-10 | 3 | 24825.1621 | 6539.8304 | 6594.126 | 54.2956 | 6970.4 | 376.274 | -376.274 | 3.626% | 5.706% | 7225.2 | 631.074 | -631.074 | 6.081% | 9.57% | 3 | 0 | 1 | 0 | 0
2013-02-10 | 4 | 24532.2155 | 6426.271 | 6483.1583 | 56.8873 | 7126.5 | 643.3417 | -643.3417 | 6.199% | 9.923% | 7381.8 | 898.6417 | -898.6417 | 8.659% | 13.86% | 4 | 0 | 1 | 0 | 0
2013-02-10 | 5 | 24485.119 | 6291.0743 | 6356.3449 | 65.2707 | 7372.8 | 1016.4551 | -1016.4551 | 9.794% | 15.99% | 7550.2 | 1193.8551 | -1193.8551 | 11.5% | 18.78% | 5 | 0 | 0 | 0 | 0
2013-02-10 | 6 | 24893.8244 | 6228.7277 | 6293.4695 | 64.7418 | 7437 | 1143.5305 | -1143.5305 | 11.02% | 18.17% | 7581.4 | 1287.9305 | -1287.9305 | 12.41% | 20.46% | 6 | 0 | 0 | 0 | 0
2013-02-10 | 7 | 25580.1285 | 6074.666 | 6125.4961 | 50.8301 | 7446.6 | 1321.1039 | -1321.1039 | 12.73% | 21.57% | 7568.4 | 1442.9039 | -1442.9039 | 13.9% | 23.56% | 7 | 0 | 0 | 0 | 0
2013-02-10 | 8 | 26482.9648 | 5702.0088 | 5752.9998 | 50.991 | 7268.7 | 1515.7002 | -1515.7002 | 14.6% | 26.35% | 7411.3 | 1658.3002 | -1658.3002 | 15.98% | 28.82% | 8 | 0 | 0 | 0 | 0
2013-02-10 | 9 | 27924.1473 | 5275.2573 | 5317.3209 | 42.0635 | 6784.1 | 1466.7791 | -1466.7791 | 14.13% | 27.58% | 6935.3 | 1617.9791 | -1617.9791 | 15.59% | 30.43% | 9 | 0 | 0 | 0 | 0
2013-02-10 | 10 | 29338.3127 | 5984.6903 | 6010.7354 | 26.0451 | 6494.6 | 483.8646 | -483.8646 | 4.662% | 8.05% | 6574.2 | 563.4646 | -563.4646 | 5.429% | 9.374% | 10 | 0 | 0 | 0 | 0
2013-02-10 | 11 | 30081.0474 | 5782.9963 | 5808.6325 | 25.6362 | 6098.6 | 289.9675 | -289.9675 | 2.794% | 4.992% | 6132.5 | 323.8675 | -323.8675 | 3.121% | 5.576% | 11 | 0 | 0 | 0 | 0
2013-02-10 | 12 | 30003.0742 | 4548.8174 | 4561.8845 | 13.0672 | 5920.8 | 1358.9155 | -1358.9155 | 13.09% | 29.79% | 5932.4 | 1370.5155 | -1370.5155 | 13.21% | 30.04% | 12 | 0 | 0 | 0 | 0
2013-02-10 | 13 | 29897.6551 | 3737.0958 | 3737.9493 | 0.8535 | 5833.7 | 2095.7507 | -2095.7507 | 20.19% | 56.07% | 5853.4 | 2115.4507 | -2115.4507 | 20.38% | 56.59% | 13 | 0 | 0 | 0 | 0
2013-02-10 | 14 | 29644.0652 | 3488.7381 | 3476.2158 | -12.5223 | 5579.9 | 2103.6842 | -2103.6842 | 20.27% | 60.52% | 5676.3 | 2200.0842 | -2200.0842 | 21.2% | 63.29% | 14 | 0 | 0 | 0 | 0
2013-02-10 | 15 | 29289.443 | 2985.4122 | 2979.0988 | -6.3134 | 5318.7 | 2339.6012 | -2339.6012 | 22.54% | 78.53% | 5364.6 | 2385.5012 | -2385.5012 | 22.99% | 80.07% | 15 | 0 | 0 | 0 | 0
2013-02-10 | 16 | 29062.7799 | 2571.5699 | 2577.9871 | 6.4172 | 4846.7 | 2268.7129 | -2268.7129 | 21.86% | 88% | 4917.1 | 2339.1129 | -2339.1129 | 22.54% | 90.73% | 16 | 0 | 0 | 0 | 0
2013-02-10 | 17 | 29112.732 | 2139.8524 | 2130.8084 | -9.044 | 4193.1 | 2062.2916 | -2062.2916 | 19.87% | 96.78% | 4269.3 | 2138.4916 | -2138.4916 | 20.61% | 100.4% | 17 | 0 | 0 | 0 | 0
2013-02-10 | 18 | 29819.7887 | 1757.9852 | 1748.7542 | -9.231 | 3263.4 | 1514.6458 | -1514.6458 | 14.59% | 86.61% | 3339.4 | 1590.6458 | -1590.6458 | 15.33% | 90.96% | 18 | 0 | 0 | 0 | 0
2013-02-10 | 19 | 31933.4953 | 1168.0728 | 1173.4026 | 5.3298 | 2936.4 | 1762.9974 | -1762.9974 | 16.99% | 150.2% | 3077.7 | 1904.2974 | -1904.2974 | 18.35% | 162.3% | 19 | 0 | 0 | 0 | 0
2013-02-10 | 20 | 32804.3336 | 935.6593 | 949.3263 | 13.6669 | 2811.3 | 1861.9737 | -1861.9737 | 17.94% | 196.1% | 3086.4 | 2137.0737 | -2137.0737 | 20.59% | 225.1% | 20 | 0 | 1 | 0 | 0
2013-02-10 | 21 | 32226.7038 | 690.6573 | 700.6417 | 9.9844 | 2868.4 | 2167.7583 | -2167.7583 | 20.89% | 309.4% | 3106.1 | 2405.4583 | -2405.4583 | 23.18% | 343.3% | 21 | 0 | 1 | 0 | 0
2013-02-10 | 22 | 31216.1287 | 529.4312 | 536.5122 | 7.081 | 2751.8 | 2215.2878 | -2215.2878 | 21.34% | 412.9% | 2996.1 | 2459.5878 | -2459.5878 | 23.7% | 458.4% | 22 | 0 | 1 | 0 | 0
2013-02-10 | 23 | 29346.2102 | 350.0362 | 363.9087 | 13.8726 | 2750.1 | 2386.1913 | -2386.1913 | 22.99% | 655.7% | 2960.2 | 2596.2913 | -2596.2913 | 25.02% | 713.4% | 23 | 0 | 1 | 0 | 0
2013-02-10 | 24 | 27240.3691 | 390.5262 | 406.8878 | 16.3617 | 2904.4 | 2497.5122 | -2497.5122 | 24.06% | 613.8% | 3081.7 | 2674.8122 | -2674.8122 | 25.77% | 657.4% | 24 | 0 | 0 | 0 | 0
2013-02-11 | 1 | 25689.441 | 536.8234 | 556.6251 | 19.8017 | 2367 | 1810.3749 | -1810.3749 | 17.44% | 325.2% | 2465.5 | 1908.8749 | -1908.8749 | 18.39% | 342.9% | 1 | 0 | 0 | 0 | 0
2013-02-11 | 2 | 24808.1212 | 757.9784 | 778.1881 | 20.2097 | 2678 | 1899.8119 | -1899.8119 | 18.31% | 244.1% | 2774.2 | 1996.0119 | -1996.0119 | 19.23% | 256.5% | 2 | 0 | 0 | 0 | 0
2013-02-11 | 3 | 24465.6573 | 1221.9155 | 1235.3615 | 13.446 | 2672.5 | 1437.1385 | -1437.1385 | 13.85% | 116.3% | 2774.7 | 1539.3385 | -1539.3385 | 14.83% | 124.6% | 3 | 0 | 0 | 0 | 0
2013-02-11 | 4 | 24533.2269 | 1415.3844 | 1420.1413 | 4.7569 | 2691.9 | 1271.7587 | -1271.7587 | 12.25% | 89.55% | 2791.1 | 1370.9587 | -1370.9587 | 13.21% | 96.54% | 4 | 0 | 0 | 0 | 0
2013-02-11 | 5 | 25420.966 | 1642.9822 | 1646.7922 | 3.81 | 2837.2 | 1190.4078 | -1190.4078 | 11.47% | 72.29% | 2940.7 | 1293.9078 | -1293.9078 | 12.47% | 78.57% | 5 | 0 | 0 | 0 | 0
2013-02-11 | 6 | 27964.07 | 1791.2217 | 1793.2962 | 2.0745 | 3302.4 | 1509.1038 | -1509.1038 | 14.54% | 84.15% | 3447.3 | 1654.0038 | -1654.0038 | 15.94% | 92.23% | 6 | 0 | 0 | 0 | 0
2013-02-11 | 7 | 32131.3857 | 2067.6166 | 2073.8874 | 6.2708 | 3897.2 | 1823.3126 | -1823.3126 | 17.57% | 87.92% | 4013 | 1939.1126 | -1939.1126 | 18.68% | 93.5% | 7 | 0 | 0 | 0 | 0
2013-02-11 | 8 | 33672.0568 | 2560.044 | 2571.1315 | 11.0875 | 4018.7 | 1447.5685 | -1447.5685 | 13.95% | 56.3% | 4139.6 | 1568.4685 | -1568.4685 | 15.11% | 61% | 8 | 0 | 0 | 0 | 0
2013-02-11 | 9 | 33289.7412 | 2366.729 | 2370.3175 | 3.5885 | 4159.4 | 1789.0825 | -1789.0825 | 17.24% | 75.48% | 4213.9 | 1843.5825 | -1843.5825 | 17.76% | 77.78% | 9 | 0 | 0 | 0 | 0
2013-02-11 | 10 | 33557.5626 | 2170.7583 | 2174.9785 | 4.2202 | 3856.2 | 1681.2215 | -1681.2215 | 16.2% | 77.3% | 3853.2 | 1678.2215 | -1678.2215 | 16.17% | 77.16% | 10 | 0 | 0 | 0 | 0
2013-02-11 | 11 | 33879.2156 | 2238.8604 | 2254.3801 | 15.5197 | 3903.6 | 1649.2199 | -1649.2199 | 15.89% | 73.16% | 3849.4 | 1595.0199 | -1595.0199 | 15.37% | 70.75% | 11 | 0 | 0 | 0 | 0
2013-02-11 | 12 | 33901.4716 | 1919.2083 | 1921.0084 | 1.8001 | 4054.7 | 2133.6916 | -2133.6916 | 20.56% | 111.1% | 3991.4 | 2070.3916 | -2070.3916 | 19.95% | 107.8% | 12 | 0 | 0 | 0 | 0
2013-02-11 | 13 | 33746.3065 | 1727.898 | 1727.1438 | -0.75419 | 4143.6 | 2416.4562 | -2416.4562 | 23.28% | 139.9% | 4118.3 | 2391.1562 | -2391.1562 | 23.04% | 138.4% | 13 | 0 | 0 | 0 | 0
2013-02-11 | 14 | 33503.0394 | 1728.684 | 1728.1907 | -0.49328 | 4266.8 | 2538.6093 | -2538.6093 | 24.46% | 146.9% | 4277.7 | 2549.5093 | -2549.5093 | 24.57% | 147.5% | 14 | 0 | 0 | 0 | 0
2013-02-11 | 15 | 33200.0726 | 2016.1433 | 2015.3584 | -0.78489 | 4559.6 | 2544.2416 | -2544.2416 | 24.51% | 126.2% | 4574.1 | 2558.7416 | -2558.7416 | 24.65% | 127% | 15 | 0 | 0 | 0 | 0
2013-02-11 | 16 | 33250.6828 | 2531.006 | 2521.6891 | -9.3169 | 4729.5 | 2207.8109 | -2207.8109 | 21.27% | 87.55% | 4760 | 2238.3109 | -2238.3109 | 21.57% | 88.76% | 16 | 0 | 0 | 0 | 0
2013-02-11 | 17 | 33718.4298 | 2829.9179 | 2829.4806 | -0.43724 | 4821.8 | 1992.3194 | -1992.3194 | 19.2% | 70.41% | 4874.1 | 2044.6194 | -2044.6194 | 19.7% | 72.26% | 17 | 0 | 0 | 0 | 0
2013-02-11 | 18 | 34752.9411 | 3196.3289 | 3191.6932 | -4.6357 | 4671.6 | 1479.9068 | -1479.9068 | 14.26% | 46.37% | 4767.1 | 1575.4068 | -1575.4068 | 15.18% | 49.36% | 18 | 0 | 0 | 0 | 0
2013-02-11 | 19 | 36621.9642 | 3527.5589 | 3528.5208 | 0.96189 | 4948.5 | 1419.9792 | -1419.9792 | 13.68% | 40.24% | 5045.7 | 1517.1792 | -1517.1792 | 14.62% | 43% | 19 | 0 | 0 | 0 | 0
2013-02-11 | 20 | 36875.0323 | 4393.6386 | 4394.0507 | 0.41211 | 5420.1 | 1026.0493 | -1026.0493 | 9.886% | 23.35% | 5510.2 | 1116.1493 | -1116.1493 | 10.75% | 25.4% | 20 | 0 | 0 | 0 | 0
2013-02-11 | 21 | 36180.3594 | 5125.2685 | 5128.8097 | 3.5411 | 5842.2 | 713.3903 | -713.3903 | 6.874% | 13.91% | 5859.6 | 730.7903 | -730.7903 | 7.041% | 14.25% | 21 | 0 | 0 | 0 | 0
2013-02-11 | 22 | 34728.1546 | 4932.2911 | 4934.3592 | 2.068 | 5876.2 | 941.8408 | -941.8408 | 9.075% | 19.09% | 5867.2 | 932.8408 | -932.8408 | 8.988% | 18.91% | 22 | 0 | 0 | 0 | 0
2013-02-11 | 23 | 32115.6642 | 4066.7664 | 4067.2471 | 0.48077 | 5605.6 | 1538.3529 | -1538.3529 | 14.82% | 37.82% | 5582.3 | 1515.0529 | -1515.0529 | 14.6% | 37.25% | 23 | 0 | 0 | 0 | 0
2013-02-11 | 24 | 29530.0254 | 3701.3846 | 3705.7464 | 4.3618 | 5301.9 | 1596.1536 | -1596.1536 | 15.38% | 43.07% | 5261.9 | 1556.1536 | -1556.1536 | 14.99% | 41.99% | 24 | 0 | 0 | 0 | 0
2013-02-12 | 1 | 28003.6685 | 4007.7548 | 4007.7653 | 0.010483 | 2693.7 | 1314.0653 | 1314.0653 | 12.66% | 32.79% | 2868.6 | 1139.1653 | 1139.1653 | 10.98% | 28.42% | 1 | 1 | 0 | 1 | 1
2013-02-12 | 2 | 27232.602 | 3556.0291 | 3561.0299 | 5.0008 | 2398.1 | 1162.9299 | 1162.9299 | 11.21% | 32.66% | 2518.7 | 1042.3299 | 1042.3299 | 10.04% | 29.27% | 2 | 1 | 0 | 1 | 1
2013-02-12 | 3 | 26763.9437 | 2167.4082 | 2172.1019 | 4.6938 | 2289.9 | 117.7981 | -117.7981 | 1.135% | 5.423% | 2332.4 | 160.2981 | -160.2981 | 1.545% | 7.38% | 3 | 0 | 0 | 0 | 0
2013-02-12 | 4 | 26704.3768 | 1634.0379 | 1638.7876 | 4.7497 | 2168.9 | 530.1124 | -530.1124 | 5.108% | 32.35% | 2245.8 | 607.0124 | -607.0124 | 5.849% | 37.04% | 4 | 0 | 0 | 0 | 0
2013-02-12 | 5 | 27461.1978 | 1272.1275 | 1278.542 | 6.4145 | 2290.8 | 1012.258 | -1012.258 | 9.753% | 79.17% | 2420.7 | 1142.158 | -1142.158 | 11.01% | 89.33% | 5 | 0 | 0 | 0 | 0
2013-02-12 | 6 | 29893.3656 | 1190.9187 | 1195.5679 | 4.6492 | 2366.6 | 1171.0321 | -1171.0321 | 11.28% | 97.95% | 2467.8 | 1272.2321 | -1272.2321 | 12.26% | 106.4% | 6 | 0 | 0 | 0 | 0
2013-02-12 | 7 | 33924.7332 | 1145.1503 | 1172.1794 | 27.0291 | 2457.8 | 1285.6206 | -1285.6206 | 12.39% | 109.7% | 2536.1 | 1363.9206 | -1363.9206 | 13.14% | 116.4% | 7 | 0 | 0 | 0 | 0
2013-02-12 | 8 | 35146.9436 | 1180.8799 | 1215.8593 | 34.9794 | 2850.9 | 1635.0407 | -1635.0407 | 15.75% | 134.5% | 2921.4 | 1705.5407 | -1705.5407 | 16.43% | 140.3% | 8 | 0 | 0 | 0 | 0
2013-02-12 | 9 | 34539.0495 | 1151.6455 | 1213.8852 | 62.2398 | 3963.7 | 2749.8148 | -2749.8148 | 26.5% | 226.5% | 4009.3 | 2795.4148 | -2795.4148 | 26.93% | 230.3% | 9 | 0 | 0 | 0 | 0
2013-02-12 | 10 | 34588.9481 | 1175.68 | 1247.9717 | 72.2917 | 4718.7 | 3470.7283 | -3470.7283 | 33.44% | 278.1% | 4758.8 | 3510.8283 | -3510.8283 | 33.83% | 281.3% | 10 | 0 | 0 | 0 | 0
2013-02-12 | 11 | 34595.9706 | 1792.3199 | 1990.1478 | 197.8279 | 4752.6 | 2762.4522 | -2762.4522 | 26.62% | 138.8% | 4738.6 | 2748.4522 | -2748.4522 | 26.48% | 138.1% | 11 | 0 | 0 | 0 | 0
2013-02-12 | 12 | 34308.2166 | 2680.4839 | 2860.2429 | 179.7589 | 4857.5 | 1997.2571 | -1997.2571 | 19.24% | 69.83% | 4820.8 | 1960.5571 | -1960.5571 | 18.89% | 68.55% | 12 | 0 | 0 | 0 | 0
2013-02-12 | 13 | 33985.7947 | 3275.9997 | 3431.3775 | 155.3777 | 5189.4 | 1758.0225 | -1758.0225 | 16.94% | 51.23% | 5163.8 | 1732.4225 | -1732.4225 | 16.69% | 50.49% | 13 | 0 | 0 | 0 | 0
2013-02-12 | 14 | 33822.6611 | 3901.1658 | 3930.1931 | 29.0273 | 5482.1 | 1551.9069 | -1551.9069 | 14.95% | 39.49% | 5480.9 | 1550.7069 | -1550.7069 | 14.94% | 39.46% | 14 | 0 | 0 | 0 | 0
2013-02-12 | 15 | 33444.8508 | 4339.6003 | 4364.6342 | 25.0338 | 5478.4 | 1113.7658 | -1113.7658 | 10.73% | 25.52% | 5485.2 | 1120.5658 | -1120.5658 | 10.8% | 25.67% | 15 | 0 | 0 | 0 | 0
2013-02-12 | 16 | 33324.5378 | 5272.8135 | 5362.7354 | 89.9219 | 5527.6 | 164.8646 | -164.8646 | 1.589% | 3.074% | 5515.7 | 152.9646 | -152.9646 | 1.474% | 2.852% | 16 | 0 | 0 | 0 | 0
2013-02-12 | 17 | 33595.7289 | 6160.2241 | 6265.2291 | 105.005 | 5372 | 893.2291 | 893.2291 | 8.607% | 14.26% | 5325.8 | 939.4291 | 939.4291 | 9.052% | 14.99% | 17 | 1 | 0 | 1 | 1
2013-02-12 | 18 | 34235.3389 | 6317.7065 | 6335.3967 | 17.6902 | 5252.9 | 1082.4967 | 1082.4967 | 10.43% | 17.09% | 5108.5 | 1226.8967 | 1226.8967 | 11.82% | 19.37% | 18 | 1 | 0 | 1 | 1
2013-02-12 | 19 | 35930.1337 | 5207.092 | 5218.2217 | 11.1297 | 5075.2 | 143.0217 | 143.0217 | 1.378% | 2.741% | 5074.7 | 143.5217 | 143.5217 | 1.383% | 2.75% | 19 | 1 | 0 | 1 | 1
2013-02-12 | 20 | 36579.0059 | 4449.3247 | 4459.9631 | 10.6384 | 4990.1 | 530.1369 | -530.1369 | 5.108% | 11.89% | 5048.4 | 588.4369 | -588.4369 | 5.67% | 13.19% | 20 | 0 | 0 | 0 | 0
2013-02-12 | 21 | 36084.0069 | 3696.7921 | 3708.3428 | 11.5506 | 4801.3 | 1092.9572 | -1092.9572 | 10.53% | 29.47% | 4895.7 | 1187.3572 | -1187.3572 | 11.44% | 32.02% | 21 | 0 | 0 | 0 | 0
2013-02-12 | 22 | 34749.6724 | 2692.3383 | 2714.3739 | 22.0356 | 4474.9 | 1760.5261 | -1760.5261 | 16.96% | 64.86% | 4615.4 | 1901.0261 | -1901.0261 | 18.32% | 70.04% | 22 | 0 | 0 | 0 | 0
2013-02-12 | 23 | 32592.1998 | 1700.5067 | 1708.8664 | 8.3597 | 4220.7 | 2511.8336 | -2511.8336 | 24.2% | 147% | 4363.9 | 2655.0336 | -2655.0336 | 25.58% | 155.4% | 23 | 0 | 0 | 0 | 0
2013-02-12 | 24 | 30337.9065 | 1527.9941 | 1521.6906 | -6.3035 | 3842.5 | 2320.8094 | -2320.8094 | 22.36% | 152.5% | 4035.8 | 2514.1094 | -2514.1094 | 24.22% | 165.2% | 24 | 0 | 0 | 0 | 0
2013-02-13 | 1 | 28940.133 | 1391.4941 | 1391.0778 | -0.41627 | 3220.6 | 1829.5222 | -1829.5222 | 17.63% | 131.5% | 3541.9 | 2150.8222 | -2150.8222 | 20.72% | 154.6% | 1 | 0 | 1 | 0 | 0
2013-02-13 | 2 | 28368.3497 | 1306.6096 | 1305.3673 | -1.2423 | 3025.2 | 1719.8327 | -1719.8327 | 16.57% | 131.8% | 3343 | 2037.6327 | -2037.6327 | 19.63% | 156.1% | 2 | 0 | 1 | 0 | 0
2013-02-13 | 3 | 28296.9761 | 1252.1952 | 1262.9451 | 10.7499 | 2971.6 | 1708.6549 | -1708.6549 | 16.46% | 135.3% | 3210 | 1947.0549 | -1947.0549 | 18.76% | 154.2% | 3 | 0 | 1 | 0 | 0
2013-02-13 | 4 | 28640.5477 | 1501.1816 | 1499.3768 | -1.8048 | 2987.5 | 1488.1232 | -1488.1232 | 14.34% | 99.25% | 3193.8 | 1694.4232 | -1694.4232 | 16.33% | 113% | 4 | 0 | 0 | 0 | 0
2013-02-13 | 5 | 29765.3254 | 1791.4864 | 1790.8056 | -0.6808 | 3074.7 | 1283.8944 | -1283.8944 | 12.37% | 71.69% | 3245.6 | 1454.7944 | -1454.7944 | 14.02% | 81.24% | 5 | 0 | 0 | 0 | 0
2013-02-13 | 6 | 32598.8151 | 1657.1762 | 1810.0427 | 152.8665 | 3115.8 | 1305.7573 | -1305.7573 | 12.58% | 72.14% | 3336 | 1525.9573 | -1525.9573 | 14.7% | 84.31% | 6 | 0 | 1 | 0 | 0
2013-02-13 | 7 | 37173.955 | 1626.5502 | 1641.9754 | 15.4252 | 3102.5 | 1460.5246 | -1460.5246 | 14.07% | 88.95% | 3345.4 | 1703.4246 | -1703.4246 | 16.41% | 103.7% | 7 | 0 | 1 | 0 | 0
2013-02-13 | 8 | 38483.3541 | 1659.5381 | 1667.5278 | 7.9897 | 2907 | 1239.4722 | -1239.4722 | 11.94% | 74.33% | 3139.6 | 1472.0722 | -1472.0722 | 14.18% | 88.28% | 8 | 0 | 1 | 0 | 0
2013-02-13 | 9 | 37438.1631 | 1769.8897 | 1774.269 | 4.3793 | 2508.9 | 734.631 | -734.631 | 7.078% | 41.4% | 2667.8 | 893.531 | -893.531 | 8.609% | 50.36% | 9 | 0 | 0 | 0 | 0
2013-02-13 | 10 | 36683.4389 | 1365.1133 | 1375.3166 | 10.2033 | 1754.7 | 379.3834 | -379.3834 | 3.655% | 27.59% | 1882.6 | 507.2834 | -507.2834 | 4.888% | 36.88% | 10 | 0 | 0 | 0 | 0
2013-02-13 | 11 | 35816.1267 | 925.9873 | 941.1343 | 15.1471 | 1481.2 | 540.0657 | -540.0657 | 5.204% | 57.38% | 1596.3 | 655.1657 | -655.1657 | 6.313% | 69.61% | 11 | 0 | 0 | 0 | 0
2013-02-13 | 12 | 34562.3254 | 651.1701 | 662.0608 | 10.8908 | 1424.2 | 762.1392 | -762.1392 | 7.343% | 115.1% | 1527.4 | 865.3392 | -865.3392 | 8.338% | 130.7% | 12 | 0 | 0 | 0 | 0
2013-02-13 | 13 | 33291.3139 | 735.7287 | 741.2429 | 5.5142 | 1404.1 | 662.8571 | -662.8571 | 6.387% | 89.43% | 1484.6 | 743.3571 | -743.3571 | 7.162% | 100.3% | 13 | 0 | 0 | 0 | 0
2013-02-13 | 14 | 32521.3859 | 893.1832 | 894.6736 | 1.4904 | 1362.6 | 467.9264 | -467.9264 | 4.509% | 52.3% | 1439.8 | 545.1264 | -545.1264 | 5.252% | 60.93% | 14 | 0 | 0 | 0 | 0
2013-02-13 | 15 | 31829.4785 | 1037.0024 | 1034.7716 | -2.2307 | 1338.9 | 304.1284 | -304.1284 | 2.93% | 29.39% | 1406.7 | 371.9284 | -371.9284 | 3.584% | 35.94% | 15 | 0 | 0 | 0 | 0
2013-02-13 | 16 | 31395.1765 | 1100.5512 | 1094.1527 | -6.3985 | 1306.9 | 212.7473 | -212.7473 | 2.05% | 19.44% | 1372 | 277.8473 | -277.8473 | 2.677% | 25.39% | 16 | 0 | 0 | 0 | 0
2013-02-13 | 17 | 31342.4713 | 919.7905 | 918.1502 | -1.6403 | 1250.1 | 331.9498 | -331.9498 | 3.198% | 36.15% | 1305.7 | 387.5498 | -387.5498 | 3.734% | 42.21% | 17 | 0 | 0 | 0 | 0
2013-02-13 | 18 | 31742.1177 | 624.9653 | 623.9131 | -1.0522 | 1079.7 | 455.7869 | -455.7869 | 4.392% | 73.05% | 1134.4 | 510.4869 | -510.4869 | 4.919% | 81.82% | 18 | 0 | 0 | 0 | 0
2013-02-13 | 19 | 34050.7314 | 345.2337 | 349.9124 | 4.6787 | 1065.7 | 715.7876 | -715.7876 | 6.897% | 204.6% | 1125 | 775.0876 | -775.0876 | 7.468% | 221.5% | 19 | 0 | 0 | 0 | 0
2013-02-13 | 20 | 35340.9745 | 349.2161 | 357.6653 | 8.4492 | 1194.9 | 837.2347 | -837.2347 | 8.067% | 234.1% | 1249.4 | 891.7347 | -891.7347 | 8.592% | 249.3% | 20 | 0 | 0 | 0 | 0
2013-02-13 | 21 | 35477.7951 | 607.2049 | 614.7697 | 7.5648 | 1450.2 | 835.4303 | -835.4303 | 8.05% | 135.9% | 1511.6 | 896.8303 | -896.8303 | 8.641% | 145.9% | 21 | 0 | 0 | 0 | 0
2013-02-13 | 22 | 34911.5243 | 1285.2412 | 1295.5468 | 10.3056 | 1787.2 | 491.6532 | -491.6532 | 4.737% | 37.95% | 1838.2 | 542.6532 | -542.6532 | 5.229% | 41.89% | 22 | 0 | 0 | 0 | 0
2013-02-13 | 23 | 33030.8316 | 1950.5506 | 1972.0748 | 21.5241 | 2240 | 267.9252 | -267.9252 | 2.582% | 13.59% | 2280.9 | 308.8252 | -308.8252 | 2.976% | 15.66% | 23 | 0 | 0 | 0 | 0
2013-02-13 | 24 | 30949.9191 | 2621.9188 | 2641.0848 | 19.166 | 2513.8 | 127.2848 | 127.2848 | 1.226% | 4.819% | 2579.3 | 61.7848 | 61.7848 | 0.5953% | 2.339% | 24 | 1 | 0 | 1 | 1
2013-02-14 | 1 | 29719.3152 | 3244.8725 | 3261.5354 | 16.6629 | 2563.3 | 698.2354 | 698.2354 | 6.728% | 21.41% | 2622.7 | 638.8354 | 638.8354 | 6.155% | 19.59% | 1 | 1 | 0 | 1 | 1
2013-02-14 | 2 | 29345.6752 | 3890.8889 | 3895.3741 | 4.4852 | 2799.7 | 1095.6741 | 1095.6741 | 10.56% | 28.13% | 2803.1 | 1092.2741 | 1092.2741 | 10.52% | 28.04% | 2 | 1 | 0 | 1 | 1
2013-02-14 | 3 | 29430.5643 | 4167.5919 | 4172.5843 | 4.9924 | 2959.6 | 1212.9843 | 1212.9843 | 11.69% | 29.07% | 2918.3 | 1254.2843 | 1254.2843 | 12.09% | 30.06% | 3 | 1 | 0 | 1 | 1
2013-02-14 | 4 | 29950.9871 | 3937.4109 | 3941.0091 | 3.5982 | 3041.9 | 899.1091 | 899.1091 | 8.663% | 22.81% | 3014.5 | 926.5091 | 926.5091 | 8.927% | 23.51% | 4 | 1 | 0 | 1 | 1
2013-02-14 | 5 | 31194.9983 | 3611.622 | 3615.8017 | 4.1797 | 3100 | 515.8017 | 515.8017 | 4.97% | 14.27% | 3063 | 552.8017 | 552.8017 | 5.326% | 15.29% | 5 | 1 | 0 | 1 | 1
2013-02-14 | 6 | 34308.6097 | 3463.8875 | 3468.5065 | 4.619 | 3064.4 | 404.1065 | 404.1065 | 3.894% | 11.65% | 3001.6 | 466.9065 | 466.9065 | 4.499% | 13.46% | 6 | 1 | 0 | 1 | 1
2013-02-14 | 7 | 39172.0675 | 3362.0062 | 3366.7837 | 4.7774 | 2852.4 | 514.3837 | 514.3837 | 4.956% | 15.28% | 2773.3 | 593.4837 | 593.4837 | 5.718% | 17.63% | 7 | 1 | 0 | 1 | 1
2013-02-14 | 8 | 40021.0624 | 3439.1058 | 3441.9788 | 2.873 | 2382.7 | 1059.2788 | 1059.2788 | 10.21% | 30.78% | 2328.3 | 1113.6788 | 1113.6788 | 10.73% | 32.36% | 8 | 1 | 0 | 1 | 1
2013-02-14 | 9 | 37869.54 | 2862.5734 | 2865.9594 | 3.386 | 1773.7 | 1092.2594 | 1092.2594 | 10.52% | 38.11% | 1760.9 | 1105.0594 | 1105.0594 | 10.65% | 38.56% | 9 | 1 | 0 | 1 | 1
2013-02-14 | 10 | 36068.9113 | 2010.3817 | 2013.7941 | 3.4124 | 1138 | 875.7941 | 875.7941 | 8.439% | 43.49% | 1124.3 | 889.4941 | 889.4941 | 8.571% | 44.17% | 10 | 1 | 0 | 1 | 1
2013-02-14 | 11 | 34601.6335 | 1405.7828 | 1410.5017 | 4.7189 | 822 | 588.5017 | 588.5017 | 5.67% | 41.72% | 823.5 | 587.0017 | 587.0017 | 5.656% | 41.62% | 11 | 1 | 0 | 1 | 1
2013-02-14 | 12 | 33294.9522 | 971.3737 | 975.0945 | 3.7208 | 727.5 | 247.5945 | 247.5945 | 2.386% | 25.39% | 745.2 | 229.8945 | 229.8945 | 2.215% | 23.58% | 12 | 1 | 0 | 1 | 1
2013-02-14 | 13 | 32211.9122 | 849.9031 | 852.5165 | 2.6134 | 748 | 104.5165 | 104.5165 | 1.007% | 12.26% | 778.8 | 73.7165 | 73.7165 | 0.7103% | 8.647% | 13 | 1 | 0 | 1 | 1
2013-02-14 | 14 | 31746.0366 | 874.7163 | 875.34 | 0.6237 | 799.9 | 75.44 | 75.44 | 0.7269% | 8.618% | 841.1 | 34.24 | 34.24 | 0.3299% | 3.912% | 14 | 1 | 0 | 1 | 1
2013-02-14 | 15 | 31285.4593 | 1170.5941 | 1171.2675 | 0.6734 | 817.4 | 353.8675 | 353.8675 | 3.41% | 30.21% | 869.6 | 301.6675 | 301.6675 | 2.907% | 25.76% | 15 | 1 | 0 | 1 | 1
2013-02-14 | 16 | 30995.53 | 1243.7748 | 1248.1327 | 4.3579 | 855.4 | 392.7327 | 392.7327 | 3.784% | 31.47% | 911.9 | 336.2327 | 336.2327 | 3.24% | 26.94% | 16 | 1 | 0 | 1 | 1
2013-02-14 | 17 | 30916.8104 | 1143.6363 | 1150.8172 | 7.1809 | 831.3 | 319.5172 | 319.5172 | 3.079% | 27.76% | 898 | 252.8172 | 252.8172 | 2.436% | 21.97% | 17 | 1 | 0 | 1 | 1
2013-02-14 | 18 | 30998.6047 | 944.6091 | 956.3982 | 11.7891 | 848.2 | 108.1982 | 108.1982 | 1.043% | 11.31% | 927.4 | 28.9982 | 28.9982 | 0.2794% | 3.032% | 18 | 1 | 0 | 1 | 1
2013-02-14 | 19 | 32738.1613 | 707.9012 | 721.668 | 13.7668 | 1249.6 | 527.932 | -527.932 | 5.087% | 73.15% | 1344.5 | 622.832 | -622.832 | 6.001% | 86.3% | 19 | 0 | 0 | 0 | 0
2013-02-14 | 20 | 33702.1774 | 948.666 | 983.0072 | 34.3412 | 2050.6 | 1067.5928 | -1067.5928 | 10.29% | 108.6% | 2170.5 | 1187.4928 | -1187.4928 | 11.44% | 120.8% | 20 | 0 | 0 | 0 | 0
2013-02-14 | 21 | 33391.2306 | 1728.1646 | 1782.7711 | 54.6065 | 2713.4 | 930.6289 | -930.6289 | 8.967% | 52.2% | 2874.7 | 1091.9289 | -1091.9289 | 10.52% | 61.25% | 21 | 0 | 0 | 0 | 0
2013-02-14 | 22 | 32358.2306 | 2952.4671 | 2992.5231 | 40.056 | 3417.7 | 425.1769 | -425.1769 | 4.097% | 14.21% | 3603.8 | 611.2769 | -611.2769 | 5.89% | 20.43% | 22 | 0 | 0 | 0 | 0
2013-02-14 | 23 | 30571.2384 | 5039.5475 | 5071.3992 | 31.8517 | 4051.9 | 1019.4992 | 1019.4992 | 9.823% | 20.1% | 4254.2 | 817.1992 | 817.1992 | 7.874% | 16.11% | 23 | 1 | 0 | 1 | 1
2013-02-14 | 24 | 28758.4232 | 6655.5282 | 6763.9255 | 108.3973 | 4270.5 | 2493.4255 | 2493.4255 | 24.02% | 36.86% | 4515.1 | 2248.8255 | 2248.8255 | 21.67% | 33.25% | 24 | 1 | 1 | 1 | 1
2013-02-15 | 1 | 27716.6481 | 7054.268 | 7120.2645 | 65.9965 | 5165.8 | 1954.4645 | 1954.4645 | 18.83% | 27.45% | 5336.7 | 1783.5645 | 1783.5645 | 17.19% | 25.05% | 1 | 1 | 0 | 1 | 1
2013-02-15 | 2 | 27316.5961 | 7144.3111 | 7254.0301 | 109.719 | 5292.5 | 1961.5301 | 1961.5301 | 18.9% | 27.04% | 5407.5 | 1846.5301 | 1846.5301 | 17.79% | 25.46% | 2 | 1 | 0 | 1 | 1
2013-02-15 | 3 | 27299.8726 | 6993.7771 | 7297.1583 | 303.3812 | 5309.4 | 1987.7583 | 1987.7583 | 19.15% | 27.24% | 5360 | 1937.1583 | 1937.1583 | 18.67% | 26.55% | 3 | 1 | 0 | 1 | 1
2013-02-15 | 4 | 27599.5893 | 6912.9542 | 7148.526 | 235.5718 | 5178.3 | 1970.226 | 1970.226 | 18.98% | 27.56% | 5170.1 | 1978.426 | 1978.426 | 19.06% | 27.68% | 4 | 1 | 0 | 1 | 1
2013-02-15 | 5 | 28698.9501 | 6940.4631 | 7050.2235 | 109.7604 | 4849.5 | 2200.7235 | 2200.7235 | 21.2% | 31.21% | 4832.7 | 2217.5235 | 2217.5235 | 21.37% | 31.45% | 5 | 1 | 0 | 1 | 1
2013-02-15 | 6 | 31339.8481 | 6761.0988 | 6783.8825 | 22.7836 | 4479.7 | 2304.1825 | 2304.1825 | 22.2% | 33.97% | 4467.9 | 2315.9825 | 2315.9825 | 22.32% | 34.14% | 6 | 1 | 0 | 1 | 1
2013-02-15 | 7 | 35752.0661 | 6152.262 | 6178.7079 | 26.4459 | 4303.8 | 1874.9079 | 1874.9079 | 18.07% | 30.34% | 4256.5 | 1922.2079 | 1922.2079 | 18.52% | 31.11% | 7 | 1 | 0 | 1 | 1
2013-02-15 | 8 | 36994.0056 | 5257.2387 | 5272.0194 | 14.7806 | 3897.9 | 1374.1194 | 1374.1194 | 13.24% | 26.06% | 3915 | 1357.0194 | 1357.0194 | 13.08% | 25.74% | 8 | 1 | 0 | 1 | 1
2013-02-15 | 9 | 36105.563 | 4887.5141 | 4889.4267 | 1.9125 | 3431.1 | 1458.3267 | 1458.3267 | 14.05% | 29.83% | 3466.9 | 1422.5267 | 1422.5267 | 13.71% | 29.09% | 9 | 1 | 0 | 1 | 1
2013-02-15 | 10 | 35697.5908 | 4667.4611 | 4862.0257 | 194.5646 | 3147.6 | 1714.4257 | 1714.4257 | 16.52% | 35.26% | 3158.6 | 1703.4257 | 1703.4257 | 16.41% | 35.04% | 10 | 1 | 0 | 1 | 1
2013-02-15 | 11 | 35281.5195 | 4689.1653 | 4692.8741 | 3.7087 | 2759.5 | 1933.3741 | 1933.3741 | 18.63% | 41.2% | 2760.9 | 1931.9741 | 1931.9741 | 18.62% | 41.17% | 11 | 1 | 0 | 1 | 1
2013-02-15 | 12 | 34595.2234 | 4332.3045 | 4335.9795 | 3.675 | 2356.3 | 1979.6795 | 1979.6795 | 19.07% | 45.66% | 2335.6 | 2000.3795 | 2000.3795 | 19.27% | 46.13% | 12 | 1 | 0 | 1 | 1
2013-02-15 | 13 | 34016.9684 | 3679.3005 | 3680.3236 | 1.0231 | 1911.5 | 1768.8236 | 1768.8236 | 17.04% | 48.06% | 1914.5 | 1765.8236 | 1765.8236 | 17.01% | 47.98% | 13 | 1 | 0 | 1 | 1
2013-02-15 | 14 | 33725.3415 | 3147.8623 | 3147.2237 | -0.63858 | 1713.7 | 1433.5237 | 1433.5237 | 13.81% | 45.55% | 1747 | 1400.2237 | 1400.2237 | 13.49% | 44.49% | 14 | 1 | 0 | 1 | 1
2013-02-15 | 15 | 33315.187 | 2972.0069 | 2970.5136 | -1.4933 | 1582.5 | 1388.0136 | 1388.0136 | 13.37% | 46.73% | 1629.9 | 1340.6136 | 1340.6136 | 12.92% | 45.13% | 15 | 1 | 0 | 1 | 1
2013-02-15 | 16 | 32873.6963 | 2767.7885 | 2765.8875 | -1.9011 | 1542.5 | 1223.3875 | 1223.3875 | 11.79% | 44.23% | 1593.4 | 1172.4875 | 1172.4875 | 11.3% | 42.39% | 16 | 1 | 0 | 1 | 1
2013-02-15 | 17 | 32993.3205 | 2321.3228 | 2320.8212 | -0.50159 | 1416.1 | 904.7212 | 904.7212 | 8.717% | 38.98% | 1489.4 | 831.4212 | 831.4212 | 8.011% | 35.82% | 17 | 1 | 0 | 1 | 1
2013-02-15 | 18 | 33505.0257 | 1917.9525 | 1915.7153 | -2.2372 | 1301.8 | 613.9153 | 613.9153 | 5.915% | 32.05% | 1393.1 | 522.6153 | 522.6153 | 5.036% | 27.28% | 18 | 1 | 0 | 1 | 1
2013-02-15 | 19 | 35551.5662 | 1406.9586 | 1410.8339 | 3.8754 | 1223.9 | 186.9339 | 186.9339 | 1.801% | 13.25% | 1355.2 | 55.6339 | 55.6339 | 0.536% | 3.943% | 19 | 1 | 0 | 1 | 1
2013-02-15 | 20 | 36341.3697 | 758.7973 | 772.0387 | 13.2413 | 1182.6 | 410.5613 | -410.5613 | 3.956% | 53.18% | 1356.9 | 584.8613 | -584.8613 | 5.635% | 75.76% | 20 | 0 | 0 | 0 | 0
2013-02-15 | 21 | 36056.8367 | 612.2112 | 614.6768 | 2.4657 | 1186.8 | 572.1232 | -572.1232 | 5.513% | 93.08% | 1412.4 | 797.7232 | -797.7232 | 7.686% | 129.8% | 21 | 0 | 1 | 0 | 0
2013-02-15 | 22 | 35393.179 | 505.7944 | 515.1826 | 9.3883 | 1536.3 | 1021.1174 | -1021.1174 | 9.839% | 198.2% | 1804.3 | 1289.1174 | -1289.1174 | 12.42% | 250.2% | 22 | 0 | 1 | 0 | 0
2013-02-15 | 23 | 34165.6964 | 687.9993 | 696.6451 | 8.6457 | 1601.1 | 904.4549 | -904.4549 | 8.715% | 129.8% | 1881 | 1184.3549 | -1184.3549 | 11.41% | 170% | 23 | 0 | 1 | 0 | 0
2013-02-15 | 24 | 32676.6919 | 765.7457 | 782.7557 | 17.01 | 1702 | 919.2443 | -919.2443 | 8.857% | 117.4% | 1994.7 | 1211.9443 | -1211.9443 | 11.68% | 154.8% | 24 | 0 | 1 | 0 | 0
2013-02-16 | 1 | 31587.6639 | 1319.4801 | 1327.6259 | 8.1458 | 2250.4 | 922.7741 | -922.7741 | 8.891% | 69.51% | 2574.3 | 1246.6741 | -1246.6741 | 12.01% | 93.9% | 1 | 0 | 1 | 0 | 0
2013-02-16 | 2 | 31187.8438 | 1467.2363 | 1488.2287 | 20.9924 | 2684 | 1195.7713 | -1195.7713 | 11.52% | 80.35% | 2978.8 | 1490.5713 | -1490.5713 | 14.36% | 100.2% | 2 | 0 | 1 | 0 | 0
2013-02-16 | 3 | 31122.0498 | 1711.3396 | 1735.13 | 23.7904 | 3154.4 | 1419.27 | -1419.27 | 13.68% | 81.8% | 3402.8 | 1667.67 | -1667.67 | 16.07% | 96.11% | 3 | 0 | 1 | 0 | 0
2013-02-16 | 4 | 31415.8092 | 1838.174 | 1841.0841 | 2.91 | 3554.4 | 1713.3159 | -1713.3159 | 16.51% | 93.06% | 3754.7 | 1913.6159 | -1913.6159 | 18.44% | 103.9% | 4 | 0 | 0 | 0 | 0
2013-02-16 | 5 | 32183.2725 | 2013.0008 | 2020.5365 | 7.5356 | 3758.3 | 1737.7635 | -1737.7635 | 16.74% | 86.01% | 3888.6 | 1868.0635 | -1868.0635 | 18% | 92.45% | 5 | 0 | 0 | 0 | 0
2013-02-16 | 6 | 33758.896 | 2045.413 | 2055.3555 | 9.9426 | 3803 | 1747.6445 | -1747.6445 | 16.84% | 85.03% | 3932.8 | 1877.4445 | -1877.4445 | 18.09% | 91.34% | 6 | 0 | 0 | 0 | 0
2013-02-16 | 7 | 35886.7318 | 2014.0702 | 2013.8155 | -0.2547 | 3765.9 | 1752.0845 | -1752.0845 | 16.88% | 87% | 3872.5 | 1858.6845 | -1858.6845 | 17.91% | 92.3% | 7 | 0 | 0 | 0 | 0
2013-02-16 | 8 | 37356.0896 | 1925.0133 | 1949.1717 | 24.1584 | 3645.1 | 1695.9283 | -1695.9283 | 16.34% | 87.01% | 3719 | 1769.8283 | -1769.8283 | 17.05% | 90.8% | 8 | 0 | 0 | 0 | 0
2013-02-16 | 9 | 37498.913 | 1474.4946 | 1478.5699 | 4.0754 | 3202 | 1723.4301 | -1723.4301 | 16.61% | 116.6% | 3238.5 | 1759.9301 | -1759.9301 | 16.96% | 119% | 9 | 0 | 0 | 0 | 0
2013-02-16 | 10 | 36655.9602 | 1082.1379 | 1089.8344 | 7.6964 | 2387.2 | 1297.3656 | -1297.3656 | 12.5% | 119% | 2419.1 | 1329.2656 | -1329.2656 | 12.81% | 122% | 10 | 0 | 0 | 0 | 0
2013-02-16 | 11 | 35249.7728 | 879.0025 | 884.8487 | 5.8462 | 2113.7 | 1228.8513 | -1228.8513 | 11.84% | 138.9% | 2137.1 | 1252.2513 | -1252.2513 | 12.07% | 141.5% | 11 | 0 | 0 | 0 | 0
2013-02-16 | 12 | 33571.1095 | 836.6482 | 829.8603 | -6.7879 | 2169.1 | 1339.2397 | -1339.2397 | 12.9% | 161.4% | 2185.2 | 1355.3397 | -1355.3397 | 13.06% | 163.3% | 12 | 0 | 0 | 0 | 0
2013-02-16 | 13 | 31934.8138 | 1310.9632 | 1303.0958 | -7.8675 | 2474.8 | 1171.7042 | -1171.7042 | 11.29% | 89.92% | 2465.3 | 1162.2042 | -1162.2042 | 11.2% | 89.19% | 13 | 0 | 0 | 0 | 0
2013-02-16 | 14 | 30478.8735 | 2185.5231 | 2186.0916 | 0.56846 | 2839.8 | 653.7084 | -653.7084 | 6.299% | 29.9% | 2834.4 | 648.3084 | -648.3084 | 6.247% | 29.66% | 14 | 0 | 0 | 0 | 0
2013-02-16 | 15 | 29355.7111 | 2181.4549 | 2181.815 | 0.36009 | 3182.4 | 1000.585 | -1000.585 | 9.641% | 45.86% | 3174.7 | 992.885 | -992.885 | 9.567% | 45.51% | 15 | 0 | 0 | 0 | 0
2013-02-16 | 16 | 28775.4657 | 1751.4569 | 1753.1611 | 1.7042 | 3243 | 1489.8389 | -1489.8389 | 14.36% | 84.98% | 3237.5 | 1484.3389 | -1484.3389 | 14.3% | 84.67% | 16 | 0 | 0 | 0 | 0
2013-02-16 | 17 | 28649.7183 | 1467.124 | 1472.7948 | 5.6708 | 3094.3 | 1621.5052 | -1621.5052 | 15.62% | 110.1% | 3092 | 1619.2052 | -1619.2052 | 15.6% | 109.9% | 17 | 0 | 0 | 0 | 0
2013-02-16 | 18 | 29087.0182 | 1089.3442 | 1090.138 | 0.79379 | 2657.2 | 1567.062 | -1567.062 | 15.1% | 143.7% | 2660.6 | 1570.462 | -1570.462 | 15.13% | 144.1% | 18 | 0 | 0 | 0 | 0
2013-02-16 | 19 | 31284.3561 | 1082.8569 | 1088.6555 | 5.7986 | 2999.5 | 1910.8445 | -1910.8445 | 18.41% | 175.5% | 3028.2 | 1939.5445 | -1939.5445 | 18.69% | 178.2% | 19 | 0 | 0 | 0 | 0
2013-02-16 | 20 | 32741.2139 | 1788.1461 | 1794.6028 | 6.4568 | 3758.1 | 1963.4972 | -1963.4972 | 18.92% | 109.4% | 3851.1 | 2056.4972 | -2056.4972 | 19.81% | 114.6% | 20 | 0 | 0 | 0 | 0
2013-02-16 | 21 | 32803.9687 | 2681.1775 | 2733.6371 | 52.4596 | 4585.9 | 1852.2629 | -1852.2629 | 17.85% | 67.76% | 4681.8 | 1948.1629 | -1948.1629 | 18.77% | 71.27% | 21 | 0 | 0 | 0 | 0
2013-02-16 | 22 | 32529.9463 | 4521.1937 | 4560.9609 | 39.7672 | 5235.1 | 674.1391 | -674.1391 | 6.496% | 14.78% | 5317.7 | 756.7391 | -756.7391 | 7.291% | 16.59% | 22 | 0 | 0 | 0 | 0
2013-02-16 | 23 | 31704.4308 | 5980.4306 | 6018.349 | 37.9184 | 5940.2 | 78.149 | 78.149 | 0.753% | 1.299% | 6012.3 | 6.049 | 6.049 | 0.05828% | 0.1005% | 23 | 1 | 0 | 1 | 1
2013-02-16 | 24 | 30677.3681 | 6615.1835 | 6789.6977 | 174.5142 | 6437.2 | 352.4977 | 352.4977 | 3.396% | 5.192% | 6507.6 | 282.0977 | 282.0977 | 2.718% | 4.155% | 24 | 1 | 0 | 1 | 1
2013-02-17 | 1 | 29719.8085 | 6920.3849 | 7095.8184 | 175.4335 | 6093.2 | 1002.6184 | 1002.6184 | 9.661% | 14.13% | 6120.4 | 975.4184 | 975.4184 | 9.398% | 13.75% | 1 | 1 | 0 | 1 | 1
2013-02-17 | 2 | 29238.6153 | 7038.7146 | 7239.9584 | 201.2438 | 6151.7 | 1088.2584 | 1088.2584 | 10.49% | 15.03% | 6174.4 | 1065.5584 | 1065.5584 | 10.27% | 14.72% | 2 | 1 | 0 | 1 | 1
2013-02-17 | 3 | 29192.0492 | 7071.483 | 7117.6096 | 46.1266 | 6170.7 | 946.9096 | 946.9096 | 9.124% | 13.3% | 6221.4 | 896.2096 | 896.2096 | 8.635% | 12.59% | 3 | 1 | 0 | 1 | 1
2013-02-17 | 4 | 29332.4639 | 6915.503 | 6975.2749 | 59.7719 | 6085.4 | 889.8749 | 889.8749 | 8.574% | 12.76% | 6154.1 | 821.1749 | 821.1749 | 7.912% | 11.77% | 4 | 1 | 0 | 1 | 1
2013-02-17 | 5 | 29780.0143 | 6699.0963 | 6750.6474 | 51.5512 | 5991 | 759.6474 | 759.6474 | 7.319% | 11.25% | 6073.7 | 676.9474 | 676.9474 | 6.523% | 10.03% | 5 | 1 | 0 | 1 | 1
2013-02-17 | 6 | 30881.8671 | 6622.7004 | 6687.2426 | 64.5422 | 5958.5 | 728.7426 | 728.7426 | 7.022% | 10.9% | 6050.3 | 636.9426 | 636.9426 | 6.137% | 9.525% | 6 | 1 | 0 | 1 | 1
2013-02-17 | 7 | 32308.0205 | 6409.6761 | 6454.5937 | 44.9176 | 5867.6 | 586.9937 | 586.9937 | 5.656% | 9.094% | 5975.6 | 478.9937 | 478.9937 | 4.615% | 7.421% | 7 | 1 | 0 | 1 | 1
2013-02-17 | 8 | 33185.7725 | 6356.0833 | 6394.1653 | 38.082 | 5845.1 | 549.0653 | 549.0653 | 5.29% | 8.587% | 5969.5 | 424.6653 | 424.6653 | 4.092% | 6.641% | 8 | 1 | 0 | 1 | 1
2013-02-17 | 9 | 33381.5473 | 5769.9897 | 5827.574 | 57.5843 | 5457.9 | 369.674 | 369.674 | 3.562% | 6.344% | 5582.8 | 244.774 | 244.774 | 2.358% | 4.2% | 9 | 1 | 0 | 1 | 1
2013-02-17 | 10 | 32558.0096 | 5285.4157 | 5304.1251 | 18.7094 | 4654.1 | 650.0251 | 650.0251 | 6.263% | 12.26% | 4801.8 | 502.3251 | 502.3251 | 4.84% | 9.47% | 10 | 1 | 0 | 1 | 1
2013-02-17 | 11 | 31306.6337 | 6036.5053 | 6049.4189 | 12.9136 | 4546.5 | 1502.9189 | 1502.9189 | 14.48% | 24.84% | 4777.1 | 1272.3189 | 1272.3189 | 12.26% | 21.03% | 11 | 1 | 1 | 1 | 1
2013-02-17 | 12 | 30230.5059 | 6812.1235 | 6819.2826 | 7.1591 | 4678.9 | 2140.3826 | 2140.3826 | 20.62% | 31.39% | 4945.6 | 1873.6826 | 1873.6826 | 18.05% | 27.48% | 12 | 1 | 1 | 1 | 1
2013-02-17 | 13 | 29453.6245 | 7148.6532 | 7162.6091 | 13.9559 | 5012.2 | 2150.4091 | 2150.4091 | 20.72% | 30.02% | 5298 | 1864.6091 | 1864.6091 | 17.97% | 26.03% | 13 | 1 | 1 | 1 | 1
2013-02-17 | 14 | 28801.8441 | 7376.026 | 7450.962 | 74.9361 | 5304.7 | 2146.262 | 2146.262 | 20.68% | 28.81% | 5606.3 | 1844.662 | 1844.662 | 17.77% | 24.76% | 14 | 1 | 1 | 1 | 1
2013-02-17 | 15 | 28416.4646 | 7698.8011 | 7866.4184 | 167.6173 | 5782.9 | 2083.5184 | 2083.5184 | 20.08% | 26.49% | 6067.4 | 1799.0184 | 1799.0184 | 17.33% | 22.87% | 15 | 1 | 1 | 1 | 1
2013-02-17 | 16 | 28201.2531 | 7748.2847 | 8224.1226 | 475.8379 | 6204.6 | 2019.5226 | 2019.5226 | 19.46% | 24.56% | 6483.4 | 1740.7226 | 1740.7226 | 16.77% | 21.17% | 16 | 1 | 1 | 1 | 1
2013-02-17 | 17 | 28356.0464 | 7812.6639 | 8495.9815 | 683.3176 | 6625.7 | 1870.2815 | 1870.2815 | 18.02% | 22.01% | 6892.4 | 1603.5815 | 1603.5815 | 15.45% | 18.87% | 17 | 1 | 1 | 1 | 1
2013-02-17 | 18 | 29010.4021 | 7842.5115 | 8516.27 | 673.7585 | 6628.8 | 1887.47 | 1887.47 | 18.19% | 22.16% | 6925.5 | 1590.77 | 1590.77 | 15.33% | 18.68% | 18 | 1 | 1 | 1 | 1
2013-02-17 | 19 | 31086.6369 | 7909.824 | 8444.514 | 534.69 | 7254.2 | 1190.314 | 1190.314 | 11.47% | 14.1% | 7532.9 | 911.614 | 911.614 | 8.784% | 10.8% | 19 | 1 | 1 | 1 | 1
2013-02-17 | 20 | 32262.4094 | 7964.7066 | 8654.1167 | 689.41 | 8149.1 | 505.0167 | 505.0167 | 4.866% | 5.836% | 8394.8 | 259.3167 | 259.3167 | 2.499% | 2.996% | 20 | 1 | 1 | 1 | 1
2013-02-17 | 21 | 31758.3252 | 7928.8113 | 8854.9324 | 926.1211 | 8777.8 | 77.1324 | 77.1324 | 0.7432% | 0.8711% | 8993.3 | 138.3676 | -138.3676 | 1.333% | 1.563% | 21 | 1 | 1 | 0 | 1
2013-02-17 | 22 | 30780.4405 | 7877.6064 | 8821.7247 | 944.1183 | 8885.1 | 63.3753 | -63.3753 | 0.6106% | 0.7184% | 9108 | 286.2753 | -286.2753 | 2.758% | 3.245% | 22 | 0 | 1 | 0 | 0
2013-02-17 | 23 | 29067.6502 | 7839.8171 | 8781.6405 | 941.8234 | 8861.1 | 79.4595 | -79.4595 | 0.7656% | 0.9048% | 9088.4 | 306.7595 | -306.7595 | 2.956% | 3.493% | 23 | 0 | 1 | 0 | 0
2013-02-17 | 24 | 27044.6443 | 7566.434 | 8789.1393 | 1222.7052 | 8812.8 | 23.6607 | -23.6607 | 0.228% | 0.2692% | 9047.3 | 258.1607 | -258.1607 | 2.487% | 2.937% | 24 | 0 | 1 | 0 | 0
2013-02-18 | 1 | 25594.286 | 7115.3729 | 8689.7058 | 1574.3329 | 8671.4 | 18.3058 | 18.3058 | 0.1764% | 0.2107% | 8834.2 | 144.4942 | -144.4942 | 1.392% | 1.663% | 1 | 1 | 0 | 0 | 1
2013-02-18 | 2 | 24798.7281 | 6973.4784 | 8441.3586 | 1467.8802 | 8481 | 39.6414 | -39.6414 | 0.382% | 0.4696% | 8672.1 | 230.7414 | -230.7414 | 2.223% | 2.733% | 2 | 0 | 0 | 0 | 0
2013-02-18 | 3 | 24368.9297 | 6750.6862 | 8267.4805 | 1516.7943 | 8361.9 | 94.4195 | -94.4195 | 0.9098% | 1.142% | 8536.7 | 269.2195 | -269.2195 | 2.594% | 3.256% | 3 | 0 | 0 | 0 | 0
2013-02-18 | 4 | 24379.3003 | 6680.445 | 8145.3806 | 1464.9356 | 8307.6 | 162.2194 | -162.2194 | 1.563% | 1.992% | 8480.3 | 334.9194 | -334.9194 | 3.227% | 4.112% | 4 | 0 | 0 | 0 | 0
2013-02-18 | 5 | 24927.7841 | 6893.5875 | 7847.7628 | 954.1753 | 8186.3 | 338.5372 | -338.5372 | 3.262% | 4.314% | 8357.8 | 510.0372 | -510.0372 | 4.914% | 6.499% | 5 | 0 | 0 | 0 | 0
2013-02-18 | 6 | 26829.7103 | 7094.0645 | 7521.1303 | 427.0658 | 7880.2 | 359.0697 | -359.0697 | 3.46% | 4.774% | 8056.7 | 535.5697 | -535.5697 | 5.16% | 7.121% | 6 | 0 | 0 | 0 | 0
2013-02-18 | 7 | 29899.2023 | 7200.363 | 7310.8371 | 110.4742 | 7512.5 | 201.6629 | -201.6629 | 1.943% | 2.758% | 7684.7 | 373.8629 | -373.8629 | 3.602% | 5.114% | 7 | 0 | 0 | 0 | 0
2013-02-18 | 8 | 31004.9298 | 6699.0735 | 6770.2892 | 71.2157 | 7085.3 | 315.0108 | -315.0108 | 3.035% | 4.653% | 7262.5 | 492.2108 | -492.2108 | 4.743% | 7.27% | 8 | 0 | 0 | 0 | 0
2013-02-18 | 9 | 31205.7907 | 5881.0016 | 5905.0886 | 24.087 | 6461.3 | 556.2114 | -556.2114 | 5.359% | 9.419% | 6642.8 | 737.7114 | -737.7114 | 7.108% | 12.49% | 9 | 0 | 0 | 0 | 0
2013-02-18 | 10 | 31821.2031 | 5949.3125 | 5959.9638 | 10.6512 | 5893.1 | 66.8638 | 66.8638 | 0.6443% | 1.122% | 6019.4 | 59.4362 | -59.4362 | 0.5727% | 0.9973% | 10 | 1 | 0 | 0 | 1
2013-02-18 | 11 | 32588.4224 | 7331.9526 | 7490.6021 | 158.6495 | 5435.2 | 2055.4021 | 2055.4021 | 19.8% | 27.44% | 5508.2 | 1982.4021 | 1982.4021 | 19.1% | 26.47% | 11 | 1 | 0 | 1 | 1
2013-02-18 | 12 | 32783.4435 | 7170.43 | 7177.4566 | 7.0266 | 5048.4 | 2129.0566 | 2129.0566 | 20.51% | 29.66% | 5136.9 | 2040.5566 | 2040.5566 | 19.66% | 28.43% | 12 | 1 | 0 | 1 | 1
2013-02-18 | 13 | 32790.1194 | 6833.5769 | 6835.884 | 2.3071 | 4550 | 2285.884 | 2285.884 | 22.03% | 33.44% | 4664.2 | 2171.684 | 2171.684 | 20.92% | 31.77% | 13 | 1 | 0 | 1 | 1
2013-02-18 | 14 | 32957.6843 | 6393.9472 | 6396.1312 | 2.184 | 4536.5 | 1859.6312 | 1859.6312 | 17.92% | 29.07% | 4623.3 | 1772.8312 | 1772.8312 | 17.08% | 27.72% | 14 | 1 | 0 | 1 | 1
2013-02-18 | 15 | 32885.1656 | 6264.7856 | 6267.6222 | 2.8366 | 4567.6 | 1700.0222 | 1700.0222 | 16.38% | 27.12% | 4625.4 | 1642.2222 | 1642.2222 | 15.82% | 26.2% | 15 | 1 | 0 | 1 | 1
2013-02-18 | 16 | 32735.3588 | 5809.1299 | 5813.2331 | 4.1032 | 4290.5 | 1522.7331 | 1522.7331 | 14.67% | 26.19% | 4342.1 | 1471.1331 | 1471.1331 | 14.17% | 25.31% | 16 | 1 | 0 | 1 | 1
2013-02-18 | 17 | 32713.114 | 5325.4419 | 5331.9867 | 6.5448 | 3840.6 | 1491.3867 | 1491.3867 | 14.37% | 27.97% | 3892.6 | 1439.3867 | 1439.3867 | 13.87% | 27% | 17 | 1 | 0 | 1 | 1
2013-02-18 | 18 | 32702.1604 | 4498.7355 | 4504.1721 | 5.4365 | 3259.8 | 1244.3721 | 1244.3721 | 11.99% | 27.63% | 3305.4 | 1198.7721 | 1198.7721 | 11.55% | 26.61% | 18 | 1 | 0 | 1 | 1
2013-02-18 | 19 | 34080.938 | 3453.4091 | 3457.8739 | 4.4648 | 3139.8 | 318.0739 | 318.0739 | 3.065% | 9.199% | 3149.9 | 307.9739 | 307.9739 | 2.967% | 8.906% | 19 | 1 | 0 | 1 | 1
2013-02-18 | 20 | 34902.3306 | 3708.352 | 3704.8486 | -3.5034 | 3310 | 394.8486 | 394.8486 | 3.804% | 10.66% | 3304.6 | 400.2486 | 400.2486 | 3.857% | 10.8% | 20 | 1 | 0 | 1 | 1
2013-02-18 | 21 | 34095.7725 | 4209.8467 | 4211.972 | 2.1253 | 3335 | 876.972 | 876.972 | 8.45% | 20.82% | 3380.9 | 831.072 | 831.072 | 8.008% | 19.73% | 21 | 1 | 0 | 1 | 1
2013-02-18 | 22 | 32626.8551 | 3817.7359 | 3819.934 | 2.1981 | 3387.4 | 432.534 | 432.534 | 4.168% | 11.32% | 3441.1 | 378.834 | 378.834 | 3.65% | 9.917% | 22 | 1 | 0 | 1 | 1
2013-02-18 | 23 | 30044.2953 | 3562.6678 | 3577.7466 | 15.0788 | 3432.1 | 145.6466 | 145.6466 | 1.403% | 4.071% | 3477.6 | 100.1466 | 100.1466 | 0.9649% | 2.799% | 23 | 1 | 0 | 1 | 1
2013-02-18 | 24 | 27488.1479 | 3430.9532 | 3444.7385 | 13.7853 | 3552.7 | 107.9615 | -107.9615 | 1.04% | 3.134% | 3578.5 | 133.7615 | -133.7615 | 1.289% | 3.883% | 24 | 0 | 0 | 0 | 0
2013-02-19 | 1 | 25861.7462 | 3449.2382 | 3473.7049 | 24.4667 | 3905.3 | 431.5951 | -431.5951 | 4.159% | 12.42% | 3996 | 522.2951 | -522.2951 | 5.032% | 15.04% | 1 | 0 | 0 | 0 | 0
2013-02-19 | 2 | 25186.199 | 3262.5396 | 3274.5007 | 11.9611 | 3893.3 | 618.7993 | -618.7993 | 5.962% | 18.9% | 3986.1 | 711.5993 | -711.5993 | 6.856% | 21.73% | 2 | 0 | 0 | 0 | 0
2013-02-19 | 3 | 25002.1626 | 3208.1936 | 3214.8353 | 6.6417 | 4178.3 | 963.4647 | -963.4647 | 9.283% | 29.97% | 4224.5 | 1009.6647 | -1009.6647 | 9.728% | 31.41% | 3 | 0 | 0 | 0 | 0
2013-02-19 | 4 | 25325.1075 | 2827.0254 | 2843.3802 | 16.3548 | 4358 | 1514.6198 | -1514.6198 | 14.59% | 53.27% | 4441.2 | 1597.8198 | -1597.8198 | 15.4% | 56.19% | 4 | 0 | 0 | 0 | 0
2013-02-19 | 5 | 26403.545 | 2198.7018 | 2228.7818 | 30.0801 | 4525.5 | 2296.7182 | -2296.7182 | 22.13% | 103% | 4663.5 | 2434.7182 | -2434.7182 | 23.46% | 109.2% | 5 | 0 | 0 | 0 | 0
2013-02-19 | 6 | 29295.9879 | 2448.4099 | 2449.4288 | 1.019 | 4642.4 | 2192.9712 | -2192.9712 | 21.13% | 89.53% | 4815.6 | 2366.1712 | -2366.1712 | 22.8% | 96.6% | 6 | 0 | 0 | 0 | 0
2013-02-19 | 7 | 34106.3113 | 2817.3762 | 2813.3738 | -4.0024 | 4685.5 | 1872.1262 | -1872.1262 | 18.04% | 66.54% | 4904.6 | 2091.2262 | -2091.2262 | 20.15% | 74.33% | 7 | 0 | 1 | 0 | 0
2013-02-19 | 8 | 35396.8493 | 3437.8219 | 3428.5304 | -9.2915 | 4877.4 | 1448.8696 | -1448.8696 | 13.96% | 42.26% | 5120.4 | 1691.8696 | -1691.8696 | 16.3% | 49.35% | 8 | 0 | 1 | 0 | 0
2013-02-19 | 9 | 34385.5759 | 3809.4664 | 3858.499 | 49.0327 | 4400.6 | 542.101 | -542.101 | 5.223% | 14.05% | 4616.4 | 757.901 | -757.901 | 7.303% | 19.64% | 9 | 0 | 1 | 0 | 0
2013-02-19 | 10 | 33711.9914 | 4403.2955 | 4501.6726 | 98.377 | 4189.1 | 312.5726 | 312.5726 | 3.012% | 6.943% | 4344 | 157.6726 | 157.6726 | 1.519% | 3.503% | 10 | 1 | 0 | 1 | 1
2013-02-19 | 11 | 33302.0397 | 4368.5004 | 4425.6308 | 57.1304 | 4358 | 67.6308 | 67.6308 | 0.6516% | 1.528% | 4464.4 | 38.7692 | -38.7692 | 0.3736% | 0.876% | 11 | 1 | 0 | 0 | 1
2013-02-19 | 12 | 32769.8065 | 4319.5523 | 4332.0768 | 12.5244 | 4501.1 | 169.0232 | -169.0232 | 1.629% | 3.902% | 4574 | 241.9232 | -241.9232 | 2.331% | 5.584% | 12 | 0 | 0 | 0 | 0
2013-02-19 | 13 | 32336.2006 | 4551.3666 | 4548.7785 | -2.5881 | 4627.9 | 79.1215 | -79.1215 | 0.7624% | 1.739% | 4684.6 | 135.8215 | -135.8215 | 1.309% | 2.986% | 13 | 0 | 0 | 0 | 0
2013-02-19 | 14 | 32092.776 | 5195.9658 | 5223.1337 | 27.1679 | 4817 | 406.1337 | 406.1337 | 3.913% | 7.776% | 4888.1 | 335.0337 | 335.0337 | 3.228% | 6.414% | 14 | 1 | 0 | 1 | 1
2013-02-19 | 15 | 31851.3386 | 6017.5089 | 6052.3471 | 34.8382 | 5313.7 | 738.6471 | 738.6471 | 7.117% | 12.2% | 5385.5 | 666.8471 | 666.8471 | 6.425% | 11.02% | 15 | 1 | 0 | 1 | 1
2013-02-19 | 16 | 31668.0608 | 6401.5728 | 6481.7917 | 80.219 | 5738.8 | 742.9917 | 742.9917 | 7.159% | 11.46% | 5825.4 | 656.3917 | 656.3917 | 6.325% | 10.13% | 16 | 1 | 0 | 1 | 1
2013-02-19 | 17 | 31699.3689 | 6601.6208 | 6711.3512 | 109.7304 | 5970.9 | 740.4512 | 740.4512 | 7.134% | 11.03% | 6050.5 | 660.8512 | 660.8512 | 6.367% | 9.847% | 17 | 1 | 0 | 1 | 1
2013-02-19 | 18 | 32141.1763 | 6290.2647 | 6353.0575 | 62.7928 | 5974.2 | 378.8575 | 378.8575 | 3.65% | 5.963% | 6071.8 | 281.2575 | 281.2575 | 2.71% | 4.427% | 18 | 1 | 0 | 1 | 1
2013-02-19 | 19 | 34338.7496 | 5652.1064 | 5693.4923 | 41.3859 | 6186.3 | 492.8077 | -492.8077 | 4.748% | 8.656% | 6283.3 | 589.8077 | -589.8077 | 5.683% | 10.36% | 19 | 0 | 0 | 0 | 0
2013-02-19 | 20 | 35110.6184 | 5243.3575 | 5269.4588 | 26.1014 | 6972.1 | 1702.6412 | -1702.6412 | 16.41% | 32.31% | 7100.6 | 1831.1412 | -1831.1412 | 17.64% | 34.75% | 20 | 0 | 0 | 0 | 0
2013-02-19 | 21 | 34599.7983 | 4721.4592 | 4761.4502 | 39.991 | 7636.6 | 2875.1498 | -2875.1498 | 27.7% | 60.38% | 7787.2 | 3025.7498 | -3025.7498 | 29.15% | 63.55% | 21 | 0 | 0 | 0 | 0
2013-02-19 | 22 | 33120.9712 | 3913.3323 | 3910.3516 | -2.9807 | 7763.3 | 3852.9484 | -3852.9484 | 37.12% | 98.53% | 7920.5 | 4010.1484 | -4010.1484 | 38.64% | 102.6% | 22 | 0 | 0 | 0 | 0
2013-02-19 | 23 | 30687.1983 | 3800.8269 | 3828.025 | 27.1981 | 7657.3 | 3829.275 | -3829.275 | 36.9% | 100% | 7822.4 | 3994.375 | -3994.375 | 38.49% | 104.3% | 23 | 0 | 0 | 0 | 0
2013-02-19 | 24 | 28325.0079 | 3573.3304 | 3599.9286 | 26.5982 | 7725.6 | 4125.6714 | -4125.6714 | 39.75% | 114.6% | 7893.8 | 4293.8714 | -4293.8714 | 41.37% | 119.3% | 24 | 0 | 0 | 0 | 0
2013-02-20 | 1 | 26717.1896 | 3714.0795 | 3723.1465 | 9.0671 | 6090.3 | 2367.1535 | -2367.1535 | 22.81% | 63.58% | 6197.8 | 2474.6535 | -2474.6535 | 23.84% | 66.47% | 1 | 0 | 0 | 0 | 0
2013-02-20 | 2 | 25973.9311 | 4222.3767 | 4221.6748 | -0.70187 | 6035.4 | 1813.7252 | -1813.7252 | 17.48% | 42.96% | 6150.3 | 1928.6252 | -1928.6252 | 18.58% | 45.68% | 2 | 0 | 0 | 0 | 0
2013-02-20 | 3 | 25816.0121 | 3667.1809 | 3646.6247 | -20.5563 | 5907.1 | 2260.4753 | -2260.4753 | 21.78% | 61.99% | 5994.1 | 2347.4753 | -2347.4753 | 22.62% | 64.37% | 3 | 0 | 0 | 0 | 0
2013-02-20 | 4 | 25973.5318 | 2374.5748 | 2400.3887 | 25.814 | 5394.3 | 2993.9113 | -2993.9113 | 28.85% | 124.7% | 5588.2 | 3187.8113 | -3187.8113 | 30.72% | 132.8% | 4 | 0 | 0 | 0 | 0
2013-02-20 | 5 | 26807.8435 | 3041.4423 | 3141.8009 | 100.3587 | 5767.7 | 2625.8991 | -2625.8991 | 25.3% | 83.58% | 6048.8 | 2906.9991 | -2906.9991 | 28.01% | 92.53% | 5 | 0 | 1 | 0 | 0
2013-02-20 | 6 | 29534.7975 | 3894.0937 | 3996.7522 | 102.6585 | 5854.8 | 1858.0478 | -1858.0478 | 17.9% | 46.49% | 6130.1 | 2133.3478 | -2133.3478 | 20.56% | 53.38% | 6 | 0 | 1 | 0 | 0
2013-02-20 | 7 | 33907.6443 | 4213.6493 | 4303.9579 | 90.3086 | 6293.4 | 1989.4421 | -1989.4421 | 19.17% | 46.22% | 6546.7 | 2242.7421 | -2242.7421 | 21.61% | 52.11% | 7 | 0 | 1 | 0 | 0
2013-02-20 | 8 | 35281.5515 | 4502.2955 | 4577.2642 | 74.9687 | 6480.5 | 1903.2358 | -1903.2358 | 18.34% | 41.58% | 6671.5 | 2094.2358 | -2094.2358 | 20.18% | 45.75% | 8 | 0 | 0 | 0 | 0
2013-02-20 | 9 | 35008.3751 | 4741.9265 | 4887.3293 | 145.4029 | 6387.1 | 1499.7707 | -1499.7707 | 14.45% | 30.69% | 6673.1 | 1785.7707 | -1785.7707 | 17.21% | 36.54% | 9 | 0 | 1 | 0 | 0
2013-02-20 | 10 | 35154.0403 | 4967.7603 | 5106.3904 | 138.6301 | 6276.3 | 1169.9096 | -1169.9096 | 11.27% | 22.91% | 6559.5 | 1453.1096 | -1453.1096 | 14% | 28.46% | 10 | 0 | 1 | 0 | 0
2013-02-20 | 11 | 35417.157 | 5243.1127 | 5397.0226 | 153.9099 | 6184.4 | 787.3774 | -787.3774 | 7.587% | 14.59% | 6460.5 | 1063.4774 | -1063.4774 | 10.25% | 19.7% | 11 | 0 | 1 | 0 | 0
2013-02-20 | 12 | 35534.6348 | 5595.7755 | 5650.7264 | 54.9509 | 6061.2 | 410.4736 | -410.4736 | 3.955% | 7.264% | 6335.8 | 685.0736 | -685.0736 | 6.601% | 12.12% | 12 | 0 | 1 | 0 | 0
2013-02-20 | 13 | 35539.5403 | 5180.0931 | 5299.5041 | 119.411 | 5836.1 | 536.5959 | -536.5959 | 5.17% | 10.13% | 6120.6 | 821.0959 | -821.0959 | 7.912% | 15.49% | 13 | 0 | 1 | 0 | 0
2013-02-20 | 14 | 35488.2697 | 5154.4167 | 5288.4173 | 134.0007 | 5624.2 | 335.7827 | -335.7827 | 3.235% | 6.349% | 5903.3 | 614.8827 | -614.8827 | 5.925% | 11.63% | 14 | 0 | 1 | 0 | 0
2013-02-20 | 15 | 35182.9421 | 5345.2594 | 5472.5192 | 127.2599 | 5514.9 | 42.3808 | -42.3808 | 0.4084% | 0.7744% | 5802.1 | 329.5808 | -329.5808 | 3.176% | 6.022% | 15 | 0 | 1 | 0 | 0
2013-02-20 | 16 | 35380.9284 | 5420.2328 | 5570.222 | 149.9893 | 5623.1 | 52.878 | -52.878 | 0.5095% | 0.9493% | 5895.8 | 325.578 | -325.578 | 3.137% | 5.845% | 16 | 0 | 1 | 0 | 0
2013-02-20 | 17 | 36019.0629 | 5553.4923 | 5718.5769 | 165.0845 | 5896.6 | 178.0231 | -178.0231 | 1.715% | 3.113% | 6154.3 | 435.7231 | -435.7231 | 4.198% | 7.619% | 17 | 0 | 1 | 0 | 0
2013-02-20 | 18 | 37088.6148 | 6040.1539 | 6252.5788 | 212.4249 | 5972.5 | 280.0788 | 280.0788 | 2.699% | 4.479% | 6238.6 | 13.9788 | 13.9788 | 0.1347% | 0.2236% | 18 | 1 | 1 | 1 | 1
2013-02-20 | 19 | 38709.4232 | 6703.7556 | 6878.8159 | 175.0603 | 6433.4 | 445.4159 | 445.4159 | 4.292% | 6.475% | 6689.3 | 189.5159 | 189.5159 | 1.826% | 2.755% | 19 | 1 | 1 | 1 | 1
2013-02-20 | 20 | 38924.051 | 7302.5007 | 7487.1595 | 184.6588 | 7081.1 | 406.0595 | 406.0595 | 3.913% | 5.423% | 7321.2 | 165.9595 | 165.9595 | 1.599% | 2.217% | 20 | 1 | 1 | 1 | 1
2013-02-20 | 21 | 38172.5693 | 7427.0938 | 7611.1501 | 184.0563 | 7410.8 | 200.3501 | 200.3501 | 1.93% | 2.632% | 7710.5 | 99.3499 | -99.3499 | 0.9573% | 1.305% | 21 | 1 | 1 | 0 | 1
2013-02-20 | 22 | 36577.3348 | 7333.8789 | 7482.5307 | 148.6518 | 6996.7 | 485.8307 | 485.8307 | 4.681% | 6.493% | 7471 | 11.5307 | 11.5307 | 0.1111% | 0.1541% | 22 | 1 | 1 | 1 | 1
2013-02-20 | 23 | 33767.8204 | 7000.0313 | 7096.4499 | 96.4185 | 6837.6 | 258.8499 | 258.8499 | 2.494% | 3.648% | 7142.2 | 45.7501 | -45.7501 | 0.4408% | 0.6447% | 23 | 1 | 1 | 0 | 1
2013-02-20 | 24 | 31092.9661 | 5848.9884 | 6002.1847 | 153.1964 | 7115.3 | 1113.1153 | -1113.1153 | 10.73% | 18.55% | 7401.4 | 1399.2153 | -1399.2153 | 13.48% | 23.31% | 24 | 0 | 1 | 0 | 0
2013-02-21 | 1 | 29313.1466 | 5352.4172 | 5406.359 | 53.9418 | 7171.5 | 1765.141 | -1765.141 | 17.01% | 32.65% | 7484.9 | 2078.541 | -2078.541 | 20.03% | 38.45% | 1 | 0 | 1 | 0 | 0
2013-02-21 | 2 | 28339.8329 | 4329.5872 | 4491.3533 | 161.7661 | 7032.2 | 2540.8467 | -2540.8467 | 24.48% | 56.57% | 7313 | 2821.6467 | -2821.6467 | 27.19% | 62.82% | 2 | 0 | 1 | 0 | 0
2013-02-21 | 3 | 27689.9018 | 4439.5693 | 4533.5548 | 93.9855 | 6769.6 | 2236.0452 | -2236.0452 | 21.54% | 49.32% | 7081.4 | 2547.8452 | -2547.8452 | 24.55% | 56.2% | 3 | 0 | 1 | 0 | 0
2013-02-21 | 4 | 27664.144 | 5205.6182 | 5272.3711 | 66.753 | 6975.7 | 1703.3289 | -1703.3289 | 16.41% | 32.31% | 7255.7 | 1983.3289 | -1983.3289 | 19.11% | 37.62% | 4 | 0 | 1 | 0 | 0
2013-02-21 | 5 | 28306.0981 | 4149.5597 | 4235.0528 | 85.4931 | 7133 | 2897.9472 | -2897.9472 | 27.92% | 68.43% | 7365 | 3129.9472 | -3129.9472 | 30.16% | 73.91% | 5 | 0 | 1 | 0 | 0
2013-02-21 | 6 | 30619.6675 | 3252.6393 | 3352.565 | 99.9257 | 7404.8 | 4052.235 | -4052.235 | 39.04% | 120.9% | 7575 | 4222.435 | -4222.435 | 40.68% | 125.9% | 6 | 0 | 0 | 0 | 0
2013-02-21 | 7 | 34428.0421 | 3506.8324 | 3499.997 | -6.8354 | 7708.5 | 4208.503 | -4208.503 | 40.55% | 120.2% | 7879 | 4379.003 | -4379.003 | 42.19% | 125.1% | 7 | 0 | 0 | 0 | 0
2013-02-21 | 8 | 35483.7664 | 4849.9013 | 4861.6068 | 11.7055 | 7716.1 | 2854.4932 | -2854.4932 | 27.5% | 58.72% | 7901 | 3039.3932 | -3039.3932 | 29.29% | 62.52% | 8 | 0 | 0 | 0 | 0
2013-02-21 | 9 | 35003.0821 | 5739.7254 | 5806.7324 | 67.0071 | 7962 | 2155.2676 | -2155.2676 | 20.77% | 37.12% | 8110.7 | 2303.9676 | -2303.9676 | 22.2% | 39.68% | 9 | 0 | 0 | 0 | 0
2013-02-21 | 10 | 34972.8318 | 6706.8642 | 6778.0956 | 71.2314 | 7703.1 | 925.0044 | -925.0044 | 8.913% | 13.65% | 7829.5 | 1051.4044 | -1051.4044 | 10.13% | 15.51% | 10 | 0 | 0 | 0 | 0
2013-02-21 | 11 | 34849.8463 | 7722.1449 | 7857.0813 | 134.9364 | 7456.8 | 400.2813 | 400.2813 | 3.857% | 5.095% | 7525 | 332.0813 | 332.0813 | 3.2% | 4.227% | 11 | 1 | 0 | 1 | 1
2013-02-21 | 12 | 34473.3919 | 7812.8726 | 7910.9499 | 98.0773 | 7440.4 | 470.5499 | 470.5499 | 4.534% | 5.948% | 7469.1 | 441.8499 | 441.8499 | 4.257% | 5.585% | 12 | 1 | 0 | 1 | 1
2013-02-21 | 13 | 34098.0858 | 7439.2273 | 7548.17 | 108.9427 | 7459.1 | 89.07 | 89.07 | 0.8582% | 1.18% | 7474.6 | 73.57 | 73.57 | 0.7089% | 0.9747% | 13 | 1 | 0 | 1 | 1
2013-02-21 | 14 | 33768.6099 | 7189.0092 | 7382.5554 | 193.5462 | 7554.4 | 171.8446 | -171.8446 | 1.656% | 2.328% | 7591.3 | 208.7446 | -208.7446 | 2.011% | 2.828% | 14 | 0 | 0 | 0 | 0
2013-02-21 | 15 | 33357.2466 | 6916.9457 | 7099.2089 | 182.2631 | 7593.3 | 494.0911 | -494.0911 | 4.761% | 6.96% | 7645.3 | 546.0911 | -546.0911 | 5.262% | 7.692% | 15 | 0 | 0 | 0 | 0
2013-02-21 | 16 | 33070.9764 | 6696.6051 | 6871.3338 | 174.7287 | 7456.8 | 585.4662 | -585.4662 | 5.641% | 8.52% | 7512.2 | 640.8662 | -640.8662 | 6.175% | 9.327% | 16 | 0 | 0 | 0 | 0
2013-02-21 | 17 | 32833.7887 | 5838.8036 | 5999.9092 | 161.1056 | 7102.8 | 1102.8908 | -1102.8908 | 10.63% | 18.38% | 7146.9 | 1146.9908 | -1146.9908 | 11.05% | 19.12% | 17 | 0 | 0 | 0 | 0
2013-02-21 | 18 | 32550.4254 | 3647.1693 | 3700.071 | 52.9017 | 6083.8 | 2383.729 | -2383.729 | 22.97% | 64.42% | 6129.8 | 2429.729 | -2429.729 | 23.41% | 65.67% | 18 | 0 | 0 | 0 | 0
2013-02-21 | 19 | 33855.9947 | 1755.4905 | 1817.4309 | 61.9404 | 5633.4 | 3815.9691 | -3815.9691 | 36.77% | 210% | 5741 | 3923.5691 | -3923.5691 | 37.8% | 215.9% | 19 | 0 | 0 | 0 | 0
2013-02-21 | 20 | 34745.0563 | 1677.575 | 1742.5795 | 65.0045 | 5661.1 | 3918.5205 | -3918.5205 | 37.76% | 224.9% | 5781.2 | 4038.6205 | -4038.6205 | 38.91% | 231.8% | 20 | 0 | 0 | 0 | 0
2013-02-21 | 21 | 34259.0677 | 2338.1859 | 2395.4604 | 57.2745 | 5768.4 | 3372.9396 | -3372.9396 | 32.5% | 140.8% | 5914.7 | 3519.2396 | -3519.2396 | 33.91% | 146.9% | 21 | 0 | 0 | 0 | 0
2013-02-21 | 22 | 33065.0297 | 2889.7131 | 2911.3235 | 21.6104 | 5451.9 | 2540.5765 | -2540.5765 | 24.48% | 87.27% | 5623 | 2711.6765 | -2711.6765 | 26.13% | 93.14% | 22 | 0 | 0 | 0 | 0
2013-02-21 | 23 | 30783.0845 | 3419.1717 | 3463.6266 | 44.4548 | 5111.2 | 1647.5734 | -1647.5734 | 15.87% | 47.57% | 5312.7 | 1849.0734 | -1849.0734 | 17.82% | 53.39% | 23 | 0 | 0 | 0 | 0
2013-02-21 | 24 | 28630.9963 | 3845.9419 | 3898.7543 | 52.8124 | 4918.9 | 1020.1457 | -1020.1457 | 9.829% | 26.17% | 5101.8 | 1203.0457 | -1203.0457 | 11.59% | 30.86% | 24 | 0 | 0 | 0 | 0
2013-02-22 | 1 | 27272.3334 | 4245.2275 | 4306.5147 | 61.2872 | 3111.6 | 1194.9147 | 1194.9147 | 11.51% | 27.75% | 3269.5 | 1037.0147 | 1037.0147 | 9.992% | 24.08% | 1 | 1 | 0 | 1 | 1
2013-02-22 | 2 | 26729.5037 | 3868.8033 | 3906.0598 | 37.2565 | 2921.3 | 984.7598 | 984.7598 | 9.488% | 25.21% | 3073 | 833.0598 | 833.0598 | 8.027% | 21.33% | 2 | 1 | 0 | 1 | 1
2013-02-22 | 3 | 26739.4942 | 3813.3264 | 3843.6227 | 30.2962 | 2652 | 1191.6227 | 1191.6227 | 11.48% | 31% | 2763.8 | 1079.8227 | 1079.8227 | 10.4% | 28.09% | 3 | 1 | 0 | 1 | 1
2013-02-22 | 4 | 27252.2229 | 3419.5312 | 3419.115 | -0.41622 | 2419.8 | 999.315 | 999.315 | 9.629% | 29.23% | 2537.6 | 881.515 | 881.515 | 8.494% | 25.78% | 4 | 1 | 0 | 1 | 1
2013-02-22 | 5 | 28430.2245 | 2350.7944 | 2330.6783 | -20.1162 | 2303 | 27.6783 | 27.6783 | 0.2667% | 1.188% | 2360 | 29.3217 | -29.3217 | 0.2825% | 1.258% | 5 | 1 | 0 | 0 | 1
2013-02-22 | 6 | 31343.0455 | 2248.0332 | 2206.8431 | -41.1901 | 1991.1 | 215.7431 | 215.7431 | 2.079% | 9.776% | 2048.3 | 158.5431 | 158.5431 | 1.528% | 7.184% | 6 | 1 | 0 | 1 | 1
2013-02-22 | 7 | 36118.3548 | 2170.7351 | 2127.7741 | -42.961 | 1754 | 373.7741 | 373.7741 | 3.601% | 17.57% | 1813.5 | 314.2741 | 314.2741 | 3.028% | 14.77% | 7 | 1 | 0 | 1 | 1
2013-02-22 | 8 | 37649.0975 | 2308.4564 | 2278.4762 | -29.9802 | 1451.4 | 827.0762 | 827.0762 | 7.969% | 36.3% | 1541.5 | 736.9762 | 736.9762 | 7.101% | 32.35% | 8 | 1 | 0 | 1 | 1
2013-02-22 | 9 | 37238.016 | 2226.9347 | 2215.8604 | -11.0743 | 1132.6 | 1083.2604 | 1083.2604 | 10.44% | 48.89% | 1190.3 | 1025.5604 | 1025.5604 | 9.882% | 46.28% | 9 | 1 | 0 | 1 | 1
2013-02-22 | 10 | 37084.511 | 1869.5665 | 1852.1589 | -17.4076 | 954.2 | 897.9589 | 897.9589 | 8.652% | 48.48% | 1013.9 | 838.2589 | 838.2589 | 8.077% | 45.26% | 10 | 1 | 0 | 1 | 1
2013-02-22 | 11 | 36749.1432 | 1477.5713 | 1507.0762 | 29.5049 | 917 | 590.0762 | 590.0762 | 5.686% | 39.15% | 994.4 | 512.6762 | 512.6762 | 4.94% | 34.02% | 11 | 1 | 0 | 1 | 1
2013-02-22 | 12 | 36042.9641 | 1151.1204 | 1180.9578 | 29.8374 | 895.7 | 285.2578 | 285.2578 | 2.749% | 24.15% | 972.2 | 208.7578 | 208.7578 | 2.011% | 17.68% | 12 | 1 | 0 | 1 | 1
2013-02-22 | 13 | 35110.1887 | 1006.0906 | 1034.5628 | 28.4722 | 896.4 | 138.1628 | 138.1628 | 1.331% | 13.35% | 977.7 | 56.8628 | 56.8628 | 0.5479% | 5.496% | 13 | 1 | 0 | 1 | 1
2013-02-22 | 14 | 34359.8095 | 817.3599 | 836.7063 | 19.3464 | 939.5 | 102.7937 | -102.7937 | 0.9904% | 12.29% | 1029.5 | 192.7937 | -192.7937 | 1.858% | 23.04% | 14 | 0 | 0 | 0 | 0
2013-02-22 | 15 | 33452.018 | 833.9833 | 858.6122 | 24.629 | 1016.2 | 157.5878 | -157.5878 | 1.518% | 18.35% | 1091.3 | 232.6878 | -232.6878 | 2.242% | 27.1% | 15 | 0 | 0 | 0 | 0
2013-02-22 | 16 | 32713.6392 | 970.5694 | 990.4935 | 19.9241 | 1119.3 | 128.8065 | -128.8065 | 1.241% | 13% | 1186.4 | 195.9065 | -195.9065 | 1.888% | 19.78% | 16 | 0 | 0 | 0 | 0
2013-02-22 | 17 | 32477.221 | 932.3823 | 945.2113 | 12.829 | 1241.2 | 295.9887 | -295.9887 | 2.852% | 31.31% | 1310.3 | 365.0887 | -365.0887 | 3.518% | 38.63% | 17 | 0 | 0 | 0 | 0
2013-02-22 | 18 | 32867.2536 | 921.9034 | 931.2683 | 9.365 | 1450.1 | 518.8317 | -518.8317 | 4.999% | 55.71% | 1534 | 602.7317 | -602.7317 | 5.807% | 64.72% | 18 | 0 | 0 | 0 | 0
2013-02-22 | 19 | 34634.5192 | 997.231 | 1000.7552 | 3.5242 | 2091.8 | 1091.0448 | -1091.0448 | 10.51% | 109% | 2174.6 | 1173.8448 | -1173.8448 | 11.31% | 117.3% | 19 | 0 | 0 | 0 | 0
2013-02-22 | 20 | 35548.1973 | 1707.6022 | 1718.3454 | 10.7431 | 2441.5 | 723.1546 | -723.1546 | 6.968% | 42.08% | 2537 | 818.6546 | -818.6546 | 7.888% | 47.64% | 20 | 0 | 0 | 0 | 0
2013-02-22 | 21 | 35203.7563 | 2340.0551 | 2361.5021 | 21.447 | 2640.1 | 278.5979 | -278.5979 | 2.684% | 11.8% | 2785.1 | 423.5979 | -423.5979 | 4.081% | 17.94% | 21 | 0 | 0 | 0 | 0
2013-02-22 | 22 | 34542.1302 | 2838.4886 | 2862.7983 | 24.3097 | 2869.6 | 6.8017 | -6.8017 | 0.06554% | 0.2376% | 3025.5 | 162.7017 | -162.7017 | 1.568% | 5.683% | 22 | 0 | 0 | 0 | 0
2013-02-22 | 23 | 33154.837 | 2787.1425 | 2810.618 | 23.4755 | 3116.2 | 305.582 | -305.582 | 2.944% | 10.87% | 3257.4 | 446.782 | -446.782 | 4.305% | 15.9% | 23 | 0 | 0 | 0 | 0
2013-02-22 | 24 | 31497.387 | 2584.8286 | 2598.3709 | 13.5423 | 3394.3 | 795.9291 | -795.9291 | 7.669% | 30.63% | 3506.7 | 908.3291 | -908.3291 | 8.752% | 34.96% | 24 | 0 | 0 | 0 | 0
2013-02-23 | 1 | 30263.5955 | 2316.6869 | 2341.1609 | 24.4739 | 2393.1 | 51.9391 | -51.9391 | 0.5004% | 2.219% | 2541 | 199.8391 | -199.8391 | 1.926% | 8.536% | 1 | 0 | 0 | 0 | 0
2013-02-23 | 2 | 29603.721 | 2151.3778 | 2172.711 | 21.3333 | 2391.9 | 219.189 | -219.189 | 2.112% | 10.09% | 2557.1 | 384.389 | -384.389 | 3.704% | 17.69% | 2 | 0 | 0 | 0 | 0
2013-02-23 | 3 | 29433.2799 | 1779.1756 | 1801.7943 | 22.6187 | 2455.6 | 653.8057 | -653.8057 | 6.3% | 36.29% | 2578.6 | 776.8057 | -776.8057 | 7.485% | 43.11% | 3 | 0 | 0 | 0 | 0
2013-02-23 | 4 | 29591.0257 | 1772.4258 | 1789.4698 | 17.044 | 2749.9 | 960.4302 | -960.4302 | 9.254% | 53.67% | 2835.6 | 1046.1302 | -1046.1302 | 10.08% | 58.46% | 4 | 0 | 0 | 0 | 0
2013-02-23 | 5 | 30152.1981 | 2222.9869 | 2217.0726 | -5.9143 | 2972.2 | 755.1274 | -755.1274 | 7.276% | 34.06% | 3060.2 | 843.1274 | -843.1274 | 8.124% | 38.03% | 5 | 0 | 0 | 0 | 0
2013-02-23 | 6 | 31457.8618 | 2383.7607 | 2402.5619 | 18.8012 | 3404.2 | 1001.6381 | -1001.6381 | 9.651% | 41.69% | 3435.2 | 1032.6381 | -1032.6381 | 9.95% | 42.98% | 6 | 0 | 0 | 0 | 0
2013-02-23 | 7 | 33530.685 | 2079.3854 | 2101.2511 | 21.8657 | 3343.9 | 1242.6489 | -1242.6489 | 11.97% | 59.14% | 3337.9 | 1236.6489 | -1236.6489 | 11.92% | 58.85% | 7 | 0 | 0 | 0 | 0
2013-02-23 | 8 | 34827.0369 | 1478.9617 | 1485.1946 | 6.2329 | 2798 | 1312.8054 | -1312.8054 | 12.65% | 88.39% | 2843.9 | 1358.7054 | -1358.7054 | 13.09% | 91.48% | 8 | 0 | 0 | 0 | 0
2013-02-23 | 9 | 35317.5403 | 1270.369 | 1284.2256 | 13.8566 | 2488.5 | 1204.2744 | -1204.2744 | 11.6% | 93.77% | 2524.9 | 1240.6744 | -1240.6744 | 11.95% | 96.61% | 9 | 0 | 0 | 0 | 0
2013-02-23 | 10 | 34870.2914 | 1237.8289 | 1248.6629 | 10.8339 | 1902 | 653.3371 | -653.3371 | 6.295% | 52.32% | 1938.1 | 689.4371 | -689.4371 | 6.643% | 55.21% | 10 | 0 | 0 | 0 | 0
2013-02-23 | 11 | 33953.9331 | 1683.2087 | 1684.9881 | 1.7794 | 1712.3 | 27.3119 | -27.3119 | 0.2632% | 1.621% | 1748.6 | 63.6119 | -63.6119 | 0.6129% | 3.775% | 11 | 0 | 0 | 0 | 0
2013-02-23 | 12 | 32842.0137 | 1915.5183 | 1929.7647 | 14.2463 | 1660.6 | 269.1647 | 269.1647 | 2.593% | 13.95% | 1697.1 | 232.6647 | 232.6647 | 2.242% | 12.06% | 12 | 1 | 0 | 1 | 1
2013-02-23 | 13 | 31653.4437 | 2064.3638 | 2072.8762 | 8.5124 | 1708.7 | 364.1762 | 364.1762 | 3.509% | 17.57% | 1762.1 | 310.7762 | 310.7762 | 2.994% | 14.99% | 13 | 1 | 0 | 1 | 1
2013-02-23 | 14 | 30484.7626 | 1957.4553 | 1966.0938 | 8.6386 | 1679.8 | 286.2938 | 286.2938 | 2.759% | 14.56% | 1746.9 | 219.1938 | 219.1938 | 2.112% | 11.15% | 14 | 1 | 0 | 1 | 1
2013-02-23 | 15 | 29681.2346 | 1686.4121 | 1692.3297 | 5.9176 | 1675.8 | 16.5297 | 16.5297 | 0.1593% | 0.9767% | 1736.9 | 44.5703 | -44.5703 | 0.4294% | 2.634% | 15 | 1 | 0 | 0 | 1
2013-02-23 | 16 | 29207.786 | 1443.2237 | 1454.1886 | 10.9648 | 1705.1 | 250.9114 | -250.9114 | 2.418% | 17.25% | 1758.5 | 304.3114 | -304.3114 | 2.932% | 20.93% | 16 | 0 | 0 | 0 | 0
2013-02-23 | 17 | 29039.4622 | 1135.4339 | 1138.3141 | 2.8802 | 1650.8 | 512.4859 | -512.4859 | 4.938% | 45.02% | 1714.8 | 576.4859 | -576.4859 | 5.555% | 50.64% | 17 | 0 | 0 | 0 | 0
2013-02-23 | 18 | 29320.1272 | 764.7779 | 773.1874 | 8.4095 | 1431.3 | 658.1126 | -658.1126 | 6.341% | 85.12% | 1478.3 | 705.1126 | -705.1126 | 6.794% | 91.2% | 18 | 0 | 0 | 0 | 0
2013-02-23 | 19 | 30970.6479 | 824.8791 | 835.506 | 10.627 | 1471.4 | 635.894 | -635.894 | 6.127% | 76.11% | 1522 | 686.494 | -686.494 | 6.615% | 82.17% | 19 | 0 | 0 | 0 | 0
2013-02-23 | 20 | 32278.5588 | 1696.6178 | 1706.1244 | 9.5066 | 1936.8 | 230.6756 | -230.6756 | 2.223% | 13.52% | 2005.3 | 299.1756 | -299.1756 | 2.883% | 17.54% | 20 | 0 | 0 | 0 | 0
2013-02-23 | 21 | 32130.4143 | 3141.168 | 3146.6584 | 5.4905 | 2627.5 | 519.1584 | 519.1584 | 5.002% | 16.5% | 2730.5 | 416.1584 | 416.1584 | 4.01% | 13.23% | 21 | 1 | 0 | 1 | 1
2013-02-23 | 22 | 31653.1446 | 4713.5304 | 4715.1569 | 1.6265 | 3356.5 | 1358.6569 | 1358.6569 | 13.09% | 28.81% | 3479.4 | 1235.7569 | 1235.7569 | 11.91% | 26.21% | 22 | 1 | 0 | 1 | 1
2013-02-23 | 23 | 30601.9734 | 6288.0616 | 6470.8479 | 182.7862 | 4008.8 | 2462.0479 | 2462.0479 | 23.72% | 38.05% | 4119.4 | 2351.4479 | 2351.4479 | 22.66% | 36.34% | 23 | 1 | 0 | 1 | 1
2013-02-23 | 24 | 29407.2805 | 6888.9217 | 7267.9405 | 379.0189 | 4519 | 2748.9405 | 2748.9405 | 26.49% | 37.82% | 4635.3 | 2632.6405 | 2632.6405 | 25.37% | 36.22% | 24 | 1 | 0 | 1 | 1
2013-02-24 | 1 | 28512.7827 | 7126.0257 | 7308.1118 | 182.086 | 5546.6 | 1761.5118 | 1761.5118 | 16.97% | 24.1% | 5637.6 | 1670.5118 | 1670.5118 | 16.1% | 22.86% | 1 | 1 | 0 | 1 | 1
2013-02-24 | 2 | 28019.1227 | 7083.3214 | 7187.9234 | 104.602 | 5748.3 | 1439.6234 | 1439.6234 | 13.87% | 20.03% | 5807.9 | 1380.0234 | 1380.0234 | 13.3% | 19.2% | 2 | 1 | 0 | 1 | 1
2013-02-24 | 3 | 27939.1381 | 6958.6858 | 7064.0606 | 105.3748 | 5935.1 | 1128.9606 | 1128.9606 | 10.88% | 15.98% | 5989.4 | 1074.6606 | 1074.6606 | 10.35% | 15.21% | 3 | 1 | 0 | 1 | 1
2013-02-24 | 4 | 28021.302 | 6804.3405 | 6905.1486 | 100.8081 | 6060.8 | 844.3486 | 844.3486 | 8.136% | 12.23% | 6104 | 801.1486 | 801.1486 | 7.719% | 11.6% | 4 | 1 | 0 | 1 | 1
2013-02-24 | 5 | 28446.3295 | 6962.7988 | 7060.4863 | 97.6876 | 6154.4 | 906.0863 | 906.0863 | 8.73% | 12.83% | 6205.1 | 855.3863 | 855.3863 | 8.242% | 12.12% | 5 | 1 | 0 | 1 | 1
2013-02-24 | 6 | 29483.9501 | 6997.3455 | 7092.9797 | 95.6341 | 6258.2 | 834.7797 | 834.7797 | 8.043% | 11.77% | 6310.3 | 782.6797 | 782.6797 | 7.541% | 11.03% | 6 | 1 | 0 | 1 | 1
2013-02-24 | 7 | 30833.389 | 6624.0569 | 6750.407 | 126.3501 | 6375.4 | 375.007 | 375.007 | 3.613% | 5.555% | 6445.9 | 304.507 | 304.507 | 2.934% | 4.511% | 7 | 1 | 0 | 1 | 1
2013-02-24 | 8 | 31631.1029 | 6544.3876 | 6681.0807 | 136.6931 | 6294.6 | 386.4807 | 386.4807 | 3.724% | 5.785% | 6373.1 | 307.9807 | 307.9807 | 2.967% | 4.61% | 8 | 1 | 0 | 1 | 1
2013-02-24 | 9 | 31963.6891 | 5975.0172 | 6044.1256 | 69.1083 | 6061.3 | 17.1744 | -17.1744 | 0.1655% | 0.2842% | 6110.7 | 66.5744 | -66.5744 | 0.6415% | 1.101% | 9 | 0 | 0 | 0 | 0
2013-02-24 | 10 | 31526.7929 | 5750.139 | 5809.578 | 59.439 | 5999.3 | 189.722 | -189.722 | 1.828% | 3.266% | 6046.2 | 236.622 | -236.622 | 2.28% | 4.073% | 10 | 0 | 0 | 0 | 0
2013-02-24 | 11 | 30670.0519 | 6178.9483 | 6232.172 | 53.2238 | 5967.3 | 264.872 | 264.872 | 2.552% | 4.25% | 6036.6 | 195.572 | 195.572 | 1.884% | 3.138% | 11 | 1 | 0 | 1 | 1
2013-02-24 | 12 | 29703.5986 | 5720.8749 | 5736.6369 | 15.762 | 5977 | 240.3631 | -240.3631 | 2.316% | 4.19% | 6063.6 | 326.9631 | -326.9631 | 3.15% | 5.7% | 12 | 0 | 0 | 0 | 0
2013-02-24 | 13 | 29108.5208 | 4548.0174 | 4547.321 | -0.69641 | 5951.2 | 1403.879 | -1403.879 | 13.53% | 30.87% | 6044.4 | 1497.079 | -1497.079 | 14.42% | 32.92% | 13 | 0 | 0 | 0 | 0
2013-02-24 | 14 | 28598.9055 | 3680.373 | 3678.132 | -2.2409 | 5948.7 | 2270.568 | -2270.568 | 21.88% | 61.73% | 6054 | 2375.868 | -2375.868 | 22.89% | 64.59% | 14 | 0 | 0 | 0 | 0
2013-02-24 | 15 | 28320.3554 | 3241.9456 | 3239.9664 | -1.9792 | 5966.6 | 2726.6336 | -2726.6336 | 26.27% | 84.16% | 6051.3 | 2811.3336 | -2811.3336 | 27.09% | 86.77% | 15 | 0 | 0 | 0 | 0
2013-02-24 | 16 | 28175.0441 | 3390.204 | 3403.44 | 13.236 | 5996.6 | 2593.16 | -2593.16 | 24.99% | 76.19% | 6081.5 | 2678.06 | -2678.06 | 25.8% | 78.69% | 16 | 0 | 0 | 0 | 0
2013-02-24 | 17 | 28458.4254 | 3831.6541 | 3853.48 | 21.8258 | 5663.3 | 1809.82 | -1809.82 | 17.44% | 46.97% | 5785.4 | 1931.92 | -1931.92 | 18.61% | 50.13% | 17 | 0 | 0 | 0 | 0
2013-02-24 | 18 | 29282.4711 | 4362.9445 | 4436.4379 | 73.4935 | 4347.9 | 88.5379 | 88.5379 | 0.8531% | 1.996% | 4522 | 85.5621 | -85.5621 | 0.8244% | 1.929% | 18 | 1 | 0 | 0 | 1
2013-02-24 | 19 | 31299.3971 | 4179.1306 | 4284.2382 | 105.1076 | 4166.8 | 117.4382 | 117.4382 | 1.132% | 2.741% | 4324.5 | 40.2618 | -40.2618 | 0.3879% | 0.9398% | 19 | 1 | 0 | 0 | 1
2013-02-24 | 20 | 32525.7982 | 5045.4022 | 5063.3433 | 17.9411 | 4303 | 760.3433 | 760.3433 | 7.326% | 15.02% | 4443.1 | 620.2433 | 620.2433 | 5.976% | 12.25% | 20 | 1 | 0 | 1 | 1
2013-02-24 | 21 | 32087.4572 | 6198.3072 | 6250.091 | 51.7838 | 4808.2 | 1441.891 | 1441.891 | 13.89% | 23.07% | 4942.9 | 1307.191 | 1307.191 | 12.6% | 20.91% | 21 | 1 | 0 | 1 | 1
2013-02-24 | 22 | 31025.7876 | 6864.3376 | 7072.2175 | 207.8799 | 5427.1 | 1645.1175 | 1645.1175 | 15.85% | 23.26% | 5460.5 | 1611.7175 | 1611.7175 | 15.53% | 22.79% | 22 | 1 | 0 | 1 | 1
2013-02-24 | 23 | 29015.4387 | 6883.4492 | 7246.2121 | 362.7629 | 5537.4 | 1708.8121 | 1708.8121 | 16.46% | 23.58% | 5646.6 | 1599.6121 | 1599.6121 | 15.41% | 22.08% | 23 | 1 | 0 | 1 | 1
2013-02-24 | 24 | 26987.5025 | 6721.3287 | 6945.8422 | 224.5136 | 5674.2 | 1271.6422 | 1271.6422 | 12.25% | 18.31% | 5803.6 | 1142.2422 | 1142.2422 | 11.01% | 16.44% | 24 | 1 | 0 | 1 | 1
2013-02-25 | 1 | 25432.4423 | 6663.8542 | 7007.6253 | 343.771 | 5807.5 | 1200.1253 | 1200.1253 | 11.56% | 17.13% | 5900.5 | 1107.1253 | 1107.1253 | 10.67% | 15.8% | 1 | 1 | 0 | 1 | 1
2013-02-25 | 2 | 24573.6818 | 6297.6581 | 6532.6465 | 234.9884 | 5588 | 944.6465 | 944.6465 | 9.102% | 14.46% | 5656.1 | 876.5465 | 876.5465 | 8.446% | 13.42% | 2 | 1 | 0 | 1 | 1
2013-02-25 | 3 | 24070.8425 | 5375.9902 | 5477.3153 | 101.3251 | 5716 | 238.6847 | -238.6847 | 2.3% | 4.358% | 5754.5 | 277.1847 | -277.1847 | 2.671% | 5.061% | 3 | 0 | 0 | 0 | 0
2013-02-25 | 4 | 24025.3587 | 3413.9581 | 3518.4315 | 104.4734 | 5894.9 | 2376.4685 | -2376.4685 | 22.9% | 67.54% | 5869.4 | 2350.9685 | -2350.9685 | 22.65% | 66.82% | 4 | 0 | 0 | 0 | 0
2013-02-25 | 5 | 24820.6626 | 2766.475 | 2885.8271 | 119.3521 | 5996.5 | 3110.6729 | -3110.6729 | 29.97% | 107.8% | 6069.1 | 3183.2729 | -3183.2729 | 30.67% | 110.3% | 5 | 0 | 0 | 0 | 0
2013-02-25 | 6 | 27149.6563 | 3224.0173 | 3426.2416 | 202.2243 | 6019.7 | 2593.4584 | -2593.4584 | 24.99% | 75.69% | 6136 | 2709.7584 | -2709.7584 | 26.11% | 79.09% | 6 | 0 | 0 | 0 | 0
2013-02-25 | 7 | 31252.5413 | 4155.1027 | 4259.8608 | 104.7581 | 6187.4 | 1927.5392 | -1927.5392 | 18.57% | 45.25% | 6317.9 | 2058.0392 | -2058.0392 | 19.83% | 48.31% | 7 | 0 | 0 | 0 | 0
2013-02-25 | 8 | 32741.3895 | 5144.9093 | 5278.5549 | 133.6456 | 6569.5 | 1290.9451 | -1290.9451 | 12.44% | 24.46% | 6727.7 | 1449.1451 | -1449.1451 | 13.96% | 27.45% | 8 | 0 | 0 | 0 | 0
2013-02-25 | 9 | 32567.9227 | 6153.6543 | 6661.3222 | 507.6679 | 7269.7 | 608.3778 | -608.3778 | 5.862% | 9.133% | 7479.9 | 818.5778 | -818.5778 | 7.887% | 12.29% | 9 | 0 | 1 | 0 | 0
2013-02-25 | 10 | 32950.995 | 6887.0661 | 8153.3196 | 1266.2536 | 7490.5 | 662.8196 | 662.8196 | 6.386% | 8.129% | 7688.7 | 464.6196 | 464.6196 | 4.477% | 5.699% | 10 | 1 | 0 | 1 | 1
2013-02-25 | 11 | 33312.3235 | 7339.7558 | 8331.9491 | 992.1933 | 7686.9 | 645.0491 | 645.0491 | 6.215% | 7.742% | 7872.8 | 459.1491 | 459.1491 | 4.424% | 5.511% | 11 | 1 | 0 | 1 | 1
2013-02-25 | 12 | 33237.1516 | 7633.9786 | 8444.5037 | 810.5251 | 7792.9 | 651.6037 | 651.6037 | 6.278% | 7.716% | 7957.6 | 486.9037 | 486.9037 | 4.691% | 5.766% | 12 | 1 | 0 | 1 | 1
2013-02-25 | 13 | 32991.5782 | 7602.6192 | 8098.6945 | 496.0753 | 7899.6 | 199.0945 | 199.0945 | 1.918% | 2.458% | 8038 | 60.6945 | 60.6945 | 0.5848% | 0.7494% | 13 | 1 | 0 | 1 | 1
2013-02-25 | 14 | 32850.8685 | 7475.9805 | 7902.2905 | 426.31 | 7893.3 | 8.9905 | 8.9905 | 0.08663% | 0.1138% | 8028 | 125.7095 | -125.7095 | 1.211% | 1.591% | 14 | 1 | 0 | 0 | 1
2013-02-25 | 15 | 32553.1723 | 7413.5689 | 7864.4052 | 450.8363 | 8084.3 | 219.8948 | -219.8948 | 2.119% | 2.796% | 8180.2 | 315.7948 | -315.7948 | 3.043% | 4.015% | 15 | 0 | 0 | 0 | 0
2013-02-25 | 16 | 32498.8966 | 7539.8173 | 7809.6877 | 269.8705 | 8105.7 | 296.0123 | -296.0123 | 2.852% | 3.79% | 8172.6 | 362.9123 | -362.9123 | 3.497% | 4.647% | 16 | 0 | 0 | 0 | 0
2013-02-25 | 17 | 32903.503 | 7776.2284 | 8149.8306 | 373.6022 | 8051.2 | 98.6306 | 98.6306 | 0.9503% | 1.21% | 8105.2 | 44.6306 | 44.6306 | 0.43% | 0.5476% | 17 | 1 | 0 | 1 | 1
2013-02-25 | 18 | 33812.291 | 8089.4667 | 8413.6018 | 324.1351 | 7884 | 529.6018 | 529.6018 | 5.103% | 6.295% | 7928.9 | 484.7018 | 484.7018 | 4.67% | 5.761% | 18 | 1 | 0 | 1 | 1
2013-02-25 | 19 | 36480.2327 | 8104.5321 | 8388.4067 | 283.8746 | 7494.3 | 894.1067 | 894.1067 | 8.615% | 10.66% | 7532.2 | 856.2067 | 856.2067 | 8.25% | 10.21% | 19 | 1 | 0 | 1 | 1
2013-02-25 | 20 | 38200.7685 | 7958.2746 | 8164.9976 | 206.723 | 7195.2 | 969.7976 | 969.7976 | 9.344% | 11.88% | 7226.5 | 938.4976 | 938.4976 | 9.043% | 11.49% | 20 | 1 | 0 | 1 | 1
2013-02-25 | 21 | 38125.3658 | 7888.566 | 8006.4819 | 117.9159 | 7069.3 | 937.1819 | 937.1819 | 9.03% | 11.71% | 7102.8 | 903.6819 | 903.6819 | 8.707% | 11.29% | 21 | 1 | 0 | 1 | 1
2013-02-25 | 22 | 37203.1752 | 7693.1904 | 7775.7434 | 82.553 | 6968.7 | 807.0434 | 807.0434 | 7.776% | 10.38% | 7014 | 761.7434 | 761.7434 | 7.34% | 9.796% | 22 | 1 | 0 | 1 | 1
2013-02-25 | 23 | 34985.7876 | 7159.8229 | 7258.5475 | 98.7246 | 6765.8 | 492.7475 | 492.7475 | 4.748% | 6.789% | 6825.6 | 432.9475 | 432.9475 | 4.172% | 5.965% | 23 | 1 | 0 | 1 | 1
2013-02-25 | 24 | 32638.893 | 6726.8212 | 6855.8926 | 129.0714 | 6485.1 | 370.7926 | 370.7926 | 3.573% | 5.408% | 6527.9 | 327.9926 | 327.9926 | 3.16% | 4.784% | 24 | 1 | 0 | 1 | 1
2013-02-26 | 1 | 31297.2967 | 6117.9868 | 6213.4943 | 95.5075 | 6146.4 | 67.0943 | 67.0943 | 0.6465% | 1.08% | 6417.8 | 204.3057 | -204.3057 | 1.969% | 3.288% | 1 | 1 | 1 | 0 | 1
2013-02-26 | 2 | 30675.3393 | 5609.3332 | 5671.0811 | 61.748 | 5945.4 | 274.3189 | -274.3189 | 2.643% | 4.837% | 6214.1 | 543.0189 | -543.0189 | 5.232% | 9.575% | 2 | 0 | 1 | 0 | 0
2013-02-26 | 3 | 30527.0505 | 5407.4037 | 5468.9094 | 61.5057 | 5671.1 | 202.1906 | -202.1906 | 1.948% | 3.697% | 5927.7 | 458.7906 | -458.7906 | 4.421% | 8.389% | 3 | 0 | 1 | 0 | 0
2013-02-26 | 4 | 30757.3262 | 4434.105 | 4511.7052 | 77.6002 | 5385.8 | 874.0948 | -874.0948 | 8.422% | 19.37% | 5614.1 | 1102.3948 | -1102.3948 | 10.62% | 24.43% | 4 | 0 | 1 | 0 | 0
2013-02-26 | 5 | 31949.114 | 3209.8672 | 3262.151 | 52.2838 | 4917.2 | 1655.049 | -1655.049 | 15.95% | 50.73% | 5133 | 1870.849 | -1870.849 | 18.03% | 57.35% | 5 | 0 | 1 | 0 | 0
2013-02-26 | 6 | 34888.0807 | 2552.4278 | 2592.1746 | 39.7469 | 4545.2 | 1953.0254 | -1953.0254 | 18.82% | 75.34% | 4759.1 | 2166.9254 | -2166.9254 | 20.88% | 83.59% | 6 | 0 | 1 | 0 | 0
2013-02-26 | 7 | 39542.3472 | 2195.7389 | 2235.8291 | 40.0902 | 4077.2 | 1841.3709 | -1841.3709 | 17.74% | 82.36% | 4249.7 | 2013.8709 | -2013.8709 | 19.4% | 90.07% | 7 | 0 | 0 | 0 | 0
2013-02-26 | 8 | 40293.6138 | 1840.013 | 1885.1726 | 45.1596 | 3208.8 | 1323.6274 | -1323.6274 | 12.75% | 70.21% | 3398 | 1512.8274 | -1512.8274 | 14.58% | 80.25% | 8 | 0 | 0 | 0 | 0
2013-02-26 | 9 | 38836.0289 | 1116.6222 | 1165.4488 | 48.8266 | 2180.6 | 1015.1512 | -1015.1512 | 9.781% | 87.1% | 2375.7 | 1210.2512 | -1210.2512 | 11.66% | 103.8% | 9 | 0 | 0 | 0 | 0
2013-02-26 | 10 | 37729.9222 | 566.3921 | 614.59 | 48.1979 | 1611 | 996.41 | -996.41 | 9.601% | 162.1% | 1745.9 | 1131.31 | -1131.31 | 10.9% | 184.1% | 10 | 0 | 0 | 0 | 0
2013-02-26 | 11 | 36478.6128 | 357.3032 | 406.2937 | 48.9905 | 1441.6 | 1035.3063 | -1035.3063 | 9.975% | 254.8% | 1521.6 | 1115.3063 | -1115.3063 | 10.75% | 274.5% | 11 | 0 | 0 | 0 | 0
2013-02-26 | 12 | 35137.5792 | 307.142 | 356.4037 | 49.2617 | 1355 | 998.5963 | -998.5963 | 9.622% | 280.2% | 1396 | 1039.5963 | -1039.5963 | 10.02% | 291.7% | 12 | 0 | 0 | 0 | 0
2013-02-26 | 13 | 33922.7458 | 291.8851 | 336.014 | 44.1289 | 1338.8 | 1002.786 | -1002.786 | 9.662% | 298.4% | 1357.5 | 1021.486 | -1021.486 | 9.842% | 304% | 13 | 0 | 0 | 0 | 0
2013-02-26 | 14 | 33034.6196 | 372.2873 | 418.7114 | 46.4241 | 1502.7 | 1083.9886 | -1083.9886 | 10.44% | 258.9% | 1485.3 | 1066.5886 | -1066.5886 | 10.28% | 254.7% | 14 | 0 | 0 | 0 | 0
2013-02-26 | 15 | 32197.3941 | 445.9569 | 496.4584 | 50.5015 | 1650.8 | 1154.3416 | -1154.3416 | 11.12% | 232.5% | 1630.6 | 1134.1416 | -1134.1416 | 10.93% | 228.4% | 15 | 0 | 0 | 0 | 0
2013-02-26 | 16 | 31618.1679 | 493.257 | 530.7622 | 37.5052 | 1813.4 | 1282.6378 | -1282.6378 | 12.36% | 241.7% | 1771.1 | 1240.3378 | -1240.3378 | 11.95% | 233.7% | 16 | 0 | 0 | 0 | 0
2013-02-26 | 17 | 31482.2658 | 689.2988 | 720.5127 | 31.2139 | 1994.8 | 1274.2873 | -1274.2873 | 12.28% | 176.9% | 1942.1 | 1221.5873 | -1221.5873 | 11.77% | 169.5% | 17 | 0 | 0 | 0 | 0
2013-02-26 | 18 | 31702.3774 | 901.873 | 967.8031 | 65.9301 | 1710.5 | 742.6969 | -742.6969 | 7.156% | 76.74% | 1688.6 | 720.7969 | -720.7969 | 6.945% | 74.48% | 18 | 0 | 0 | 0 | 0
2013-02-26 | 19 | 33849.0462 | 1621.2431 | 1673.8178 | 52.5746 | 1597.2 | 76.6178 | 76.6178 | 0.7382% | 4.577% | 1606.1 | 67.7178 | 67.7178 | 0.6525% | 4.046% | 19 | 1 | 0 | 1 | 1
2013-02-26 | 20 | 35391.2389 | 2451.51 | 2492.085 | 40.5751 | 1800.1 | 691.985 | 691.985 | 6.667% | 27.77% | 1813.9 | 678.185 | 678.185 | 6.535% | 27.21% | 20 | 1 | 0 | 1 | 1
2013-02-26 | 21 | 35299.5082 | 3658.0559 | 3701.9713 | 43.9155 | 2250.7 | 1451.2713 | 1451.2713 | 13.98% | 39.2% | 2290.3 | 1411.6713 | 1411.6713 | 13.6% | 38.13% | 21 | 1 | 0 | 1 | 1
2013-02-26 | 22 | 34192.0557 | 4976.8143 | 5068.2544 | 91.4401 | 2724.4 | 2343.8544 | 2343.8544 | 22.58% | 46.25% | 2772.1 | 2296.1544 | 2296.1544 | 22.12% | 45.3% | 22 | 1 | 0 | 1 | 1
2013-02-26 | 23 | 32108.3911 | 5804.9813 | 5926.7544 | 121.7731 | 3481.3 | 2445.4544 | 2445.4544 | 23.56% | 41.26% | 3550.9 | 2375.8544 | 2375.8544 | 22.89% | 40.09% | 23 | 1 | 0 | 1 | 1
2013-02-26 | 24 | 30002.5091 | 5991.0632 | 6034.5581 | 43.4949 | 4782.4 | 1252.1581 | 1252.1581 | 12.06% | 20.75% | 4854.5 | 1180.0581 | 1180.0581 | 11.37% | 19.56% | 24 | 1 | 0 | 1 | 1
2013-02-27 | 1 | 28783.5627 | 5089.5406 | 5114.3323 | 24.7917 | 5044.1 | 70.2323 | 70.2323 | 0.6767% | 1.373% | 5159.1 | 44.7677 | -44.7677 | 0.4313% | 0.8753% | 1 | 1 | 0 | 0 | 1
2013-02-27 | 2 | 28368.0596 | 4939.531 | 5010.9231 | 71.3921 | 5015.5 | 4.5769 | -4.5769 | 0.0441% | 0.09134% | 5028 | 17.0769 | -17.0769 | 0.1645% | 0.3408% | 2 | 0 | 0 | 0 | 0
2013-02-27 | 3 | 28409.2591 | 5222.4971 | 5353.1172 | 130.6201 | 4825.7 | 527.4172 | 527.4172 | 5.082% | 9.853% | 4903.9 | 449.2172 | 449.2172 | 4.328% | 8.392% | 3 | 1 | 0 | 1 | 1
2013-02-27 | 4 | 28918.3907 | 6253.6254 | 6453.2112 | 199.5858 | 4984 | 1469.2112 | 1469.2112 | 14.16% | 22.77% | 5017.4 | 1435.8112 | 1435.8112 | 13.83% | 22.25% | 4 | 1 | 0 | 1 | 1
2013-02-27 | 5 | 30138.3021 | 5410.8699 | 5568.436 | 157.5661 | 5133.2 | 435.236 | 435.236 | 4.194% | 7.816% | 5044.5 | 523.936 | 523.936 | 5.048% | 9.409% | 5 | 1 | 0 | 1 | 1
2013-02-27 | 6 | 33129.6076 | 4444.27 | 4607.1782 | 162.9083 | 4697.5 | 90.3218 | -90.3218 | 0.8703% | 1.96% | 4738.9 | 131.7218 | -131.7218 | 1.269% | 2.859% | 6 | 0 | 0 | 0 | 0
2013-02-27 | 7 | 37771.5201 | 4174.0942 | 4340.9937 | 166.8995 | 3775.2 | 565.7937 | 565.7937 | 5.452% | 13.03% | 4195.5 | 145.4937 | 145.4937 | 1.402% | 3.352% | 7 | 1 | 1 | 1 | 1
2013-02-27 | 8 | 38348.0729 | 4067.0175 | 4223.4305 | 156.4129 | 3264.6 | 958.8305 | 958.8305 | 9.239% | 22.7% | 3732.5 | 490.9305 | 490.9305 | 4.73% | 11.62% | 8 | 1 | 1 | 1 | 1
2013-02-27 | 9 | 36775.8158 | 3615.5188 | 3776.4331 | 160.9144 | 3448.2 | 328.2331 | 328.2331 | 3.163% | 8.692% | 3628 | 148.4331 | 148.4331 | 1.43% | 3.931% | 9 | 1 | 0 | 1 | 1
2013-02-27 | 10 | 35676.8496 | 4947.3226 | 5119.9774 | 172.6548 | 3591 | 1528.9774 | 1528.9774 | 14.73% | 29.86% | 3672.4 | 1447.5774 | 1447.5774 | 13.95% | 28.27% | 10 | 1 | 0 | 1 | 1
2013-02-27 | 11 | 34851.2324 | 4989.6617 | 5145.8814 | 156.2197 | 3771.5 | 1374.3814 | 1374.3814 | 13.24% | 26.71% | 3820.7 | 1325.1814 | 1325.1814 | 12.77% | 25.75% | 11 | 1 | 0 | 1 | 1
2013-02-27 | 12 | 34020.0653 | 5184.6139 | 5330.506 | 145.8921 | 3820.9 | 1509.606 | 1509.606 | 14.55% | 28.32% | 3879.2 | 1451.306 | 1451.306 | 13.98% | 27.23% | 12 | 1 | 0 | 1 | 1
2013-02-27 | 13 | 33270.3308 | 5146.6253 | 5294.4175 | 147.7922 | 3811.1 | 1483.3175 | 1483.3175 | 14.29% | 28.02% | 3847.2 | 1447.2175 | 1447.2175 | 13.94% | 27.33% | 13 | 1 | 0 | 1 | 1
2013-02-27 | 14 | 32778.2137 | 5125.8686 | 5271.5867 | 145.7181 | 3739.5 | 1532.0867 | 1532.0867 | 14.76% | 29.06% | 3840.8 | 1430.7867 | 1430.7867 | 13.79% | 27.14% | 14 | 1 | 0 | 1 | 1
2013-02-27 | 15 | 32254.3268 | 5197.6725 | 5338.1196 | 140.4471 | 3639 | 1699.1196 | 1699.1196 | 16.37% | 31.83% | 3747.5 | 1590.6196 | 1590.6196 | 15.33% | 29.8% | 15 | 1 | 0 | 1 | 1
2013-02-27 | 16 | 31874.7826 | 4940.1299 | 5060.3724 | 120.2425 | 3435.5 | 1624.8724 | 1624.8724 | 15.66% | 32.11% | 3468.7 | 1591.6724 | 1591.6724 | 15.34% | 31.45% | 16 | 1 | 0 | 1 | 1
2013-02-27 | 17 | 31973.9558 | 4375.3191 | 4451.4739 | 76.1548 | 3186.1 | 1265.3739 | 1265.3739 | 12.19% | 28.43% | 3175.1 | 1276.3739 | 1276.3739 | 12.3% | 28.67% | 17 | 1 | 0 | 1 | 1
2013-02-27 | 18 | 32429.9167 | 3947.5439 | 4012.9784 | 65.4344 | 2657.7 | 1355.2784 | 1355.2784 | 13.06% | 33.77% | 2651 | 1361.9784 | 1361.9784 | 13.12% | 33.94% | 18 | 1 | 0 | 1 | 1
2013-02-27 | 19 | 34745.711 | 3043.1115 | 3100.7898 | 57.6783 | 2067.1 | 1033.6898 | 1033.6898 | 9.96% | 33.34% | 2090 | 1010.7898 | 1010.7898 | 9.739% | 32.6% | 19 | 1 | 0 | 1 | 1
2013-02-27 | 20 | 36640.0957 | 2605.8029 | 2657.4659 | 51.663 | 2218.2 | 439.2659 | 439.2659 | 4.232% | 16.53% | 2151.7 | 505.7659 | 505.7659 | 4.873% | 19.03% | 20 | 1 | 0 | 1 | 1
2013-02-27 | 21 | 36636.1596 | 2458.0992 | 2501.8537 | 43.7545 | 2193.5 | 308.3537 | 308.3537 | 2.971% | 12.33% | 2233.8 | 268.0537 | 268.0537 | 2.583% | 10.71% | 21 | 1 | 0 | 1 | 1
2013-02-27 | 22 | 35666.8778 | 2325.9086 | 2344.0299 | 18.1213 | 2081.5 | 262.5299 | 262.5299 | 2.53% | 11.2% | 2216.5 | 127.5299 | 127.5299 | 1.229% | 5.441% | 22 | 1 | 0 | 1 | 1
2013-02-27 | 23 | 33712.888 | 2448.4928 | 2483.4708 | 34.978 | 2019.2 | 464.2708 | 464.2708 | 4.473% | 18.69% | 2186.7 | 296.7708 | 296.7708 | 2.859% | 11.95% | 23 | 1 | 0 | 1 | 1
2013-02-27 | 24 | 31667.9323 | 2544.2869 | 2589.2299 | 44.943 | 1960.9 | 628.3299 | 628.3299 | 6.054% | 24.27% | 2146.9 | 442.3299 | 442.3299 | 4.262% | 17.08% | 24 | 1 | 0 | 1 | 1
2013-02-28 | 1 | 30668.8242 | 2279.1801 | 2307.6518 | 28.4717 | 2043.2 | 264.4518 | 264.4518 | 2.548% | 11.46% | 2190.6 | 117.0518 | 117.0518 | 1.128% | 5.072% | 1 | 1 | 0 | 1 | 1
2013-02-28 | 2 | 30415.7135 | 2007.557 | 2060.7251 | 53.1681 | 2018.7 | 42.0251 | 42.0251 | 0.4049% | 2.039% | 2166 | 105.2749 | -105.2749 | 1.014% | 5.109% | 2 | 1 | 0 | 0 | 1
2013-02-28 | 3 | 30471.7114 | 1799.015 | 1863.7199 | 64.7049 | 1927.6 | 63.8801 | -63.8801 | 0.6155% | 3.428% | 2088.5 | 224.7801 | -224.7801 | 2.166% | 12.06% | 3 | 0 | 0 | 0 | 0
2013-02-28 | 4 | 31001.7407 | 1656.5428 | 1722.0771 | 65.5342 | 1980.5 | 258.4229 | -258.4229 | 2.49% | 15.01% | 2162.1 | 440.0229 | -440.0229 | 4.24% | 25.55% | 4 | 0 | 0 | 0 | 0
2013-02-28 | 5 | 32336.4968 | 1707.4311 | 1774.3965 | 66.9654 | 2115.3 | 340.9035 | -340.9035 | 3.285% | 19.21% | 2300.8 | 526.4035 | -526.4035 | 5.072% | 29.67% | 5 | 0 | 0 | 0 | 0
2013-02-28 | 6 | 35388.0959 | 1736.8735 | 1806.1571 | 69.2836 | 2186.2 | 380.0429 | -380.0429 | 3.662% | 21.04% | 2321.7 | 515.5429 | -515.5429 | 4.967% | 28.54% | 6 | 0 | 0 | 0 | 0
2013-02-28 | 7 | 40081.2223 | 1587.7821 | 1660.2065 | 72.4244 | 2171.2 | 510.9935 | -510.9935 | 4.924% | 30.78% | 2295.5 | 635.2935 | -635.2935 | 6.121% | 38.27% | 7 | 0 | 0 | 0 | 0
2013-02-28 | 8 | 40736.9259 | 1501.5728 | 1583.2983 | 81.7255 | 1831.4 | 248.1017 | -248.1017 | 2.391% | 15.67% | 1973.3 | 390.0017 | -390.0017 | 3.758% | 24.63% | 8 | 0 | 0 | 0 | 0
2013-02-28 | 9 | 39013.6688 | 1387.9523 | 1457.5163 | 69.564 | 1445.2 | 12.3163 | 12.3163 | 0.1187% | 0.845% | 1538.6 | 81.0837 | -81.0837 | 0.7813% | 5.563% | 9 | 1 | 0 | 0 | 1
2013-02-28 | 10 | 37929.9673 | 1379.1101 | 1449.6789 | 70.5688 | 1065.2 | 384.4789 | 384.4789 | 3.705% | 26.52% | 1155.2 | 294.4789 | 294.4789 | 2.837% | 20.31% | 10 | 1 | 0 | 1 | 1
2013-02-28 | 11 | 36850.0684 | 1577.9597 | 1640.2344 | 62.2747 | 1131.3 | 508.9344 | 508.9344 | 4.904% | 31.03% | 1233.5 | 406.7344 | 406.7344 | 3.919% | 24.8% | 11 | 1 | 0 | 1 | 1
2013-02-28 | 12 | 35654.2976 | 1440.7163 | 1493.2397 | 52.5235 | 1243.4 | 249.8397 | 249.8397 | 2.407% | 16.73% | 1363.6 | 129.6397 | 129.6397 | 1.249% | 8.682% | 12 | 1 | 0 | 1 | 1
2013-02-28 | 13 | 34429.5681 | 1216.8857 | 1266.2054 | 49.3196 | 1293.8 | 27.5946 | -27.5946 | 0.2659% | 2.179% | 1433.5 | 167.2946 | -167.2946 | 1.612% | 13.21% | 13 | 0 | 0 | 0 | 0
2013-02-28 | 14 | 33398.1186 | 1078.4228 | 1135.9324 | 57.5096 | 1389.5 | 253.5676 | -253.5676 | 2.443% | 22.32% | 1551.4 | 415.4676 | -415.4676 | 4.003% | 36.58% | 14 | 0 | 0 | 0 | 0
2013-02-28 | 15 | 32486.3833 | 1066.0537 | 1115.0131 | 48.9594 | 1480.8 | 365.7869 | -365.7869 | 3.524% | 32.81% | 1646.9 | 531.8869 | -531.8869 | 5.125% | 47.7% | 15 | 0 | 0 | 0 | 0
2013-02-28 | 16 | 31882.8706 | 1375.9293 | 1419.0404 | 43.1111 | 1561.1 | 142.0596 | -142.0596 | 1.369% | 10.01% | 1635.7 | 216.6596 | -216.6596 | 2.088% | 15.27% | 16 | 0 | 0 | 0 | 0
2013-02-28 | 17 | 31848.4338 | 1540.6148 | 1588.1049 | 47.4901 | 1572.6 | 15.5049 | 15.5049 | 0.1494% | 0.9763% | 1688.8 | 100.6951 | -100.6951 | 0.9702% | 6.341% | 17 | 1 | 0 | 0 | 1
2013-02-28 | 18 | 32441.5538 | 1296.7393 | 1346.4567 | 49.7174 | 1369.4 | 22.9433 | -22.9433 | 0.2211% | 1.704% | 1452.5 | 106.0433 | -106.0433 | 1.022% | 7.876% | 18 | 0 | 0 | 0 | 0
2013-02-28 | 19 | 34824.421 | 739.117 | 785.2832 | 46.1662 | 1240.4 | 455.1168 | -455.1168 | 4.385% | 57.96% | 1274.4 | 489.1168 | -489.1168 | 4.713% | 62.29% | 19 | 0 | 0 | 0 | 0
2013-02-28 | 20 | 36881.83 | 393.0292 | 441.9124 | 48.8832 | 1169.6 | 727.6876 | -727.6876 | 7.011% | 164.7% | 1181 | 739.0876 | -739.0876 | 7.121% | 167.2% | 20 | 0 | 0 | 0 | 0
2013-02-28 | 21 | 37045.7765 | 372.8689 | 423.0513 | 50.1824 | 1082.1 | 659.0487 | -659.0487 | 6.35% | 155.8% | 1078.5 | 655.4487 | -655.4487 | 6.315% | 154.9% | 21 | 0 | 0 | 0 | 0
2013-02-28 | 22 | 36205.1348 | 471.4444 | 527.1787 | 55.7342 | 1070.5 | 543.3213 | -543.3213 | 5.235% | 103.1% | 1106.4 | 579.2213 | -579.2213 | 5.581% | 109.9% | 22 | 0 | 0 | 0 | 0
2013-02-28 | 23 | 34179.6043 | 598.9939 | 640.4822 | 41.4884 | 1046.1 | 405.6178 | -405.6178 | 3.908% | 63.33% | 1094.5 | 454.0178 | -454.0178 | 4.375% | 70.89% | 23 | 0 | 0 | 0 | 0
2013-02-28 | 24 | 32235.7768 | 508.2068 | 549.2178 | 41.011 | 986.6 | 437.3822 | -437.3822 | 4.214% | 79.64% | 1040.2 | 490.9822 | -490.9822 | 4.731% | 89.4% | 24 | 0 | 0 | 0 | 0

## HOUR-AHEAD BY OUTPUT LEVEL
February 2013
Hour-Ahead Aggregated WPF - By Output Level
|  | ERCOT System Load [MW] | Real-Time Mean |  |  | Hour-Ahead Mean | [9 empty] | By Estimated Uncurtailed Output Level | Percent of Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
By Estimated Uncurtailed Output Level | <1000 | 32077.1912 | 631.5868 | 648.2883 | 16.7015 | 1042.05 | 410.938 | -393.7617 | 3.96% | 75.48% | 1129.9276 | 493.2841 | -481.6394 | 4.753% | 88.6% | <1000 | 3.947% | 3.947% | 3.947% | 3.947%
| 1000-2000 | 32639.072 | 1510.1708 | 1530.8191 | 20.6482 | 1911.4656 | 527.9427 | -380.6465 | 5.087% | 35.63% | 2031.1721 | 599.6232 | -500.3531 | 5.778% | 40.47% | 1000-2000 | 28.69% | 17.21% | 18.85% | 28.69%
| 2000-3000 | 32332.3171 | 2427.5798 | 2442.9488 | 15.369 | 2728.0389 | 545.8613 | -285.0902 | 5.26% | 22.4% | 2849.0095 | 593.8313 | -406.0607 | 5.722% | 24.44% | 2000-3000 | 35.79% | 16.84% | 29.47% | 35.79%
| 3000-4000 | 30543.1987 | 3519.6861 | 3542.3124 | 22.6262 | 3802.167 | 713.5419 | -259.8546 | 6.875% | 20.22% | 3912.5629 | 742.2378 | -370.2505 | 7.152% | 21.09% | 3000-4000 | 49.48% | 11.34% | 42.27% | 49.48%
| 4000-5000 | 31170.1862 | 4393.5921 | 4440.5817 | 46.9896 | 4435.9859 | 755.0697 | 4.5958 | 7.275% | 16.9% | 4546.8521 | 775.4421 | -106.2704 | 7.472% | 17.35% | 4000-5000 | 56.34% | 14.08% | 50.7% | 56.34%
| 5000-6000 | 31342.9729 | 5368.2685 | 5436.7216 | 68.4531 | 5182.8879 | 694.145 | 253.8337 | 6.688% | 12.81% | 5346.3818 | 739.4966 | 90.3398 | 7.125% | 13.62% | 5000-6000 | 54.55% | 33.33% | 50% | 54.55%
| 6000-7000 | 30299.7146 | 6439.4163 | 6523.6004 | 84.1841 | 6142.955 | 595.141 | 380.6454 | 5.734% | 9.201% | 6333.3967 | 580.9701 | 190.2037 | 5.598% | 8.99% | 6000-7000 | 66.67% | 46.67% | 55% | 66.67%
| >=7000 | 30822.2688 | 7439.716 | 7774.7346 | 335.0186 | 7508.6965 | 511.3376 | 266.0381 | 4.927% | 6.735% | 7724.3306 | 500.9936 | 50.404 | 4.827% | 6.596% | >=7000 | 61.18% | 49.41% | 48.24% | 61.18%

## HR-AHEAD BY HOUR, ON-OFF PEAK
February 2013
Hour-Ahead Aggregated WPF - By Operating Hour
|  | ERCOT System Load [MW] | Real-Time Mean |  |  | Hour-Ahead Mean | [9 empty] | Operating Hour |  | Percent of Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
All Hours Average |  | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3875.3134 | 588.2535 | -98.3972 | 5.668% | 25.81% | 4012.0708 | 625.5364 | -235.1547 | 6.027% | 28.67% | All Hours Average |  | 42.86% | 22.77% | 35.42% | 42.86%
Off-Peak Hours (1-6,23-24) |  | 28253.9071 | 4018.2701 | 4112.4485 | 94.1784 | 4366.4723 | 654.4816 | -254.0238 | 6.306% | 26.4% | 4518.567 | 714.7956 | -406.1184 | 6.887% | 30.3% | Off-Peak Hours (1-6,23-24) |  | 36.69% | 25.81% | 27.82% | 36.69%
On-Peak Hours (7-22) |  | 33135.7448 | 3547.2548 | 3609.15 | 61.8952 | 3629.7339 | 555.1395 | -20.584 | 5.349% | 25.51% | 3758.8228 | 580.9069 | -149.6728 | 5.597% | 27.86% | On-Peak Hours (7-22) |  | 39.72% | 17.94% | 34.07% | 39.72%
By Operating Hour | 1 | 27667.8458 | 4333.2378 | 4441.3649 | 108.1271 | 4494.6393 | 601.4562 | -53.2744 | 5.795% | 24.33% | 4650.35 | 635.633 | -208.9851 | 6.125% | 27.31% | 1 | Number of Hours when: | 14 | 9 | 12 | 14
| 2 | 26973.9786 | 4200.6242 | 4304.1763 | 103.552 | 4497.0393 | 530.6039 | -192.863 | 5.113% | 19.45% | 4644.6464 | 599.2932 | -340.4701 | 5.774% | 23.31% | 2 |  | 12 | 10 | 9 | 12
| 3 | 26727.0852 | 4040.3346 | 4141.0629 | 100.7283 | 4435.3321 | 566.8632 | -294.2692 | 5.462% | 21.28% | 4582.1321 | 642.7938 | -441.0692 | 6.194% | 25.86% | 3 |  | 10 | 9 | 8 | 10
| 4 | 26867.0931 | 3858.59 | 3960.7758 | 102.1859 | 4383.7429 | 734.9153 | -422.967 | 7.081% | 29.27% | 4531.3429 | 806.4689 | -570.567 | 7.771% | 33.28% | 4 |  | 10 | 7 | 7 | 10
| 5 | 27632.9234 | 3664.5957 | 3738.5774 | 73.9817 | 4335.575 | 766.4686 | -596.9976 | 7.385% | 31.83% | 4468.6536 | 854.6293 | -730.0762 | 8.235% | 36.15% | 5 |  | 8 | 8 | 5 | 8
| 6 | 29773.4606 | 3585.4175 | 3648.2905 | 62.873 | 4225.4714 | 703.8755 | -577.1809 | 6.782% | 27.44% | 4355.2036 | 780.5934 | -706.9131 | 7.521% | 31.16% | 6 |  | 8 | 4 | 3 | 8
| 7 | 33277.2537 | 3529.235 | 3568.0168 | 38.7818 | 4124.5107 | 610.3902 | -556.4939 | 5.881% | 22.55% | 4248.9929 | 704.5017 | -680.976 | 6.788% | 26.53% | 7 |  | 5 | 4 | 3 | 5
| 8 | 34491.8526 | 3539.6341 | 3577.963 | 38.3289 | 4026.6107 | 517.1051 | -448.6478 | 4.982% | 20.76% | 4154.775 | 618.1108 | -576.812 | 5.956% | 24.14% | 8 |  | 8 | 5 | 5 | 8
| 9 | 34156.5464 | 3373.7918 | 3427.0123 | 53.2205 | 3792.7964 | 467.9771 | -365.7841 | 4.509% | 22.82% | 3916.2821 | 549.3331 | -489.2698 | 5.293% | 25.71% | 9 |  | 7 | 5 | 6 | 7
| 10 | 33950.9527 | 3345.8809 | 3432.343 | 86.4621 | 3502.0714 | 507.5549 | -69.7284 | 4.89% | 25.94% | 3619.6143 | 535.3147 | -187.2713 | 5.158% | 27.75% | 10 |  | 12 | 4 | 11 | 12
| 11 | 33634.3941 | 3586.3944 | 3669.9358 | 83.5414 | 3369.0964 | 628.1416 | 300.8394 | 6.052% | 27.54% | 3474.9179 | 605.0128 | 195.018 | 5.829% | 28.59% | 11 |  | 17 | 3 | 15 | 17
| 12 | 33092.9227 | 3568.646 | 3633.3198 | 64.6737 | 3279.9464 | 689.4271 | 353.3733 | 6.643% | 32.72% | 3374.1571 | 646.3664 | 259.1626 | 6.228% | 33.47% | 12 |  | 17 | 3 | 17 | 17
| 13 | 32554.9016 | 3490.1192 | 3545.0568 | 54.9376 | 3290.2143 | 601.1343 | 254.8425 | 5.792% | 29.73% | 3391.6571 | 613.5287 | 153.3997 | 5.912% | 30.79% | 13 |  | 13 | 4 | 12 | 13
| 14 | 32176.5925 | 3518.7033 | 3569.5255 | 50.8221 | 3472.2429 | 549.6836 | 97.2826 | 5.296% | 25.07% | 3568.4607 | 548.5264 | 1.0647 | 5.285% | 25.82% | 14 |  | 12 | 4 | 12 | 12
| 15 | 31790.7457 | 3617.9186 | 3672.2501 | 54.3315 | 3529.0179 | 547.489 | 143.2322 | 5.275% | 17.58% | 3631.7571 | 538.1024 | 40.4929 | 5.185% | 18.46% | 15 |  | 15 | 4 | 13 | 15
| 16 | 31564.5667 | 3717.0181 | 3778.3743 | 61.3563 | 3547.8107 | 550.875 | 230.5636 | 5.308% | 17.22% | 3662.95 | 549.7178 | 115.4243 | 5.297% | 16.8% | 16 |  | 17 | 4 | 15 | 17
| 17 | 31619.3104 | 3702.956 | 3775.8704 | 72.9143 | 3508.1857 | 534.9389 | 267.6847 | 5.154% | 17.57% | 3637.1607 | 516.4067 | 138.7097 | 4.976% | 17.68% | 17 |  | 15 | 6 | 15 | 15
| 18 | 31999.6914 | 3453.7114 | 3516.5921 | 62.8807 | 3386.5679 | 437.213 | 130.0243 | 4.213% | 19.23% | 3525.0071 | 414.3766 | -8.415 | 3.993% | 20.46% | 18 |  | 16 | 6 | 14 | 16
| 19 | 33824.9951 | 3144.9909 | 3199.8666 | 54.8757 | 3519.7929 | 469.0938 | -319.9263 | 4.52% | 30.88% | 3662.8 | 523.7275 | -462.9334 | 5.046% | 36.19% | 19 |  | 8 | 6 | 6 | 8
| 20 | 34647.642 | 3394.8642 | 3452.4689 | 57.6047 | 3781.0786 | 501.7987 | -328.6097 | 4.835% | 35.87% | 3942.2107 | 593.1894 | -489.7418 | 5.716% | 42% | 20 |  | 8 | 8 | 5 | 8
| 21 | 34225.5582 | 3766.1424 | 3839.4934 | 73.351 | 3951.1786 | 626.1995 | -111.6851 | 6.034% | 34.52% | 4135.8607 | 662.431 | -296.3673 | 6.383% | 38.77% | 21 |  | 11 | 11 | 9 | 11
| 22 | 33163.9914 | 4006.0707 | 4088.3108 | 82.2401 | 3994.6214 | 643.21 | 93.6894 | 6.198% | 28.14% | 4194.5607 | 675.864 | -106.2499 | 6.512% | 32.64% | 22 |  | 16 | 12 | 11 | 16
| 23 | 31234.4151 | 4191.9971 | 4289.0738 | 97.0767 | 4182.2571 | 680.5405 | 106.8167 | 6.557% | 29.85% | 4371.2107 | 712.2339 | -82.1369 | 6.863% | 33.92% | 23 |  | 15 | 10 | 12 | 15
| 24 | 29154.4552 | 4271.364 | 4376.2665 | 104.9025 | 4377.7214 | 651.1291 | -1.455 | 6.274% | 27.78% | 4544.9964 | 686.7189 | -168.73 | 6.617% | 31.37% | 24 |  | 14 | 7 | 13 | 14
Operating Hours 23-24, 1-2 |  | 28757.6737 | 4249.3058 | 4352.7204 | 103.4146 | 4387.9143 | 615.9324 | -35.1939 | 5.935% | 25.35% | 4552.8009 | 658.4698 | -200.0805 | 6.345% | 28.98% | Operating Hours 23-24, 1-2 |  | 44.35% | 29.03% | 37.1% | 44.35%
Operating Hours 3-6 |  | 27750.1406 | 3787.2345 | 3872.1767 | 84.9422 | 4345.0304 | 693.0307 | -472.8537 | 6.678% | 27.46% | 4484.333 | 771.1214 | -612.1564 | 7.43% | 31.61% | Operating Hours 3-6 |  | 29.03% | 22.58% | 18.55% | 29.03%
Operating Hours 7-10 |  | 33969.1514 | 3447.1354 | 3501.3338 | 54.1983 | 3861.4973 | 525.7568 | -360.1636 | 5.066% | 23.02% | 3984.9161 | 601.8151 | -483.5823 | 5.799% | 26.03% | Operating Hours 7-10 |  | 25.81% | 14.52% | 20.16% | 25.81%
Operating Hours 11-14 |  | 32864.7027 | 3540.9658 | 3604.4595 | 63.4937 | 3352.875 | 617.0966 | 251.5845 | 5.946% | 28.77% | 3452.2982 | 603.3586 | 152.1613 | 5.814% | 29.67% | Operating Hours 11-14 |  | 47.58% | 11.29% | 45.16% | 47.58%
Operating Hours 15-18 |  | 31743.5786 | 3622.901 | 3685.7717 | 62.8707 | 3492.8955 | 517.629 | 192.8762 | 4.988% | 17.9% | 3614.2188 | 504.6509 | 71.553 | 4.862% | 18.35% | Operating Hours 15-18 |  | 50.81% | 16.13% | 45.97% | 50.81%
Operating Hours 19-22 |  | 33965.5467 | 3578.0171 | 3645.0349 | 67.0179 | 3811.6679 | 560.0755 | -166.6329 | 5.396% | 32.35% | 3983.858 | 613.803 | -338.8231 | 5.914% | 37.4% | Operating Hours 19-22 |  | 34.68% | 29.84% | 25% | 34.68%

## HOUR-AHEAD DAILY MEAN
February 2013
Hour-Ahead Aggregated WPF - Daily Mean
Operating Day | ERCOT System Load [MW] | Real-Time Daily Mean |  |  | Hour-Ahead Daily Mean | [9 empty] | Operating Day | Percent of Hours when:
|  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[6 empty] | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
Monthly Average | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3875.3134 | 588.2535 | -98.3972 | 5.668% | 25.81% | 4012.0708 | 625.5364 | -235.1547 | 6.027% | 28.67% |  | 42.86% | 22.77% | 35.42% | 42.86%
2013-02-01 | 32658.7786 | 3639.1257 | 3686.0787 | 46.953 | 3184.325 | 705.3894 | 501.7537 | 6.797% | 18.81% | 3285.0708 | 662.6364 | 401.0078 | 6.385% | 18.66% | 2013-02-01 | 66.67% | 0% | 54.17% | 66.67%
2013-02-02 | 29393.6932 | 3166.5569 | 3170.2058 | 3.6489 | 3190.45 | 545.1375 | -20.2442 | 5.253% | 25.99% | 3234.1125 | 575.1231 | -63.9067 | 5.541% | 28.48% | 2013-02-02 | 33.33% | 0% | 37.5% | 33.33%
2013-02-03 | 28652.3427 | 3816.8101 | 3818.8872 | 2.0771 | 3370.3167 | 697.8224 | 448.5705 | 6.724% | 19.81% | 3442.9417 | 705.9411 | 375.9455 | 6.802% | 22.67% | 2013-02-03 | 62.5% | 12.5% | 54.17% | 62.5%
2013-02-04 | 30155.1557 | 3028.5372 | 3042.9548 | 14.4176 | 3621.25 | 685.775 | -578.2952 | 6.608% | 23.44% | 3758.7333 | 791.4083 | -715.7785 | 7.625% | 26.76% | 2013-02-04 | 16.67% | 12.5% | 16.67% | 16.67%
2013-02-05 | 30868.8698 | 1209.3239 | 1219.1493 | 9.8254 | 1280.0167 | 348.7851 | -60.8673 | 3.361% | 59.81% | 1358.1083 | 357.3072 | -138.959 | 3.443% | 65.51% | 2013-02-05 | 37.5% | 0% | 29.17% | 37.5%
2013-02-06 | 30610.9759 | 3071.3932 | 3087.3536 | 15.9605 | 3294.8042 | 672.7959 | -207.4505 | 6.483% | 23.86% | 3378.9833 | 704.1828 | -291.6297 | 6.785% | 25.18% | 2013-02-06 | 41.67% | 16.67% | 33.33% | 41.67%
2013-02-07 | 30500.7563 | 3960.9827 | 4030.1195 | 69.1368 | 4171.5958 | 304.7252 | -141.4763 | 2.936% | 7.598% | 4246.75 | 329.4481 | -216.6305 | 3.174% | 8.454% | 2013-02-07 | 45.83% | 4.167% | 33.33% | 45.83%
2013-02-08 | 30132.8696 | 3089.5321 | 3101.1631 | 11.631 | 3200.5042 | 386.7636 | -99.3411 | 3.727% | 17.07% | 3320.8167 | 408.3595 | -219.6536 | 3.935% | 19.32% | 2013-02-08 | 37.5% | 0% | 37.5% | 37.5%
2013-02-09 | 30165.599 | 7634.0866 | 7731.2296 | 97.143 | 7740.75 | 246.2844 | -9.5204 | 2.373% | 3.274% | 7927.475 | 248.6384 | -196.2454 | 2.396% | 3.437% | 2013-02-09 | 54.17% | 37.5% | 33.33% | 54.17%
2013-02-10 | 28415.358 | 3871.6319 | 3895.4641 | 23.8322 | 4221.3083 | 552.9121 | -325.8442 | 5.327% | 46.88% | 4371.1125 | 631.0383 | -475.6484 | 6.08% | 55.19% | 2013-02-10 | 29.17% | 20.83% | 16.67% | 29.17%
2013-02-11 | 31730.6495 | 2519.4337 | 2523.6832 | 4.2495 | 2894.6833 | 534.8745 | -371.0001 | 5.154% | 36.72% | 3026.5042 | 626.0345 | -502.8209 | 6.032% | 43.73% | 2013-02-11 | 25% | 16.67% | 16.67% | 25%
2013-02-12 | 32576.8689 | 2978.9997 | 3023.9627 | 44.963 | 3470.6583 | 999.0859 | -446.6956 | 9.626% | 52.76% | 3551.1708 | 1005.8817 | -527.2081 | 9.692% | 54% | 2013-02-12 | 37.5% | 8.333% | 37.5% | 37.5%
2013-02-13 | 33027.1346 | 1223.7074 | 1235.8274 | 12.1199 | 1550.6 | 400.0027 | -314.7726 | 3.854% | 47.24% | 1704.3375 | 512.1611 | -468.5101 | 4.935% | 58.31% | 2013-02-13 | 20.83% | 25% | 12.5% | 20.83%
2013-02-14 | 32693.8388 | 2526.1252 | 2541.6121 | 15.4868 | 2388.9792 | 411.43 | 152.6329 | 3.964% | 19.18% | 2450.2042 | 364.205 | 91.4079 | 3.509% | 18.98% | 2013-02-14 | 54.17% | 20.83% | 54.17% | 54.17%
2013-02-15 | 33125.5147 | 3889.0233 | 3936.5723 | 47.5491 | 3775.1 | 460.8811 | 161.4723 | 4.441% | 23.99% | 3895.925 | 455.8395 | 40.6473 | 4.392% | 29.25% | 2013-02-15 | 62.5% | 8.333% | 62.5% | 62.5%
2013-02-16 | 32395.7082 | 2135.8694 | 2153.6275 | 17.7581 | 2532.7833 | 608.3731 | -379.1558 | 5.862% | 35.08% | 2649.8792 | 682.019 | -496.2517 | 6.571% | 40.88% | 2013-02-16 | 12.5% | 16.67% | 12.5% | 12.5%
2013-02-17 | 30223.127 | 7110.4923 | 7449.0893 | 338.5969 | 7031.3583 | 510.3966 | 417.7309 | 4.918% | 6.905% | 7273.35 | 484.7391 | 175.7393 | 4.671% | 6.578% | 2013-02-17 | 62.5% | 75% | 54.17% | 62.5%
2013-02-18 | 30425.9863 | 5793.6812 | 6120.5499 | 326.8687 | 5754.5542 | 772.4814 | 365.9958 | 7.443% | 12.67% | 5934.7667 | 771.7597 | 185.7833 | 7.436% | 12.32% | 2013-02-18 | 58.33% | 25% | 50% | 58.33%
2013-02-19 | 31196.6078 | 4271.3681 | 4303.2326 | 31.8645 | 4756.3708 | 938.4274 | -453.1383 | 9.042% | 25.12% | 4944.4208 | 978.4802 | -641.1883 | 9.428% | 26.71% | 2013-02-19 | 45.83% | 37.5% | 33.33% | 45.83%
2013-02-20 | 33461.2597 | 5187.0068 | 5300.5495 | 113.5427 | 6021.5292 | 752.3088 | -720.9797 | 7.249% | 20.08% | 6305.0833 | 1008.211 | -1004.5338 | 9.714% | 25.15% | 2013-02-20 | 8.333% | 95.83% | 4.167% | 8.333%
2013-02-21 | 32340.0881 | 4863.3988 | 4951.5059 | 88.1072 | 5928.4875 | 1187.0012 | -976.9816 | 11.44% | 33.63% | 6119.9958 | 1319.6492 | -1168.4899 | 12.72% | 37.05% | 2013-02-21 | 20.83% | 29.17% | 16.67% | 20.83%
2013-02-22 | 33092.0778 | 2078.6557 | 2088.5159 | 9.8602 | 2170.9917 | 345.5047 | -82.4758 | 3.329% | 18.61% | 2313.5333 | 415.3536 | -225.0174 | 4.002% | 25.27% | 2013-02-22 | 29.17% | 12.5% | 20.83% | 29.17%
2013-02-23 | 31344.6674 | 2287.3555 | 2320.7534 | 33.3979 | 2260.45 | 582.4835 | 60.3034 | 5.612% | 28.87% | 2341.6708 | 602.2825 | -20.9174 | 5.803% | 30.61% | 2013-02-23 | 45.83% | 4.167% | 41.67% | 45.83%
2013-02-24 | 29651.5147 | 5736.3765 | 5828.893 | 92.5165 | 5657.9792 | 604.8132 | 170.9138 | 5.828% | 12.03% | 5759.0708 | 586.1016 | 69.8222 | 5.647% | 12.12% | 2013-02-24 | 70.83% | 8.333% | 66.67% | 70.83%
2013-02-25 | 31724.1458 | 6520.2212 | 6861.0907 | 340.8696 | 7244.8542 | 688.6109 | -383.7634 | 6.635% | 14.59% | 7535.4458 | 783.0638 | -674.3551 | 7.545% | 16.74% | 2013-02-25 | 45.83% | 83.33% | 20.83% | 45.83%
2013-02-26 | 33871.3596 | 2558.8567 | 2614.6232 | 55.7665 | 2666.6375 | 623.8597 | -52.0143 | 6.011% | 40.62% | 2772.8333 | 671.8305 | -158.2102 | 6.473% | 42.54% | 2013-02-26 | 29.17% | 12.5% | 29.17% | 29.17%
2013-02-27 | 33285.0804 | 4270.726 | 4381.2587 | 110.5327 | 3898.8542 | 583.37 | 482.4045 | 5.621% | 12.82% | 4046.7958 | 512.1683 | 334.4629 | 4.935% | 11.53% | 2013-02-27 | 79.17% | 20.83% | 70.83% | 79.17%
2013-02-28 | 34517.0085 | 1279.9999 | 1335.6992 | 55.6992 | 1228.5833 | 320.8032 | 107.1158 | 3.091% | 35.13% | 1388.8917 | 321.1566 | -53.1925 | 3.094% | 37.43% | 2013-02-28 | 66.67% | 33.33% | 41.67% | 66.67%
Formulas:
Operating Day = [Operating Day]

## HOUR-AHEAD HOURLY MEAN
February 2013
Hour-Ahead Aggregate WPF - Hourly Mean
Operating Day | Operating Hour | ERCOT System Load [MW] | Real-Time |  |  | Hour-Ahead | [9 empty] | Operating Hour | Hours when:
|  |  | WGRs Aggregated Power Output [MW] | WGRs Aggregated HSL (Estimated Uncurtailed Output) [MW] | Estimated Curtailments [MW] | Short-term Wind Power Forecast STWPF [MW] | STWPF Forecast Error |  |  |  | COP HSL [MW] | COP HSL "Forecast" Error
[7 empty] | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Absolute MW Error [MW] | Mean MW Error [MW] | Absolute Percent Error of Installed Capacity [%] | Absolute Percent Error of Estimated Uncurtailed Output [%] |  | Estimated Uncurtailed Output > STWPF TARGET 50% | COP HSL-STWPF > 2% Installed Capacity TARGET 0% | Estimated Uncurtailed Output >=COP HSL TARGET 50% | Estimated Uncurtailed Output >=STWPF TARGET 50%
Monthly Average |  | 31508.4656 | 3704.2599 | 3776.9162 | 72.6562 | 3875.3134 | 588.2535 | -98.3972 | 5.668% | 25.81% | 4012.0708 | 625.5364 | -235.1547 | 6.027% | 28.67% | Average | 42.86% | 22.77% | 35.42% | 42.86%
Monthly Standard Deviation |  | 3458.3871 | 2243.6544 | 2325.6638 | 176.1796 | 2187.2794 | 533.9448 | 788.6435 | 5.145% | 33.22% | 2232.045 | 551.3325 | 800.2914 | 5.312% | 37.54% | St. Deviation
Monthly Maximum |  | 40736.9259 | 8526.8431 | 8854.9324 | 1574.3329 | 9013.1 | 4067.203 | 2726.9343 | 39.19% | 274.9% | 9301.1 | 4195.203 | 2724.9343 | 40.42% | 323.9% | Max.
Monthly Minimum |  | 23611.8924 | 135.1685 | 143.8527 | -42.961 | 346.9 | 1.1347 | -4067.203 | 0.01093% | 0.01775% | 376.6 | 1.2319 | -4195.203 | 0.01187% | 0.01493% | Min.
2013-02-01 | 1 | 28903.2237 | 3176.1174 | 3185.6333 | 9.5159 | 3046.4 | 139.2333 | 139.2333 | 1.342% | 4.371% | 3220.1 | 34.4667 | -34.4667 | 0.3321% | 1.082% | 1 | 1 | 0 | 0 | 1
2013-02-01 | 2 | 28565.4173 | 2903.9421 | 2912.5707 | 8.6286 | 2698.4 | 214.1707 | 214.1707 | 2.064% | 7.353% | 2850.8 | 61.7707 | 61.7707 | 0.5952% | 2.121% | 2 | 1 | 0 | 1 | 1
2013-02-01 | 3 | 28719.4526 | 2296.8456 | 2300.1776 | 3.332 | 2818.3 | 518.1224 | -518.1224 | 4.992% | 22.53% | 2909.2 | 609.0224 | -609.0224 | 5.868% | 26.48% | 3 | 0 | 0 | 0 | 0
2013-02-01 | 4 | 29209.5197 | 2107.0549 | 2112.7068 | 5.6519 | 2914.5 | 801.7932 | -801.7932 | 7.726% | 37.95% | 2968.3 | 855.5932 | -855.5932 | 8.244% | 40.5% | 4 | 0 | 0 | 0 | 0
2013-02-01 | 5 | 30503.9308 | 1861.1293 | 1872.3455 | 11.2162 | 2227.8 | 355.4545 | -355.4545 | 3.425% | 18.98% | 2319.6 | 447.2545 | -447.2545 | 4.309% | 23.89% | 5 | 0 | 0 | 0 | 0
2013-02-01 | 6 | 33457.6174 | 1842.8186 | 1855.7023 | 12.8837 | 1886.1 | 30.3977 | -30.3977 | 0.2929% | 1.638% | 1993.2 | 137.4977 | -137.4977 | 1.325% | 7.409% | 6 | 0 | 0 | 0 | 0
2013-02-01 | 7 | 38169.9799 | 1842.1573 | 1856.1608 | 14.0035 | 1797.7 | 58.4608 | 58.4608 | 0.5633% | 3.15% | 1910.9 | 54.7392 | -54.7392 | 0.5274% | 2.949% | 7 | 1 | 0 | 0 | 1
2013-02-01 | 8 | 39596.6815 | 1771.4323 | 1796.1919 | 24.7596 | 1743.5 | 52.6919 | 52.6919 | 0.5077% | 2.934% | 1828.9 | 32.7081 | -32.7081 | 0.3152% | 1.821% | 8 | 1 | 0 | 0 | 1
2013-02-01 | 9 | 38139.0816 | 1546.2695 | 1563.9631 | 17.6936 | 1647.9 | 83.9369 | -83.9369 | 0.8088% | 5.367% | 1723.6 | 159.6369 | -159.6369 | 1.538% | 10.21% | 9 | 0 | 0 | 0 | 0
2013-02-01 | 10 | 36747.1527 | 974.4528 | 982.002 | 7.5492 | 1406.9 | 424.898 | -424.898 | 4.094% | 43.27% | 1446.1 | 464.098 | -464.098 | 4.472% | 47.26% | 10 | 0 | 0 | 0 | 0
2013-02-01 | 11 | 35470.6573 | 1167.7999 | 1174.3049 | 6.505 | 1234.9 | 60.5951 | -60.5951 | 0.5839% | 5.16% | 1285 | 110.6951 | -110.6951 | 1.067% | 9.426% | 11 | 0 | 0 | 0 | 0
2013-02-01 | 12 | 34103.5191 | 1701.6092 | 1698.8609 | -2.7483 | 1416.8 | 282.0609 | 282.0609 | 2.718% | 16.6% | 1446.4 | 252.4609 | 252.4609 | 2.433% | 14.86% | 12 | 1 | 0 | 1 | 1
2013-02-01 | 13 | 32920.1769 | 2650.61 | 2646.5781 | -4.0319 | 1651.5 | 995.0781 | 995.0781 | 9.588% | 37.6% | 1716.5 | 930.0781 | 930.0781 | 8.962% | 35.14% | 13 | 1 | 0 | 1 | 1
2013-02-01 | 14 | 32258.5193 | 3791.3046 | 3784.776 | -6.5286 | 2019.5 | 1765.276 | 1765.276 | 17.01% | 46.64% | 2120.3 | 1664.476 | 1664.476 | 16.04% | 43.98% | 14 | 1 | 0 | 1 | 1
2013-02-01 | 15 | 31634.0832 | 4793.1525 | 4785.2925 | -7.8599 | 2460.5 | 2324.7925 | 2324.7925 | 22.4% | 48.58% | 2578.4 | 2206.8925 | 2206.8925 | 21.26% | 46.12% | 15 | 1 | 0 | 1 | 1
2013-02-01 | 16 | 31086.6036 | 4821.9216 | 4818.3999 | -3.5217 | 3151.4 | 1666.9999 | 1666.9999 | 16.06% | 34.6% | 3258.8 | 1559.5999 | 1559.5999 | 15.03% | 32.37% | 16 | 1 | 0 | 1 | 1
2013-02-01 | 17 | 30819.4854 | 5391.8369 | 5394.7412 | 2.9043 | 3822.3 | 1572.4412 | 1572.4412 | 15.15% | 29.15% | 3941 | 1453.7412 | 1453.7412 | 14.01% | 26.95% | 17 | 1 | 0 | 1 | 1
2013-02-01 | 18 | 31053.0181 | 4874.8601 | 4881.562 | 6.7019 | 4170.2 | 711.362 | 711.362 | 6.854% | 14.57% | 4276.1 | 605.462 | 605.462 | 5.834% | 12.4% | 18 | 1 | 0 | 1 | 1
2013-02-01 | 19 | 33039.3482 | 4407.9627 | 4420.8684 | 12.9057 | 4589.3 | 168.4316 | -168.4316 | 1.623% | 3.81% | 4654.7 | 233.8316 | -233.8316 | 2.253% | 5.289% | 19 | 0 | 0 | 0 | 0
2013-02-01 | 20 | 33403.3872 | 5905.9255 | 5975.0626 | 69.137 | 5432.6 | 542.4626 | 542.4626 | 5.227% | 9.079% | 5503.6 | 471.4626 | 471.4626 | 4.543% | 7.891% | 20 | 1 | 0 | 1 | 1
2013-02-01 | 21 | 33109.2029 | 6660.6719 | 6850.3465 | 189.6746 | 5693.3 | 1157.0465 | 1157.0465 | 11.15% | 16.89% | 5878 | 972.3465 | 972.3465 | 9.369% | 14.19% | 21 | 1 | 0 | 1 | 1
2013-02-01 | 22 | 32452.2227 | 6984.9051 | 7292.1243 | 307.2191 | 5677.6 | 1614.5243 | 1614.5243 | 15.56% | 22.14% | 5839.1 | 1453.0243 | 1453.0243 | 14% | 19.93% | 22 | 1 | 0 | 1 | 1
2013-02-01 | 23 | 31061.5721 | 7017.4619 | 7402.0304 | 384.5685 | 6385.7 | 1016.3304 | 1016.3304 | 9.793% | 13.73% | 6511.8 | 890.2304 | 890.2304 | 8.578% | 12.03% | 23 | 1 | 0 | 1 | 1
2013-02-01 | 24 | 29386.8325 | 6846.7748 | 6903.4861 | 56.7113 | 6530.7 | 372.7861 | 372.7861 | 3.592% | 5.4% | 6661.3 | 242.1861 | 242.1861 | 2.334% | 3.508% | 24 | 1 | 0 | 1 | 1
2013-02-02 | 1 | 27878.9467 | 6490.5691 | 6490.108 | -0.46103 | 6631.7 | 141.592 | -141.592 | 1.364% | 2.182% | 6694.9 | 204.792 | -204.792 | 1.973% | 3.155% | 1 | 0 | 0 | 0 | 0
2013-02-02 | 2 | 27069.7084 | 6133.4399 | 6143.7593 | 10.3193 | 6321 | 177.2407 | -177.2407 | 1.708% | 2.885% | 6447.3 | 303.5407 | -303.5407 | 2.925% | 4.941% | 2 | 0 | 0 | 0 | 0
2013-02-02 | 3 | 26605.6481 | 5566.7216 | 5571.0564 | 4.3348 | 5661.5 | 90.4436 | -90.4436 | 0.8715% | 1.623% | 5766.1 | 195.0436 | -195.0436 | 1.879% | 3.501% | 3 | 0 | 0 | 0 | 0
2013-02-02 | 4 | 26544.8923 | 5032.4626 | 5046.3782 | 13.9156 | 5227.2 | 180.8218 | -180.8218 | 1.742% | 3.583% | 5286.9 | 240.5218 | -240.5218 | 2.317% | 4.766% | 4 | 0 | 0 | 0 | 0
2013-02-02 | 5 | 26879.1872 | 4176.7663 | 4186.2765 | 9.5101 | 4897.5 | 711.2235 | -711.2235 | 6.853% | 16.99% | 4939.4 | 753.1235 | -753.1235 | 7.257% | 17.99% | 5 | 0 | 0 | 0 | 0
2013-02-02 | 6 | 28071.9553 | 3420.9208 | 3429.8217 | 8.9009 | 3992.3 | 562.4783 | -562.4783 | 5.42% | 16.4% | 4023.1 | 593.2783 | -593.2783 | 5.716% | 17.3% | 6 | 0 | 0 | 0 | 0
2013-02-02 | 7 | 29641.7545 | 2482.8561 | 2492.9852 | 10.1291 | 3541.7 | 1048.7148 | -1048.7148 | 10.1% | 42.07% | 3569.9 | 1076.9148 | -1076.9148 | 10.38% | 43.2% | 7 | 0 | 0 | 0 | 0
2013-02-02 | 8 | 30885.7539 | 2436.9042 | 2446.5822 | 9.6781 | 3246.3 | 799.7178 | -799.7178 | 7.706% | 32.69% | 3281.8 | 835.2178 | -835.2178 | 8.048% | 34.14% | 8 | 0 | 0 | 0 | 0
2013-02-02 | 9 | 31622.2274 | 3032.7336 | 3040.6248 | 7.8912 | 2931.4 | 109.2248 | 109.2248 | 1.052% | 3.592% | 2985.1 | 55.5248 | 55.5248 | 0.535% | 1.826% | 9 | 1 | 0 | 1 | 1
2013-02-02 | 10 | 31543.065 | 3467.4311 | 3466.3619 | -1.0692 | 2489.7 | 976.6619 | 976.6619 | 9.41% | 28.18% | 2540.6 | 925.7619 | 925.7619 | 8.92% | 26.71% | 10 | 1 | 0 | 1 | 1
2013-02-02 | 11 | 31173.0258 | 4456.7679 | 4456.9822 | 0.21428 | 2786.4 | 1670.5822 | 1670.5822 | 16.1% | 37.48% | 2791.2 | 1665.7822 | 1665.7822 | 16.05% | 37.37% | 11 | 1 | 0 | 1 | 1
2013-02-02 | 12 | 30601.4203 | 4693.9226 | 4695.3365 | 1.4139 | 3040.9 | 1654.4365 | 1654.4365 | 15.94% | 35.24% | 3027.4 | 1667.9365 | 1667.9365 | 16.07% | 35.52% | 12 | 1 | 0 | 1 | 1
2013-02-02 | 13 | 30036.3124 | 3998.8734 | 4001.6153 | 2.7419 | 3175.9 | 825.7153 | 825.7153 | 7.956% | 20.63% | 3164.6 | 837.0153 | 837.0153 | 8.065% | 20.92% | 13 | 1 | 0 | 1 | 1
2013-02-02 | 14 | 29517.5566 | 3550.2428 | 3553.0769 | 2.8341 | 3561.1 | 8.0231 | -8.0231 | 0.07731% | 0.2258% | 3547.8 | 5.2769 | 5.2769 | 0.05084% | 0.1485% | 14 | 0 | 0 | 1 | 0
2013-02-02 | 15 | 29229.8271 | 3449.0174 | 3440.5 | -8.5174 | 3548.7 | 108.2 | -108.2 | 1.043% | 3.145% | 3533.6 | 93.1 | -93.1 | 0.897% | 2.706% | 15 | 0 | 0 | 0 | 0
2013-02-02 | 16 | 29131.8985 | 3477.2609 | 3448.7004 | -28.5605 | 3070.2 | 378.5004 | 378.5004 | 3.647% | 10.98% | 3068.4 | 380.3004 | 380.3004 | 3.664% | 11.03% | 16 | 1 | 0 | 1 | 1
2013-02-02 | 17 | 29208.9046 | 2814.1586 | 2813.8832 | -0.27537 | 2263.8 | 550.0832 | 550.0832 | 5.3% | 19.55% | 2310.4 | 503.4832 | 503.4832 | 4.851% | 17.89% | 17 | 1 | 0 | 1 | 1
2013-02-02 | 18 | 29489.3291 | 1974.0312 | 1977.6161 | 3.5849 | 1844.1 | 133.5161 | 133.5161 | 1.286% | 6.751% | 1884.1 | 93.5161 | 93.5161 | 0.9011% | 4.729% | 18 | 1 | 0 | 1 | 1
2013-02-02 | 19 | 31246.7644 | 1401.0812 | 1408.0817 | 7.0004 | 1970.4 | 562.3183 | -562.3183 | 5.418% | 39.94% | 1988.3 | 580.2183 | -580.2183 | 5.591% | 41.21% | 19 | 0 | 0 | 0 | 0
2013-02-02 | 20 | 31544.0224 | 1097.3471 | 1098.7455 | 1.3984 | 1707.7 | 608.9545 | -608.9545 | 5.867% | 55.42% | 1741.1 | 642.3545 | -642.3545 | 6.189% | 58.46% | 20 | 0 | 0 | 0 | 0
2013-02-02 | 21 | 31005.7798 | 835.8227 | 839.0936 | 3.2708 | 1485.8 | 646.7064 | -646.7064 | 6.231% | 77.07% | 1560.2 | 721.1064 | -721.1064 | 6.948% | 85.94% | 21 | 0 | 0 | 0 | 0
2013-02-02 | 22 | 30196.05 | 693.6634 | 701.5625 | 7.8991 | 1256.7 | 555.1375 | -555.1375 | 5.349% | 79.13% | 1361.6 | 660.0375 | -660.0375 | 6.36% | 94.08% | 22 | 0 | 0 | 0 | 0
2013-02-02 | 23 | 28915.9602 | 636.967 | 651.7683 | 14.8014 | 1052.4 | 400.6317 | -400.6317 | 3.86% | 61.47% | 1129 | 477.2317 | -477.2317 | 4.598% | 73.22% | 23 | 0 | 0 | 0 | 0
2013-02-02 | 24 | 27408.647 | 677.4041 | 684.0232 | 6.6192 | 866.4 | 182.3768 | -182.3768 | 1.757% | 26.66% | 975.9 | 291.8768 | -291.8768 | 2.812% | 42.67% | 24 | 0 | 0 | 0 | 0
2013-02-03 | 1 | 26305.8048 | 680.0233 | 684.6273 | 4.604 | 814.8 | 130.1727 | -130.1727 | 1.254% | 19.01% | 928.8 | 244.1727 | -244.1727 | 2.353% | 35.67% | 1 | 0 | 0 | 0 | 0
2013-02-03 | 2 | 25654.4219 | 659.7585 | 671.6533 | 11.8948 | 839.7 | 168.0467 | -168.0467 | 1.619% | 25.02% | 959.7 | 288.0467 | -288.0467 | 2.775% | 42.89% | 2 | 0 | 0 | 0 | 0
2013-02-03 | 3 | 25413.7978 | 596.6463 | 601.5307 | 4.8843 | 867.9 | 266.3693 | -266.3693 | 2.567% | 44.28% | 969.5 | 367.9693 | -367.9693 | 3.545% | 61.17% | 3 | 0 | 0 | 0 | 0
2013-02-03 | 4 | 25479.8261 | 808.467 | 811.0769 | 2.6099 | 1032.5 | 221.4231 | -221.4231 | 2.133% | 27.3% | 1132.2 | 321.1231 | -321.1231 | 3.094% | 39.59% | 4 | 0 | 0 | 0 | 0
2013-02-03 | 5 | 25860.1781 | 1067.5778 | 1068.5545 | 0.97676 | 1395 | 326.4455 | -326.4455 | 3.145% | 30.55% | 1490.6 | 422.0455 | -422.0455 | 4.067% | 39.5% | 5 | 0 | 0 | 0 | 0
2013-02-03 | 6 | 26777.7699 | 1310.0743 | 1316.4932 | 6.4189 | 1560.6 | 244.1068 | -244.1068 | 2.352% | 18.54% | 1628.3 | 311.8068 | -311.8068 | 3.004% | 23.68% | 6 | 0 | 0 | 0 | 0
2013-02-03 | 7 | 28163.6435 | 1646.2459 | 1648.5286 | 2.2827 | 1618.1 | 30.4286 | 30.4286 | 0.2932% | 1.846% | 1684 | 35.4714 | -35.4714 | 0.3418% | 2.152% | 7 | 1 | 0 | 0 | 1
2013-02-03 | 8 | 29405.3214 | 2003.5307 | 2005.316 | 1.7853 | 1926.3 | 79.016 | 79.016 | 0.7613% | 3.94% | 1981.8 | 23.516 | 23.516 | 0.2266% | 1.173% | 8 | 1 | 0 | 1 | 1
2013-02-03 | 9 | 30479.5242 | 2300.0943 | 2302.4091 | 2.3148 | 2183.2 | 119.2091 | 119.2091 | 1.149% | 5.178% | 2223.5 | 78.9091 | 78.9091 | 0.7603% | 3.427% | 9 | 1 | 0 | 1 | 1
2013-02-03 | 10 | 30581.6688 | 2156.117 | 2162.6435 | 6.5265 | 1982.3 | 180.3435 | 180.3435 | 1.738% | 8.339% | 2034.1 | 128.5435 | 128.5435 | 1.239% | 5.944% | 10 | 1 | 0 | 1 | 1
2013-02-03 | 11 | 30015.6169 | 3107.1968 | 3113.3459 | 6.1491 | 2066.8 | 1046.5459 | 1046.5459 | 10.08% | 33.61% | 2077.6 | 1035.7459 | 1035.7459 | 9.98% | 33.27% | 11 | 1 | 0 | 1 | 1
2013-02-03 | 12 | 29536.7907 | 4616.2409 | 4617.2281 | 0.9872 | 2314.9 | 2302.3281 | 2302.3281 | 22.18% | 49.86% | 2305.2 | 2312.0281 | 2312.0281 | 22.28% | 50.07% | 12 | 1 | 0 | 1 | 1
2013-02-03 | 13 | 29325.8769 | 5362.4148 | 5354.1343 | -8.2805 | 2627.2 | 2726.9343 | 2726.9343 | 26.27% | 50.93% | 2629.2 | 2724.9343 | 2724.9343 | 26.26% | 50.89% | 13 | 1 | 0 | 1 | 1
2013-02-03 | 14 | 29083.2635 | 5162.1937 | 5139.3084 | -22.8853 | 3465.7 | 1673.6084 | 1673.6084 | 16.13% | 32.56% | 3445 | 1694.3084 | 1694.3084 | 16.33% | 32.97% | 14 | 1 | 0 | 1 | 1
2013-02-03 | 15 | 29140.2239 | 5281.8599 | 5263.7545 | -18.1054 | 4239.3 | 1024.4545 | 1024.4545 | 9.871% | 19.46% | 4194.3 | 1069.4545 | 1069.4545 | 10.3% | 20.32% | 15 | 1 | 0 | 1 | 1
2013-02-03 | 16 | 29237.0841 | 5796.9883 | 5794.7537 | -2.2345 | 4552.2 | 1242.5537 | 1242.5537 | 11.97% | 21.44% | 4485 | 1309.7537 | 1309.7537 | 12.62% | 22.6% | 16 | 1 | 0 | 1 | 1
2013-02-03 | 17 | 29330.7828 | 5789.0055 | 5814.9711 | 25.9656 | 4377.5 | 1437.4711 | 1437.4711 | 13.85% | 24.72% | 4379.2 | 1435.7711 | 1435.7711 | 13.83% | 24.69% | 17 | 1 | 0 | 1 | 1
2013-02-03 | 18 | 29421.7777 | 4854.2721 | 4860.8497 | 6.5776 | 4476.1 | 384.7497 | 384.7497 | 3.707% | 7.915% | 4528.9 | 331.9497 | 331.9497 | 3.198% | 6.829% | 18 | 1 | 0 | 1 | 1
2013-02-03 | 19 | 30801.081 | 4644.675 | 4650.7126 | 6.0376 | 5384.4 | 733.6874 | -733.6874 | 7.069% | 15.78% | 5435.5 | 784.7874 | -784.7874 | 7.562% | 16.87% | 19 | 0 | 0 | 0 | 0
2013-02-03 | 20 | 31124.222 | 5800.7068 | 5798.0338 | -2.673 | 6014.3 | 216.2662 | -216.2662 | 2.084% | 3.73% | 6092.8 | 294.7662 | -294.7662 | 2.84% | 5.084% | 20 | 0 | 0 | 0 | 0
2013-02-03 | 21 | 30906.9563 | 6910.91 | 6913.7396 | 2.8296 | 6364.5 | 549.2396 | 549.2396 | 5.292% | 7.944% | 6585.6 | 328.1396 | 328.1396 | 3.162% | 4.746% | 21 | 1 | 1 | 1 | 1
2013-02-03 | 22 | 29938.1846 | 7344.414 | 7346.0854 | 1.6715 | 6578.4 | 767.6854 | 767.6854 | 7.397% | 10.45% | 6836.5 | 509.5854 | 509.5854 | 4.91% | 6.937% | 22 | 1 | 1 | 1 | 1
2013-02-03 | 23 | 29057.3629 | 7131.7504 | 7138.5474 | 6.797 | 6946.4 | 192.1474 | 192.1474 | 1.851% | 2.692% | 7172.4 | 33.8526 | -33.8526 | 0.3262% | 0.4742% | 23 | 1 | 1 | 0 | 1
2013-02-03 | 24 | 26615.0456 | 6572.2799 | 6574.9948 | 2.7149 | 7259.5 | 684.5052 | -684.5052 | 6.595% | 10.41% | 7430.9 | 855.9052 | -855.9052 | 8.247% | 13.02% | 24 | 0 | 0 | 0 | 0
2013-02-04 | 1 | 24890.9166 | 5908.5078 | 5910.9356 | 2.4277 | 7070.5 | 1159.5644 | -1159.5644 | 11.17% | 19.62% | 7291.3 | 1380.3644 | -1380.3644 | 13.3% | 23.35% | 1 | 0 | 1 | 0 | 0
2013-02-04 | 2 | 23937.541 | 5354.5929 | 5357.8685 | 3.2755 | 6458.1 | 1100.2315 | -1100.2315 | 10.6% | 20.53% | 6690.6 | 1332.7315 | -1332.7315 | 12.84% | 24.87% | 2 | 0 | 1 | 0 | 0
2013-02-04 | 3 | 23611.8924 | 5035.0563 | 5041.0477 | 5.9914 | 5688.7 | 647.6523 | -647.6523 | 6.24% | 12.85% | 5930.4 | 889.3523 | -889.3523 | 8.569% | 17.64% | 3 | 0 | 1 | 0 | 0
2013-02-04 | 4 | 23668.521 | 4592.5687 | 4601.1593 | 8.5906 | 5856.4 | 1255.2407 | -1255.2407 | 12.09% | 27.28% | 6049.2 | 1448.0407 | -1448.0407 | 13.95% | 31.47% | 4 | 0 | 0 | 0 | 0
2013-02-04 | 5 | 24382.2297 | 4180.3616 | 4194.3853 | 14.0238 | 5531.9 | 1337.5147 | -1337.5147 | 12.89% | 31.89% | 5698.5 | 1504.1147 | -1504.1147 | 14.49% | 35.86% | 5 | 0 | 0 | 0 | 0
2013-02-04 | 6 | 26667.8482 | 4287.4076 | 4302.0949 | 14.6873 | 5301.6 | 999.5051 | -999.5051 | 9.631% | 23.23% | 5457.4 | 1155.3051 | -1155.3051 | 11.13% | 26.85% | 6 | 0 | 0 | 0 | 0
2013-02-04 | 7 | 30636.634 | 4012.1782 | 4010.3017 | -1.8765 | 5124.8 | 1114.4983 | -1114.4983 | 10.74% | 27.79% | 5271.4 | 1261.0983 | -1261.0983 | 12.15% | 31.45% | 7 | 0 | 0 | 0 | 0
2013-02-04 | 8 | 32207.8746 | 3839.748 | 3843.5795 | 3.8316 | 4770.8 | 927.2205 | -927.2205 | 8.934% | 24.12% | 4921.5 | 1077.9205 | -1077.9205 | 10.39% | 28.04% | 8 | 0 | 0 | 0 | 0
2013-02-04 | 9 | 31741.641 | 3311.7498 | 3318.4081 | 6.6583 | 4154.8 | 836.3919 | -836.3919 | 8.059% | 25.2% | 4303.5 | 985.0919 | -985.0919 | 9.492% | 29.69% | 9 | 0 | 0 | 0 | 0
2013-02-04 | 10 | 32060.5536 | 2790.7125 | 2797.035 | 6.3225 | 3505.4 | 708.365 | -708.365 | 6.825% | 25.33% | 3701.6 | 904.565 | -904.565 | 8.716% | 32.34% | 10 | 0 | 0 | 0 | 0
2013-02-04 | 11 | 32202.06 | 2782.5156 | 2834.0324 | 51.5168 | 2837.2 | 3.1676 | -3.1676 | 0.03052% | 0.1118% | 2999.3 | 165.2676 | -165.2676 | 1.592% | 5.832% | 11 | 0 | 0 | 0 | 0
2013-02-04 | 12 | 32255.2395 | 1956.0868 | 2031.4368 | 75.3499 | 2289.9 | 258.4632 | -258.4632 | 2.49% | 12.72% | 2407.7 | 376.2632 | -376.2632 | 3.625% | 18.52% | 12 | 0 | 0 | 0 | 0
2013-02-04 | 13 | 32231.2884 | 1689.8074 | 1749.8047 | 59.9973 | 2071 | 321.1953 | -321.1953 | 3.095% | 18.36% | 2143.3 | 393.4953 | -393.4953 | 3.791% | 22.49% | 13 | 0 | 0 | 0 | 0
2013-02-04 | 14 | 32268.1277 | 2084.1914 | 2097.2131 | 13.0217 | 2259.3 | 162.0869 | -162.0869 | 1.562% | 7.729% | 2334.9 | 237.6869 | -237.6869 | 2.29% | 11.33% | 14 | 0 | 0 | 0 | 0
2013-02-04 | 15 | 32255.3367 | 2424.6632 | 2450.5385 | 25.8753 | 2060 | 390.5385 | 390.5385 | 3.763% | 15.94% | 2141.9 | 308.6385 | 308.6385 | 2.974% | 12.59% | 15 | 1 | 0 | 1 | 1
2013-02-04 | 16 | 32277.3375 | 2613.4128 | 2621.623 | 8.2102 | 2098.5 | 523.123 | 523.123 | 5.04% | 19.95% | 2176.8 | 444.823 | 444.823 | 4.286% | 16.97% | 16 | 1 | 0 | 1 | 1
2013-02-04 | 17 | 32390.3207 | 2421.7103 | 2414.89 | -6.8203 | 2211.5 | 203.39 | 203.39 | 1.96% | 8.422% | 2280.4 | 134.49 | 134.49 | 1.296% | 5.569% | 17 | 1 | 0 | 1 | 1
2013-02-04 | 18 | 32621.8877 | 2216.5702 | 2216.8676 | 0.29735 | 2436.4 | 219.5324 | -219.5324 | 2.115% | 9.903% | 2511.7 | 294.8324 | -294.8324 | 2.841% | 13.3% | 18 | 0 | 0 | 0 | 0
2013-02-04 | 19 | 34330.5697 | 1942.7284 | 1947.8911 | 5.1627 | 2615.2 | 667.3089 | -667.3089 | 6.43% | 34.26% | 2711.9 | 764.0089 | -764.0089 | 7.361% | 39.22% | 19 | 0 | 0 | 0 | 0
2013-02-04 | 20 | 34664.6416 | 1942.1996 | 1958.785 | 16.5853 | 2795.8 | 837.015 | -837.015 | 8.065% | 42.73% | 2894.4 | 935.615 | -935.615 | 9.015% | 47.77% | 20 | 0 | 0 | 0 | 0
2013-02-04 | 21 | 33758.0269 | 1858.6212 | 1875.6864 | 17.0652 | 2969.5 | 1093.8136 | -1093.8136 | 10.54% | 58.32% | 3148.2 | 1272.5136 | -1272.5136 | 12.26% | 67.84% | 21 | 0 | 0 | 0 | 0
2013-02-04 | 22 | 32192.5779 | 1692.4282 | 1703.7297 | 11.3015 | 2694.9 | 991.1703 | -991.1703 | 9.55% | 58.18% | 2805.6 | 1101.8703 | -1101.8703 | 10.62% | 64.67% | 22 | 0 | 0 | 0 | 0
2013-02-04 | 23 | 29499.635 | 1798.4626 | 1804.795 | 6.3324 | 2333.7 | 528.905 | -528.905 | 5.096% | 29.31% | 2410.9 | 606.105 | -606.105 | 5.84% | 33.58% | 23 | 0 | 0 | 0 | 0
2013-02-04 | 24 | 26971.0347 | 1948.6111 | 1946.8059 | -1.8052 | 1774.1 | 172.7059 | 172.7059 | 1.664% | 8.871% | 1927.2 | 19.6059 | 19.6059 | 0.1889% | 1.007% | 24 | 1 | 0 | 1 | 1
2013-02-05 | 1 | 25242.3479 | 1789.8665 | 1787.1869 | -2.6796 | 1423.5 | 363.6869 | 363.6869 | 3.504% | 20.35% | 1575 | 212.1869 | 212.1869 | 2.044% | 11.87% | 1 | 1 | 0 | 1 | 1
2013-02-05 | 2 | 24361.1331 | 1274.8193 | 1278.3024 | 3.4831 | 1249.9 | 28.4024 | 28.4024 | 0.2737% | 2.222% | 1385 | 106.6976 | -106.6976 | 1.028% | 8.347% | 2 | 1 | 0 | 0 | 1
2013-02-05 | 3 | 23958.4144 | 840.7356 | 844.0309 | 3.2954 | 1332.9 | 488.8691 | -488.8691 | 4.71% | 57.92% | 1431.3 | 587.2691 | -587.2691 | 5.659% | 69.58% | 3 | 0 | 0 | 0 | 0
2013-02-05 | 4 | 23934.8524 | 546.9935 | 549.1649 | 2.1714 | 1070.1 | 520.9351 | -520.9351 | 5.019% | 94.86% | 1176.5 | 627.3351 | -627.3351 | 6.045% | 114.2% | 4 | 0 | 0 | 0 | 0
2013-02-05 | 5 | 24570.2447 | 390.4942 | 393.6511 | 3.1569 | 829.9 | 436.2489 | -436.2489 | 4.203% | 110.8% | 920.8 | 527.1489 | -527.1489 | 5.079% | 133.9% | 5 | 0 | 0 | 0 | 0
2013-02-05 | 6 | 26826.795 | 356.8095 | 365.7525 | 8.943 | 727.6 | 361.8475 | -361.8475 | 3.487% | 98.93% | 835.7 | 469.9475 | -469.9475 | 4.528% | 128.5% | 6 | 0 | 0 | 0 | 0
2013-02-05 | 7 | 30875.4234 | 467.8347 | 480.4111 | 12.5763 | 713 | 232.5889 | -232.5889 | 2.241% | 48.41% | 815.1 | 334.6889 | -334.6889 | 3.225% | 69.67% | 7 | 0 | 0 | 0 | 0
2013-02-05 | 8 | 32312.7929 | 538.6193 | 555.4865 | 16.8673 | 944 | 388.5135 | -388.5135 | 3.743% | 69.94% | 994.7 | 439.2135 | -439.2135 | 4.232% | 79.07% | 8 | 0 | 0 | 0 | 0
2013-02-05 | 9 | 31905.7771 | 468.7664 | 483.2921 | 14.5256 | 1006.6 | 523.3079 | -523.3079 | 5.042% | 108.3% | 1024.9 | 541.6079 | -541.6079 | 5.219% | 112.1% | 9 | 0 | 0 | 0 | 0
2013-02-05 | 10 | 32079.6836 | 481.8668 | 496.9967 | 15.1299 | 883.3 | 386.3033 | -386.3033 | 3.722% | 77.73% | 894.8 | 397.8033 | -397.8033 | 3.833% | 80.04% | 10 | 0 | 0 | 0 | 0
2013-02-05 | 11 | 32546.3122 | 315.0159 | 326.932 | 11.916 | 585.9 | 258.968 | -258.968 | 2.495% | 79.21% | 592.7 | 265.768 | -265.768 | 2.561% | 81.29% | 11 | 0 | 0 | 0 | 0
2013-02-05 | 12 | 32851.1331 | 212.7565 | 216.1149 | 3.3584 | 476.5 | 260.3851 | -260.3851 | 2.509% | 120.5% | 492.5 | 276.3851 | -276.3851 | 2.663% | 127.9% | 12 | 0 | 0 | 0 | 0
2013-02-05 | 13 | 33166.4823 | 155.6117 | 162.9123 | 7.3006 | 459.2 | 296.2877 | -296.2877 | 2.855% | 181.9% | 461.5 | 298.5877 | -298.5877 | 2.877% | 183.3% | 13 | 0 | 0 | 0 | 0
2013-02-05 | 14 | 33562.6492 | 135.1685 | 143.8527 | 8.6842 | 368.8 | 224.9473 | -224.9473 | 2.167% | 156.4% | 380.6 | 236.7473 | -236.7473 | 2.281% | 164.6% | 14 | 0 | 0 | 0 | 0
2013-02-05 | 15 | 33750.5329 | 276.9715 | 269.9006 | -7.0709 | 346.9 | 76.9994 | -76.9994 | 0.7419% | 28.53% | 376.6 | 106.6994 | -106.6994 | 1.028% | 39.53% | 15 | 0 | 0 | 0 | 0
2013-02-05 | 16 | 33949.7471 | 528.7421 | 531.4117 | 2.6695 | 394.8 | 136.6117 | 136.6117 | 1.316% | 25.71% | 458.3 | 73.1117 | 73.1117 | 0.7045% | 13.76% | 16 | 1 | 0 | 1 | 1
2013-02-05 | 17 | 34025.0913 | 770.9189 | 782.0844 | 11.1655 | 460.7 | 321.3844 | 321.3844 | 3.097% | 41.09% | 544.9 | 237.1844 | 237.1844 | 2.285% | 30.33% | 17 | 1 | 0 | 1 | 1
2013-02-05 | 18 | 33963.1682 | 788.2129 | 799.2726 | 11.0597 | 875.2 | 75.9274 | -75.9274 | 0.7316% | 9.5% | 984 | 184.7274 | -184.7274 | 1.78% | 23.11% | 18 | 0 | 0 | 0 | 0
2013-02-05 | 19 | 35337.276 | 1154.2942 | 1157.4004 | 3.1062 | 1541.1 | 383.6996 | -383.6996 | 3.697% | 33.15% | 1663.7 | 506.2996 | -506.2996 | 4.878% | 43.74% | 19 | 0 | 0 | 0 | 0
2013-02-05 | 20 | 35542.6911 | 2152.116 | 2164.4325 | 12.3166 | 2090.7 | 73.7325 | 73.7325 | 0.7104% | 3.407% | 2212.7 | 48.2675 | -48.2675 | 0.4651% | 2.23% | 20 | 1 | 0 | 0 | 1
2013-02-05 | 21 | 34737.8211 | 3171.564 | 3206.8321 | 35.2681 | 2549 | 657.8321 | 657.8321 | 6.338% | 20.51% | 2670.9 | 535.9321 | 535.9321 | 5.164% | 16.71% | 21 | 1 | 0 | 1 | 1
2013-02-05 | 22 | 33078.8062 | 3944.2496 | 3992.0898 | 47.8402 | 2990.9 | 1001.1898 | 1001.1898 | 9.647% | 25.08% | 3120.7 | 871.3898 | 871.3898 | 8.396% | 21.83% | 22 | 1 | 0 | 1 | 1
2013-02-05 | 23 | 30498.1686 | 4116.3935 | 4124.8779 | 8.4844 | 3356.6 | 768.2779 | 768.2779 | 7.403% | 18.63% | 3471.2 | 653.6779 | 653.6779 | 6.298% | 15.85% | 23 | 1 | 0 | 1 | 1
2013-02-05 | 24 | 27775.5302 | 4144.9534 | 4147.1953 | 2.2419 | 4043.3 | 103.8953 | 103.8953 | 1.001% | 2.505% | 4110.5 | 36.6953 | 36.6953 | 0.3536% | 0.8848% | 24 | 1 | 0 | 1 | 1
2013-02-06 | 1 | 25925.042 | 3623.6332 | 3627.5148 | 3.8816 | 4235.9 | 608.3852 | -608.3852 | 5.862% | 16.77% | 4171 | 543.4852 | -543.4852 | 5.237% | 14.98% | 1 | 0 | 0 | 0 | 0
2013-02-06 | 2 | 24927.7028 | 3743.8942 | 3746.3413 | 2.4472 | 4188.7 | 442.3587 | -442.3587 | 4.262% | 11.81% | 4174.3 | 427.9587 | -427.9587 | 4.124% | 11.42% | 2 | 0 | 0 | 0 | 0
2013-02-06 | 3 | 24419.9018 | 3671.444 | 3673.9111 | 2.467 | 3667.1 | 6.8111 | 6.8111 | 0.06563% | 0.1854% | 3776 | 102.0889 | -102.0889 | 0.9837% | 2.779% | 3 | 1 | 0 | 0 | 1
2013-02-06 | 4 | 24304.2386 | 3836.9741 | 3837.4178 | 0.44379 | 3327.3 | 510.1178 | 510.1178 | 4.915% | 13.29% | 3422 | 415.4178 | 415.4178 | 4.003% | 10.83% | 4 | 1 | 0 | 1 | 1
2013-02-06 | 5 | 24860.8766 | 4047.776 | 4052.1918 | 4.4158 | 3619.5 | 432.6918 | 432.6918 | 4.169% | 10.68% | 3678.6 | 373.5918 | 373.5918 | 3.6% | 9.219% | 5 | 1 | 0 | 1 | 1
2013-02-06 | 6 | 26954.9423 | 3773.459 | 3785.396 | 11.937 | 3733.6 | 51.796 | 51.796 | 0.4991% | 1.368% | 3798.3 | 12.904 | -12.904 | 0.1243% | 0.3409% | 6 | 1 | 0 | 0 | 1
2013-02-06 | 7 | 30913.6438 | 3436.406 | 3448.4954 | 12.0894 | 3843.9 | 395.4046 | -395.4046 | 3.81% | 11.47% | 3913.8 | 465.3046 | -465.3046 | 4.483% | 13.49% | 7 | 0 | 0 | 0 | 0
2013-02-06 | 8 | 32448.8541 | 3097.205 | 3092.6042 | -4.6009 | 4305.3 | 1212.6958 | -1212.6958 | 11.68% | 39.21% | 4350.4 | 1257.7958 | -1257.7958 | 12.12% | 40.67% | 8 | 0 | 0 | 0 | 0
2013-02-06 | 9 | 32079.9853 | 2677.4008 | 2676.4785 | -0.92223 | 4324.7 | 1648.2215 | -1648.2215 | 15.88% | 61.58% | 4340.2 | 1663.7215 | -1663.7215 | 16.03% | 62.16% | 9 | 0 | 0 | 0 | 0
2013-02-06 | 10 | 32381.66 | 2396.0519 | 2400.7922 | 4.7403 | 3570.5 | 1169.7078 | -1169.7078 | 11.27% | 48.72% | 3578.6 | 1177.8078 | -1177.8078 | 11.35% | 49.06% | 10 | 0 | 0 | 0 | 0
2013-02-06 | 11 | 32746.0646 | 3053.8407 | 3060.6141 | 6.7733 | 2978.8 | 81.8141 | 81.8141 | 0.7883% | 2.673% | 3047.2 | 13.4141 | 13.4141 | 0.1292% | 0.4383% | 11 | 1 | 0 | 1 | 1
2013-02-06 | 12 | 32879.0259 | 2823.2963 | 2843.5418 | 20.2455 | 2570.4 | 273.1418 | 273.1418 | 2.632% | 9.606% | 2669.6 | 173.9418 | 173.9418 | 1.676% | 6.117% | 12 | 1 | 0 | 1 | 1
2013-02-06 | 13 | 32907.044 | 2288.921 | 2299.3689 | 10.4479 | 2457.7 | 158.3311 | -158.3311 | 1.526% | 6.886% | 2553.2 | 253.8311 | -253.8311 | 2.446% | 11.04% | 13 | 0 | 0 | 0 | 0
2013-02-06 | 14 | 33075.5516 | 2041.1339 | 2053.2321 | 12.0981 | 2559.6 | 506.3679 | -506.3679 | 4.879% | 24.66% | 2635.5 | 582.2679 | -582.2679 | 5.61% | 28.36% | 14 | 0 | 0 | 0 | 0
2013-02-06 | 15 | 32979.2423 | 2631.6168 | 2644.109 | 12.4922 | 2133.5 | 510.609 | 510.609 | 4.92% | 19.31% | 2194.7 | 449.409 | 449.409 | 4.33% | 17% | 15 | 1 | 0 | 1 | 1
2013-02-06 | 16 | 32930.4021 | 3316.2815 | 3311.2319 | -5.0496 | 1803.6 | 1507.6319 | 1507.6319 | 14.53% | 45.53% | 1852.6 | 1458.6319 | 1458.6319 | 14.05% | 44.05% | 16 | 1 | 0 | 1 | 1
2013-02-06 | 17 | 32819.386 | 3321.451 | 3326.706 | 5.255 | 1869.3 | 1457.406 | 1457.406 | 14.04% | 43.81% | 1933.9 | 1392.806 | 1392.806 | 13.42% | 41.87% | 17 | 1 | 0 | 1 | 1
2013-02-06 | 18 | 32955.4063 | 2779.9706 | 2786.6249 | 6.6544 | 2034.5 | 752.1249 | 752.1249 | 7.247% | 26.99% | 2113.2 | 673.4249 | 673.4249 | 6.489% | 24.17% | 18 | 1 | 0 | 1 | 1
2013-02-06 | 19 | 34467.0357 | 2119.8275 | 2132.1187 | 12.2912 | 2889.1 | 756.9813 | -756.9813 | 7.294% | 35.5% | 2895.6 | 763.4813 | -763.4813 | 7.356% | 35.81% | 19 | 0 | 0 | 0 | 0
2013-02-06 | 20 | 34642.0874 | 2063.6154 | 2066.5492 | 2.9337 | 3267.6 | 1201.0508 | -1201.0508 | 11.57% | 58.12% | 3501.5 | 1434.9508 | -1434.9508 | 13.83% | 69.44% | 20 | 0 | 1 | 0 | 0
2013-02-06 | 21 | 33795.0075 | 2370.3551 | 2394.1367 | 23.7817 | 3379 | 984.8633 | -984.8633 | 9.489% | 41.14% | 3595.6 | 1201.4633 | -1201.4633 | 11.58% | 50.18% | 21 | 0 | 1 | 0 | 0
2013-02-06 | 22 | 32355.1999 | 2750.0626 | 2831.6407 | 81.5781 | 3409.4 | 577.7593 | -577.7593 | 5.567% | 20.4% | 3654.1 | 822.4593 | -822.4593 | 7.925% | 29.05% | 22 | 0 | 1 | 0 | 0
2013-02-06 | 23 | 29752.8892 | 3479.9252 | 3553.6746 | 73.7494 | 4020.6 | 466.9254 | -466.9254 | 4.499% | 13.14% | 4244.7 | 691.0254 | -691.0254 | 6.658% | 19.45% | 23 | 0 | 1 | 0 | 0
2013-02-06 | 24 | 27142.2329 | 4368.8941 | 4451.7952 | 82.9012 | 4885.7 | 433.9048 | -433.9048 | 4.181% | 9.747% | 5001 | 549.2048 | -549.2048 | 5.292% | 12.34% | 24 | 0 | 0 | 0 | 0
2013-02-07 | 1 | 25347.8937 | 4870.5205 | 5062.8643 | 192.3438 | 4769.8 | 293.0643 | 293.0643 | 2.824% | 5.789% | 4848 | 214.8643 | 214.8643 | 2.07% | 4.244% | 1 | 1 | 0 | 1 | 1
2013-02-07 | 2 | 24457.3209 | 4893.5587 | 5021.3118 | 127.7531 | 5003.8 | 17.5118 | 17.5118 | 0.1687% | 0.3487% | 5064.2 | 42.8882 | -42.8882 | 0.4132% | 0.8541% | 2 | 1 | 0 | 0 | 1
2013-02-07 | 3 | 23984.2033 | 4810.5782 | 4868.0297 | 57.4514 | 5222.5 | 354.4703 | -354.4703 | 3.415% | 7.282% | 5241.4 | 373.3703 | -373.3703 | 3.598% | 7.67% | 3 | 0 | 0 | 0 | 0
2013-02-07 | 4 | 23917.7483 | 4777.0694 | 4859.0503 | 81.9809 | 5422.3 | 563.2497 | -563.2497 | 5.427% | 11.59% | 5455.6 | 596.5497 | -596.5497 | 5.748% | 12.28% | 4 | 0 | 0 | 0 | 0
2013-02-07 | 5 | 24452.3871 | 4608.8987 | 4698.2457 | 89.3471 | 5373.2 | 674.9543 | -674.9543 | 6.503% | 14.37% | 5369.2 | 670.9543 | -670.9543 | 6.465% | 14.28% | 5 | 0 | 0 | 0 | 0
2013-02-07 | 6 | 26437.4943 | 4359.0832 | 4447.6651 | 88.5819 | 5092 | 644.3349 | -644.3349 | 6.208% | 14.49% | 5125.5 | 677.8349 | -677.8349 | 6.531% | 15.24% | 6 | 0 | 0 | 0 | 0
2013-02-07 | 7 | 30348.1355 | 4305.5332 | 4383.7069 | 78.1737 | 5024.8 | 641.0931 | -641.0931 | 6.177% | 14.62% | 5006.6 | 622.8931 | -622.8931 | 6.002% | 14.21% | 7 | 0 | 0 | 0 | 0
2013-02-07 | 8 | 31703.7274 | 4209.2005 | 4298.8149 | 89.6144 | 4685.4 | 386.5851 | -386.5851 | 3.725% | 8.993% | 4685.4 | 386.5851 | -386.5851 | 3.725% | 8.993% | 8 | 0 | 0 | 0 | 0
2013-02-07 | 9 | 31438.4421 | 3672.2759 | 3761.0341 | 88.7582 | 4036.2 | 275.1659 | -275.1659 | 2.651% | 7.316% | 4037.9 | 276.8659 | -276.8659 | 2.668% | 7.361% | 9 | 0 | 0 | 0 | 0
2013-02-07 | 10 | 31789.2742 | 3586.8986 | 3668.6201 | 81.7215 | 3603.5 | 65.1201 | 65.1201 | 0.6275% | 1.775% | 3621.8 | 46.8201 | 46.8201 | 0.4511% | 1.276% | 10 | 1 | 0 | 1 | 1
2013-02-07 | 11 | 32372.5942 | 3949.3464 | 4049.6241 | 100.2777 | 3592.9 | 456.7241 | 456.7241 | 4.401% | 11.28% | 3615 | 434.6241 | 434.6241 | 4.188% | 10.73% | 11 | 1 | 0 | 1 | 1
2013-02-07 | 12 | 32591.5782 | 3309.3661 | 3413.9416 | 104.5755 | 3601.3 | 187.3584 | -187.3584 | 1.805% | 5.488% | 3637.5 | 223.5584 | -223.5584 | 2.154% | 6.548% | 12 | 0 | 0 | 0 | 0
2013-02-07 | 13 | 32822.9764 | 3784.9037 | 3888.8584 | 103.9547 | 3696.7 | 192.1584 | 192.1584 | 1.852% | 4.941% | 3727.5 | 161.3584 | 161.3584 | 1.555% | 4.149% | 13 | 1 | 0 | 1 | 1
2013-02-07 | 14 | 33307.7706 | 4207.1987 | 4296.7575 | 89.5588 | 4036 | 260.7575 | 260.7575 | 2.512% | 6.069% | 4065.4 | 231.3575 | 231.3575 | 2.229% | 5.384% | 14 | 1 | 0 | 1 | 1
2013-02-07 | 15 | 33402.322 | 3974.435 | 4056.0885 | 81.6534 | 3880.5 | 175.5885 | 175.5885 | 1.692% | 4.329% | 3931.9 | 124.1885 | 124.1885 | 1.197% | 3.062% | 15 | 1 | 0 | 1 | 1
2013-02-07 | 16 | 33431.5088 | 4149.6482 | 4231.363 | 81.7149 | 4179.4 | 51.963 | 51.963 | 0.5007% | 1.228% | 4264.8 | 33.437 | -33.437 | 0.3222% | 0.7902% | 16 | 1 | 0 | 0 | 1
2013-02-07 | 17 | 33414.5693 | 4207.1025 | 4271.7606 | 64.6581 | 4087.2 | 184.5606 | 184.5606 | 1.778% | 4.32% | 4210.7 | 61.0606 | 61.0606 | 0.5883% | 1.429% | 17 | 1 | 0 | 1 | 1
2013-02-07 | 18 | 33233.515 | 3731.6461 | 3772.2384 | 40.5923 | 3544.8 | 227.4384 | 227.4384 | 2.191% | 6.029% | 3692.7 | 79.5384 | 79.5384 | 0.7664% | 2.109% | 18 | 1 | 0 | 1 | 1
2013-02-07 | 19 | 34487.0449 | 2986.5092 | 2995.6444 | 9.1353 | 3498.7 | 503.0556 | -503.0556 | 4.847% | 16.79% | 3659.5 | 663.8556 | -663.8556 | 6.396% | 22.16% | 19 | 0 | 0 | 0 | 0
2013-02-07 | 20 | 34883.5663 | 3119.3448 | 3123.6187 | 4.274 | 3600.8 | 477.1813 | -477.1813 | 4.598% | 15.28% | 3787.3 | 663.6813 | -663.6813 | 6.395% | 21.25% | 20 | 0 | 0 | 0 | 0
2013-02-07 | 21 | 34175.7921 | 3453.1871 | 3453.8543 | 0.66726 | 3703.3 | 249.4457 | -249.4457 | 2.403% | 7.222% | 3893 | 439.1457 | -439.1457 | 4.231% | 12.71% | 21 | 0 | 0 | 0 | 0
2013-02-07 | 22 | 32625.4483 | 3357.6651 | 3357.9996 | 0.33451 | 3323.9 | 34.0996 | 34.0996 | 0.3286% | 1.015% | 3532.2 | 174.2004 | -174.2004 | 1.678% | 5.188% | 22 | 1 | 1 | 0 | 1
2013-02-07 | 23 | 30024.5661 | 3370.737 | 3370.7546 | 0.017577 | 3435.3 | 64.5454 | -64.5454 | 0.6219% | 1.915% | 3617.2 | 246.4454 | -246.4454 | 2.375% | 7.311% | 23 | 0 | 0 | 0 | 0
2013-02-07 | 24 | 27368.2718 | 3368.8791 | 3371.022 | 2.1429 | 3704 | 332.978 | -332.978 | 3.208% | 9.878% | 3831.7 | 460.678 | -460.678 | 4.439% | 13.67% | 24 | 0 | 0 | 0 | 0
2013-02-08 | 1 | 25652.9017 | 3478.7096 | 3479.1849 | 0.47532 | 3736.6 | 257.4151 | -257.4151 | 2.48% | 7.399% | 3874.5 | 395.3151 | -395.3151 | 3.809% | 11.36% | 1 | 0 | 0 | 0 | 0
2013-02-08 | 2 | 24683.7991 | 3561.7203 | 3561.8071 | 0.08677 | 3738.7 | 176.8929 | -176.8929 | 1.704% | 4.966% | 3903.5 | 341.6929 | -341.6929 | 3.292% | 9.593% | 2 | 0 | 0 | 0 | 0
2013-02-08 | 3 | 24299.721 | 3797.6023 | 3798.8661 | 1.2639 | 3572.9 | 225.9661 | 225.9661 | 2.177% | 5.948% | 3712.7 | 86.1661 | 86.1661 | 0.8302% | 2.268% | 3 | 1 | 0 | 1 | 1
2013-02-08 | 4 | 24324.7217 | 3944.3567 | 3947.5387 | 3.182 | 3653.3 | 294.2387 | 294.2387 | 2.835% | 7.454% | 3776.9 | 170.6387 | 170.6387 | 1.644% | 4.323% | 4 | 1 | 0 | 1 | 1
2013-02-08 | 5 | 25032.3177 | 3969.6774 | 3969.9061 | 0.22873 | 3670 | 299.9061 | 299.9061 | 2.89% | 7.554% | 3793.1 | 176.8061 | 176.8061 | 1.704% | 4.454% | 5 | 1 | 0 | 1 | 1
2013-02-08 | 6 | 27370.2614 | 3792.7036 | 3799.5622 | 6.8587 | 3608.9 | 190.6622 | 190.6622 | 1.837% | 5.018% | 3722.8 | 76.7622 | 76.7622 | 0.7396% | 2.02% | 6 | 1 | 0 | 1 | 1
2013-02-08 | 7 | 31760.9368 | 3734.3304 | 3743.4438 | 9.1134 | 3531.2 | 212.2438 | 212.2438 | 2.045% | 5.67% | 3688.4 | 55.0438 | 55.0438 | 0.5304% | 1.47% | 7 | 1 | 0 | 1 | 1
2013-02-08 | 8 | 33241.7953 | 3385.5765 | 3375.0727 | -10.5038 | 3394 | 18.9273 | -18.9273 | 0.1824% | 0.5608% | 3563.2 | 188.1273 | -188.1273 | 1.813% | 5.574% | 8 | 0 | 0 | 0 | 0
2013-02-08 | 9 | 32861.3686 | 2484.923 | 2464.2731 | -20.6499 | 2859.8 | 395.5269 | -395.5269 | 3.811% | 16.05% | 3034.2 | 569.9269 | -569.9269 | 5.491% | 23.13% | 9 | 0 | 0 | 0 | 0
2013-02-08 | 10 | 32809.2171 | 1705.7463 | 1702.735 | -3.0113 | 2476.5 | 773.765 | -773.765 | 7.455% | 45.44% | 2608.9 | 906.165 | -906.165 | 8.731% | 53.22% | 10 | 0 | 0 | 0 | 0
2013-02-08 | 11 | 32650.4938 | 1606.9479 | 1599.1577 | -7.7902 | 2442.8 | 843.6423 | -843.6423 | 8.129% | 52.76% | 2566 | 966.8423 | -966.8423 | 9.316% | 60.46% | 11 | 0 | 0 | 0 | 0
2013-02-08 | 12 | 32294.5245 | 1460.7497 | 1453.9253 | -6.8244 | 2024.7 | 570.7747 | -570.7747 | 5.5% | 39.26% | 2217.9 | 763.9747 | -763.9747 | 7.361% | 52.55% | 12 | 0 | 0 | 0 | 0
2013-02-08 | 13 | 31818.1137 | 1270.2105 | 1268.9152 | -1.2952 | 1649.5 | 380.5848 | -380.5848 | 3.667% | 29.99% | 1770.7 | 501.7848 | -501.7848 | 4.835% | 39.54% | 13 | 0 | 0 | 0 | 0
2013-02-08 | 14 | 31803.0493 | 1179.2044 | 1193.0865 | 13.8821 | 1752 | 558.9135 | -558.9135 | 5.385% | 46.85% | 1845.1 | 652.0135 | -652.0135 | 6.282% | 54.65% | 14 | 0 | 0 | 0 | 0
2013-02-08 | 15 | 31645.9608 | 1296.2292 | 1311.0909 | 14.8617 | 1762.6 | 451.5091 | -451.5091 | 4.35% | 34.44% | 1783.8 | 472.7091 | -472.7091 | 4.555% | 36.05% | 15 | 0 | 0 | 0 | 0
2013-02-08 | 16 | 31433.4554 | 1610.1605 | 1609.3756 | -0.78484 | 2000.9 | 391.5244 | -391.5244 | 3.772% | 24.33% | 2029.3 | 419.9244 | -419.9244 | 4.046% | 26.09% | 16 | 0 | 0 | 0 | 0
2013-02-08 | 17 | 31310.2462 | 2186.6664 | 2188.2553 | 1.5889 | 2247.8 | 59.5447 | -59.5447 | 0.5737% | 2.721% | 2331.8 | 143.5447 | -143.5447 | 1.383% | 6.56% | 17 | 0 | 0 | 0 | 0
2013-02-08 | 18 | 31164.1501 | 2609.4316 | 2610.215 | 0.78338 | 2396.4 | 213.815 | 213.815 | 2.06% | 8.191% | 2495.1 | 115.115 | 115.115 | 1.109% | 4.41% | 18 | 1 | 0 | 1 | 1
2013-02-08 | 19 | 32539.0751 | 2565.4722 | 2568.5242 | 3.052 | 2834.5 | 265.9758 | -265.9758 | 2.563% | 10.36% | 2910.9 | 342.3758 | -342.3758 | 3.299% | 13.33% | 19 | 0 | 0 | 0 | 0
2013-02-08 | 20 | 32794.6821 | 3069.92 | 3076.3646 | 6.4446 | 3603.4 | 527.0354 | -527.0354 | 5.078% | 17.13% | 3693.5 | 617.1354 | -617.1354 | 5.946% | 20.06% | 20 | 0 | 0 | 0 | 0
2013-02-08 | 21 | 32238.5375 | 4125.6482 | 4162.4754 | 36.8272 | 4323.7 | 161.2246 | -161.2246 | 1.553% | 3.873% | 4417.1 | 254.6246 | -254.6246 | 2.453% | 6.117% | 21 | 0 | 0 | 0 | 0
2013-02-08 | 22 | 31371.2466 | 4921.1336 | 5007.392 | 86.2583 | 4591.3 | 416.092 | 416.092 | 4.009% | 8.31% | 4706.3 | 301.092 | 301.092 | 2.901% | 6.013% | 22 | 1 | 0 | 1 | 1
2013-02-08 | 23 | 29931.9508 | 5831.402 | 5912.9687 | 81.5667 | 5158.7 | 754.2687 | 754.2687 | 7.268% | 12.76% | 5314.8 | 598.1687 | 598.1687 | 5.764% | 10.12% | 23 | 1 | 0 | 1 | 1
2013-02-08 | 24 | 28156.3442 | 6560.2477 | 6623.7785 | 63.5308 | 5781.9 | 841.8785 | 841.8785 | 8.112% | 12.71% | 5939.1 | 684.6785 | 684.6785 | 6.597% | 10.34% | 24 | 1 | 0 | 1 | 1
2013-02-09 | 1 | 26746.2565 | 6498.6347 | 6576.8002 | 78.1655 | 6208.3 | 368.5002 | 368.5002 | 3.551% | 5.603% | 6341.6 | 235.2002 | 235.2002 | 2.266% | 3.576% | 1 | 1 | 0 | 1 | 1
2013-02-09 | 2 | 25916.2932 | 6734.0204 | 6825.5516 | 91.5312 | 6659.6 | 165.9516 | 165.9516 | 1.599% | 2.431% | 6757 | 68.5516 | 68.5516 | 0.6605% | 1.004% | 2 | 1 | 0 | 1 | 1
2013-02-09 | 3 | 25481.2976 | 6966.4739 | 7129.0606 | 162.5867 | 7080.7 | 48.3606 | 48.3606 | 0.466% | 0.6784% | 7171.4 | 42.3394 | -42.3394 | 0.408% | 0.5939% | 3 | 1 | 0 | 0 | 1
2013-02-09 | 4 | 25275.6193 | 6971.464 | 7209.1939 | 237.7299 | 7356.4 | 147.2061 | -147.2061 | 1.418% | 2.042% | 7429.9 | 220.7061 | -220.7061 | 2.127% | 3.061% | 4 | 0 | 0 | 0 | 0
2013-02-09 | 5 | 25472.0603 | 7129.6311 | 7182.4698 | 52.8386 | 7476.9 | 294.4302 | -294.4302 | 2.837% | 4.099% | 7573.4 | 390.9302 | -390.9302 | 3.767% | 5.443% | 5 | 0 | 0 | 0 | 0
2013-02-09 | 6 | 26332.4562 | 7211.3343 | 7308.2703 | 96.936 | 7638.3 | 330.0297 | -330.0297 | 3.18% | 4.516% | 7751.5 | 443.2297 | -443.2297 | 4.271% | 6.065% | 6 | 0 | 0 | 0 | 0
2013-02-09 | 7 | 27852.6056 | 7313.9236 | 7408.5101 | 94.5864 | 7734.1 | 325.5899 | -325.5899 | 3.137% | 4.395% | 7846.8 | 438.2899 | -438.2899 | 4.223% | 5.916% | 7 | 0 | 0 | 0 | 0
2013-02-09 | 8 | 29232.4853 | 7373.215 | 7451.5629 | 78.3479 | 7682.1 | 230.5371 | -230.5371 | 2.221% | 3.094% | 7818.4 | 366.8371 | -366.8371 | 3.535% | 4.923% | 8 | 0 | 0 | 0 | 0
2013-02-09 | 9 | 30753.0811 | 7495.6746 | 7545.9575 | 50.2829 | 7787.5 | 241.5425 | -241.5425 | 2.327% | 3.201% | 7899 | 353.0425 | -353.0425 | 3.402% | 4.679% | 9 | 0 | 0 | 0 | 0
2013-02-09 | 10 | 32056.2716 | 7719.0917 | 7755.5476 | 36.4559 | 7996.3 | 240.7524 | -240.7524 | 2.32% | 3.104% | 8111.6 | 356.0524 | -356.0524 | 3.431% | 4.591% | 10 | 0 | 0 | 0 | 0
2013-02-09 | 11 | 32751.4603 | 7958.8734 | 7992.3402 | 33.4667 | 8007.3 | 14.9598 | -14.9598 | 0.1441% | 0.1872% | 8146.1 | 153.7598 | -153.7598 | 1.482% | 1.924% | 11 | 0 | 0 | 0 | 0
2013-02-09 | 12 | 32822.7783 | 8143.3364 | 8253.9319 | 110.5956 | 8127.7 | 126.2319 | 126.2319 | 1.216% | 1.529% | 8252.7 | 1.2319 | 1.2319 | 0.01187% | 0.01493% | 12 | 1 | 0 | 1 | 1
2013-02-09 | 13 | 32520.2619 | 8175.6932 | 8370.7173 | 195.0241 | 8166.9 | 203.8173 | 203.8173 | 1.964% | 2.435% | 8318.8 | 51.9173 | 51.9173 | 0.5002% | 0.6202% | 13 | 1 | 0 | 1 | 1
2013-02-09 | 14 | 32012.2157 | 8336.0705 | 8496.8283 | 160.7578 | 8359.4 | 137.4283 | 137.4283 | 1.324% | 1.617% | 8548.6 | 51.7717 | -51.7717 | 0.4988% | 0.6093% | 14 | 1 | 0 | 0 | 1
2013-02-09 | 15 | 31745.1077 | 8342.6684 | 8521.2482 | 178.5798 | 8388.9 | 132.3482 | 132.3482 | 1.275% | 1.553% | 8574.3 | 53.0518 | -53.0518 | 0.5112% | 0.6226% | 15 | 1 | 0 | 0 | 1
2013-02-09 | 16 | 31624.1969 | 8294.173 | 8475.1879 | 181.0148 | 8450.4 | 24.7879 | 24.7879 | 0.2388% | 0.2925% | 8678.4 | 203.2121 | -203.2121 | 1.958% | 2.398% | 16 | 1 | 1 | 0 | 1
2013-02-09 | 17 | 31888.0463 | 8385.0973 | 8524.2439 | 139.1465 | 8230.8 | 293.4439 | 293.4439 | 2.827% | 3.442% | 8479.1 | 45.1439 | 45.1439 | 0.435% | 0.5296% | 17 | 1 | 1 | 1 | 1
2013-02-09 | 18 | 32599.5027 | 8421.9493 | 8489.4419 | 67.4926 | 8044.1 | 445.3419 | 445.3419 | 4.291% | 5.246% | 8325.5 | 163.9419 | 163.9419 | 1.58% | 1.931% | 18 | 1 | 1 | 1 | 1
2013-02-09 | 19 | 33865.5417 | 8407.6902 | 8462.8834 | 55.1932 | 8142.5 | 320.3834 | 320.3834 | 3.087% | 3.786% | 8427.2 | 35.6834 | 35.6834 | 0.3438% | 0.4216% | 19 | 1 | 1 | 1 | 1
2013-02-09 | 20 | 33739.6155 | 8526.8431 | 8594.4452 | 67.6021 | 8274.3 | 320.1452 | 320.1452 | 3.085% | 3.725% | 8567.4 | 27.0452 | 27.0452 | 0.2606% | 0.3147% | 20 | 1 | 1 | 1 | 1
2013-02-09 | 21 | 32953.6341 | 8241.2146 | 8299.4275 | 58.2128 | 8045 | 254.4275 | 254.4275 | 2.451% | 3.066% | 8342.9 | 43.4725 | -43.4725 | 0.4189% | 0.5238% | 21 | 1 | 1 | 0 | 1
2013-02-09 | 22 | 31836.251 | 7346.7211 | 7379.3771 | 32.656 | 7507.5 | 128.1229 | -128.1229 | 1.235% | 1.736% | 7847.3 | 467.9229 | -467.9229 | 4.509% | 6.341% | 22 | 0 | 1 | 0 | 0
2013-02-09 | 23 | 30186.2783 | 6623.5242 | 6651.7389 | 28.2148 | 7246 | 594.2611 | -594.2611 | 5.726% | 8.934% | 7589.4 | 937.6611 | -937.6611 | 9.035% | 14.1% | 23 | 0 | 1 | 0 | 0
2013-02-09 | 24 | 28311.0593 | 6600.7607 | 6644.7739 | 44.0133 | 7167 | 522.2261 | -522.2261 | 5.032% | 7.859% | 7461.1 | 816.3261 | -816.3261 | 7.866% | 12.29% | 24 | 0 | 1 | 0 | 0
2013-02-10 | 1 | 26712.4644 | 6869.3889 | 6900.8414 | 31.4525 | 6804.5 | 96.3414 | 96.3414 | 0.9283% | 1.396% | 7006.4 | 105.5586 | -105.5586 | 1.017% | 1.53% | 1 | 1 | 0 | 0 | 1
2013-02-10 | 2 | 25516.4264 | 6450.4008 | 6504.636 | 54.2351 | 6421.1 | 83.536 | 83.536 | 0.8049% | 1.284% | 6636.3 | 131.664 | -131.664 | 1.269% | 2.024% | 2 | 1 | 1 | 0 | 1
2013-02-10 | 3 | 24825.1621 | 6539.8304 | 6594.126 | 54.2956 | 6218.1 | 376.026 | 376.026 | 3.623% | 5.702% | 6488.5 | 105.626 | 105.626 | 1.018% | 1.602% | 3 | 1 | 1 | 1 | 1
2013-02-10 | 4 | 24532.2155 | 6426.271 | 6483.1583 | 56.8873 | 6405.3 | 77.8583 | 77.8583 | 0.7502% | 1.201% | 6707.1 | 223.9417 | -223.9417 | 2.158% | 3.454% | 4 | 1 | 1 | 0 | 1
2013-02-10 | 5 | 24485.119 | 6291.0743 | 6356.3449 | 65.2707 | 6401.5 | 45.1551 | -45.1551 | 0.4351% | 0.7104% | 6619.7 | 263.3551 | -263.3551 | 2.538% | 4.143% | 5 | 0 | 1 | 0 | 0
2013-02-10 | 6 | 24893.8244 | 6228.7277 | 6293.4695 | 64.7418 | 6593.4 | 299.9305 | -299.9305 | 2.89% | 4.766% | 6785.8 | 492.3305 | -492.3305 | 4.744% | 7.823% | 6 | 0 | 0 | 0 | 0
2013-02-10 | 7 | 25580.1285 | 6074.666 | 6125.4961 | 50.8301 | 6570.9 | 445.4039 | -445.4039 | 4.292% | 7.271% | 6737.5 | 612.0039 | -612.0039 | 5.897% | 9.991% | 7 | 0 | 0 | 0 | 0
2013-02-10 | 8 | 26482.9648 | 5702.0088 | 5752.9998 | 50.991 | 6400.5 | 647.5002 | -647.5002 | 6.239% | 11.26% | 6590.8 | 837.8002 | -837.8002 | 8.072% | 14.56% | 8 | 0 | 0 | 0 | 0
2013-02-10 | 9 | 27924.1473 | 5275.2573 | 5317.3209 | 42.0635 | 5769.7 | 452.3791 | -452.3791 | 4.359% | 8.508% | 5978.8 | 661.4791 | -661.4791 | 6.374% | 12.44% | 9 | 0 | 1 | 0 | 0
2013-02-10 | 10 | 29338.3127 | 5984.6903 | 6010.7354 | 26.0451 | 5229 | 781.7354 | 781.7354 | 7.532% | 13.01% | 5385.4 | 625.3354 | 625.3354 | 6.025% | 10.4% | 10 | 1 | 0 | 1 | 1
2013-02-10 | 11 | 30081.0474 | 5782.9963 | 5808.6325 | 25.6362 | 4739.1 | 1069.5325 | 1069.5325 | 10.31% | 18.41% | 4860.4 | 948.2325 | 948.2325 | 9.137% | 16.32% | 11 | 1 | 0 | 1 | 1
2013-02-10 | 12 | 30003.0742 | 4548.8174 | 4561.8845 | 13.0672 | 4322.1 | 239.7845 | 239.7845 | 2.31% | 5.256% | 4376.4 | 185.4845 | 185.4845 | 1.787% | 4.066% | 12 | 1 | 0 | 1 | 1
2013-02-10 | 13 | 29897.6551 | 3737.0958 | 3737.9493 | 0.8535 | 4178.2 | 440.2507 | -440.2507 | 4.242% | 11.78% | 4230.9 | 492.9507 | -492.9507 | 4.75% | 13.19% | 13 | 0 | 0 | 0 | 0
2013-02-10 | 14 | 29644.0652 | 3488.7381 | 3476.2158 | -12.5223 | 4208.7 | 732.4842 | -732.4842 | 7.058% | 21.07% | 4233.2 | 756.9842 | -756.9842 | 7.294% | 21.78% | 14 | 0 | 0 | 0 | 0
2013-02-10 | 15 | 29289.443 | 2985.4122 | 2979.0988 | -6.3134 | 3678.3 | 699.2012 | -699.2012 | 6.737% | 23.47% | 3716.5 | 737.4012 | -737.4012 | 7.105% | 24.75% | 15 | 0 | 0 | 0 | 0
2013-02-10 | 16 | 29062.7799 | 2571.5699 | 2577.9871 | 6.4172 | 3132.1 | 554.1129 | -554.1129 | 5.339% | 21.49% | 3176.4 | 598.4129 | -598.4129 | 5.766% | 23.21% | 16 | 0 | 0 | 0 | 0
2013-02-10 | 17 | 29112.732 | 2139.8524 | 2130.8084 | -9.044 | 2937.1 | 806.2916 | -806.2916 | 7.769% | 37.84% | 2969.8 | 838.9916 | -838.9916 | 8.084% | 39.37% | 17 | 0 | 0 | 0 | 0
2013-02-10 | 18 | 29819.7887 | 1757.9852 | 1748.7542 | -9.231 | 2173.7 | 424.9458 | -424.9458 | 4.094% | 24.3% | 2259 | 510.2458 | -510.2458 | 4.916% | 29.18% | 18 | 0 | 0 | 0 | 0
2013-02-10 | 19 | 31933.4953 | 1168.0728 | 1173.4026 | 5.3298 | 1956 | 782.5974 | -782.5974 | 7.541% | 66.69% | 2119.3 | 945.8974 | -945.8974 | 9.114% | 80.61% | 19 | 0 | 0 | 0 | 0
2013-02-10 | 20 | 32804.3336 | 935.6593 | 949.3263 | 13.6669 | 1669.7 | 720.3737 | -720.3737 | 6.941% | 75.88% | 1838.8 | 889.4737 | -889.4737 | 8.57% | 93.7% | 20 | 0 | 0 | 0 | 0
2013-02-10 | 21 | 32226.7038 | 690.6573 | 700.6417 | 9.9844 | 1487.2 | 786.5583 | -786.5583 | 7.579% | 112.3% | 1651.7 | 951.0583 | -951.0583 | 9.164% | 135.7% | 21 | 0 | 0 | 0 | 0
2013-02-10 | 22 | 31216.1287 | 529.4312 | 536.5122 | 7.081 | 1260.3 | 723.7878 | -723.7878 | 6.974% | 134.9% | 1438.4 | 901.8878 | -901.8878 | 8.69% | 168.1% | 22 | 0 | 0 | 0 | 0
2013-02-10 | 23 | 29346.2102 | 350.0362 | 363.9087 | 13.8726 | 1364.2 | 1000.2913 | -1000.2913 | 9.638% | 274.9% | 1542.6 | 1178.6913 | -1178.6913 | 11.36% | 323.9% | 23 | 0 | 0 | 0 | 0
2013-02-10 | 24 | 27240.3691 | 390.5262 | 406.8878 | 16.3617 | 1390.7 | 983.8122 | -983.8122 | 9.479% | 241.8% | 1557 | 1150.1122 | -1150.1122 | 11.08% | 282.7% | 24 | 0 | 0 | 0 | 0
2013-02-11 | 1 | 25689.441 | 536.8234 | 556.6251 | 19.8017 | 1925.4 | 1368.7749 | -1368.7749 | 13.19% | 245.9% | 2107.5 | 1550.8749 | -1550.8749 | 14.94% | 278.6% | 1 | 0 | 0 | 0 | 0
2013-02-11 | 2 | 24808.1212 | 757.9784 | 778.1881 | 20.2097 | 1943.9 | 1165.7119 | -1165.7119 | 11.23% | 149.8% | 2151.8 | 1373.6119 | -1373.6119 | 13.24% | 176.5% | 2 | 0 | 1 | 0 | 0
2013-02-11 | 3 | 24465.6573 | 1221.9155 | 1235.3615 | 13.446 | 1865.8 | 630.4385 | -630.4385 | 6.074% | 51.03% | 2124.5 | 889.1385 | -889.1385 | 8.567% | 71.97% | 3 | 0 | 1 | 0 | 0
2013-02-11 | 4 | 24533.2269 | 1415.3844 | 1420.1413 | 4.7569 | 2192 | 771.8587 | -771.8587 | 7.437% | 54.35% | 2474.3 | 1054.1587 | -1054.1587 | 10.16% | 74.23% | 4 | 0 | 1 | 0 | 0
2013-02-11 | 5 | 25420.966 | 1642.9822 | 1646.7922 | 3.81 | 2554.7 | 907.9078 | -907.9078 | 8.748% | 55.13% | 2791.4 | 1144.6078 | -1144.6078 | 11.03% | 69.51% | 5 | 0 | 1 | 0 | 0
2013-02-11 | 6 | 27964.07 | 1791.2217 | 1793.2962 | 2.0745 | 3008.3 | 1215.0038 | -1215.0038 | 11.71% | 67.75% | 3199.6 | 1406.3038 | -1406.3038 | 13.55% | 78.42% | 6 | 0 | 0 | 0 | 0
2013-02-11 | 7 | 32131.3857 | 2067.6166 | 2073.8874 | 6.2708 | 2871.1 | 797.2126 | -797.2126 | 7.681% | 38.44% | 3076.3 | 1002.4126 | -1002.4126 | 9.659% | 48.33% | 7 | 0 | 0 | 0 | 0
2013-02-11 | 8 | 33672.0568 | 2560.044 | 2571.1315 | 11.0875 | 2966.6 | 395.4685 | -395.4685 | 3.81% | 15.38% | 3168.8 | 597.6685 | -597.6685 | 5.759% | 23.25% | 8 | 0 | 0 | 0 | 0
2013-02-11 | 9 | 33289.7412 | 2366.729 | 2370.3175 | 3.5885 | 2626 | 255.6825 | -255.6825 | 2.464% | 10.79% | 2773.6 | 403.2825 | -403.2825 | 3.886% | 17.01% | 9 | 0 | 0 | 0 | 0
2013-02-11 | 10 | 33557.5626 | 2170.7583 | 2174.9785 | 4.2202 | 2365 | 190.0215 | -190.0215 | 1.831% | 8.737% | 2465.3 | 290.3215 | -290.3215 | 2.797% | 13.35% | 10 | 0 | 0 | 0 | 0
2013-02-11 | 11 | 33879.2156 | 2238.8604 | 2254.3801 | 15.5197 | 2249.6 | 4.7801 | 4.7801 | 0.04606% | 0.212% | 2326 | 71.6199 | -71.6199 | 0.6901% | 3.177% | 11 | 1 | 0 | 0 | 1
2013-02-11 | 12 | 33901.4716 | 1919.2083 | 1921.0084 | 1.8001 | 2249 | 327.9916 | -327.9916 | 3.16% | 17.07% | 2314.5 | 393.4916 | -393.4916 | 3.791% | 20.48% | 12 | 0 | 0 | 0 | 0
2013-02-11 | 13 | 33746.3065 | 1727.898 | 1727.1438 | -0.75419 | 2160.6 | 433.4562 | -433.4562 | 4.176% | 25.1% | 2186.9 | 459.7562 | -459.7562 | 4.43% | 26.62% | 13 | 0 | 0 | 0 | 0
2013-02-11 | 14 | 33503.0394 | 1728.684 | 1728.1907 | -0.49328 | 2318.7 | 590.5093 | -590.5093 | 5.69% | 34.17% | 2342.3 | 614.1093 | -614.1093 | 5.917% | 35.53% | 14 | 0 | 0 | 0 | 0
2013-02-11 | 15 | 33200.0726 | 2016.1433 | 2015.3584 | -0.78489 | 2449.4 | 434.0416 | -434.0416 | 4.182% | 21.54% | 2482 | 466.6416 | -466.6416 | 4.496% | 23.15% | 15 | 0 | 0 | 0 | 0
2013-02-11 | 16 | 33250.6828 | 2531.006 | 2521.6891 | -9.3169 | 2637.5 | 115.8109 | -115.8109 | 1.116% | 4.593% | 2695 | 173.3109 | -173.3109 | 1.67% | 6.873% | 16 | 0 | 0 | 0 | 0
2013-02-11 | 17 | 33718.4298 | 2829.9179 | 2829.4806 | -0.43724 | 3063.4 | 233.9194 | -233.9194 | 2.254% | 8.267% | 3154.5 | 325.0194 | -325.0194 | 3.132% | 11.49% | 17 | 0 | 0 | 0 | 0
2013-02-11 | 18 | 34752.9411 | 3196.3289 | 3191.6932 | -4.6357 | 3735.3 | 543.6068 | -543.6068 | 5.238% | 17.03% | 3820 | 628.3068 | -628.3068 | 6.054% | 19.69% | 18 | 0 | 0 | 0 | 0
2013-02-11 | 19 | 36621.9642 | 3527.5589 | 3528.5208 | 0.96189 | 4021.6 | 493.0792 | -493.0792 | 4.751% | 13.97% | 4159.4 | 630.8792 | -630.8792 | 6.079% | 17.88% | 19 | 0 | 0 | 0 | 0
2013-02-11 | 20 | 36875.0323 | 4393.6386 | 4394.0507 | 0.41211 | 4321.6 | 72.4507 | 72.4507 | 0.6981% | 1.649% | 4464.8 | 70.7493 | -70.7493 | 0.6817% | 1.61% | 20 | 1 | 0 | 0 | 1
2013-02-11 | 21 | 36180.3594 | 5125.2685 | 5128.8097 | 3.5411 | 4328 | 800.8097 | 800.8097 | 7.716% | 15.61% | 4488.9 | 639.9097 | 639.9097 | 6.166% | 12.48% | 21 | 1 | 0 | 1 | 1
2013-02-11 | 22 | 34728.1546 | 4932.2911 | 4934.3592 | 2.068 | 4411.8 | 522.5592 | 522.5592 | 5.035% | 10.59% | 4563.1 | 371.2592 | 371.2592 | 3.577% | 7.524% | 22 | 1 | 0 | 1 | 1
2013-02-11 | 23 | 32115.6642 | 4066.7664 | 4067.2471 | 0.48077 | 3651.4 | 415.8471 | 415.8471 | 4.007% | 10.22% | 3731 | 336.2471 | 336.2471 | 3.24% | 8.267% | 23 | 1 | 0 | 1 | 1
2013-02-11 | 24 | 29530.0254 | 3701.3846 | 3705.7464 | 4.3618 | 3555.7 | 150.0464 | 150.0464 | 1.446% | 4.049% | 3574.6 | 131.1464 | 131.1464 | 1.264% | 3.539% | 24 | 1 | 0 | 1 | 1
2013-02-12 | 1 | 28003.6685 | 4007.7548 | 4007.7653 | 0.010483 | 3133.4 | 874.3653 | 874.3653 | 8.425% | 21.82% | 3141.5 | 866.2653 | 866.2653 | 8.347% | 21.61% | 1 | 1 | 0 | 1 | 1
2013-02-12 | 2 | 27232.602 | 3556.0291 | 3561.0299 | 5.0008 | 2923 | 638.0299 | 638.0299 | 6.148% | 17.92% | 2897.2 | 663.8299 | 663.8299 | 6.396% | 18.64% | 2 | 1 | 0 | 1 | 1
2013-02-12 | 3 | 26763.9437 | 2167.4082 | 2172.1019 | 4.6938 | 3212.3 | 1040.1981 | -1040.1981 | 10.02% | 47.89% | 3216.8 | 1044.6981 | -1044.6981 | 10.07% | 48.1% | 3 | 0 | 0 | 0 | 0
2013-02-12 | 4 | 26704.3768 | 1634.0379 | 1638.7876 | 4.7497 | 3240.2 | 1601.4124 | -1601.4124 | 15.43% | 97.72% | 3214.3 | 1575.5124 | -1575.5124 | 15.18% | 96.14% | 4 | 0 | 0 | 0 | 0
2013-02-12 | 5 | 27461.1978 | 1272.1275 | 1278.542 | 6.4145 | 3178.5 | 1899.958 | -1899.958 | 18.31% | 148.6% | 3153 | 1874.458 | -1874.458 | 18.06% | 146.6% | 5 | 0 | 0 | 0 | 0
2013-02-12 | 6 | 29893.3656 | 1190.9187 | 1195.5679 | 4.6492 | 2399.8 | 1204.2321 | -1204.2321 | 11.6% | 100.7% | 2398.8 | 1203.2321 | -1203.2321 | 11.59% | 100.6% | 6 | 0 | 0 | 0 | 0
2013-02-12 | 7 | 33924.7332 | 1145.1503 | 1172.1794 | 27.0291 | 2302.2 | 1130.0206 | -1130.0206 | 10.89% | 96.4% | 2292.2 | 1120.0206 | -1120.0206 | 10.79% | 95.55% | 7 | 0 | 0 | 0 | 0
2013-02-12 | 8 | 35146.9436 | 1180.8799 | 1215.8593 | 34.9794 | 2293.4 | 1077.5407 | -1077.5407 | 10.38% | 88.62% | 2311.7 | 1095.8407 | -1095.8407 | 10.56% | 90.13% | 8 | 0 | 0 | 0 | 0
2013-02-12 | 9 | 34539.0495 | 1151.6455 | 1213.8852 | 62.2398 | 2645.6 | 1431.7148 | -1431.7148 | 13.8% | 117.9% | 2676.1 | 1462.2148 | -1462.2148 | 14.09% | 120.5% | 9 | 0 | 0 | 0 | 0
2013-02-12 | 10 | 34588.9481 | 1175.68 | 1247.9717 | 72.2917 | 2936.6 | 1688.6283 | -1688.6283 | 16.27% | 135.3% | 2976.2 | 1728.2283 | -1728.2283 | 16.65% | 138.5% | 10 | 0 | 0 | 0 | 0
2013-02-12 | 11 | 34595.9706 | 1792.3199 | 1990.1478 | 197.8279 | 3585.6 | 1595.4522 | -1595.4522 | 15.37% | 80.17% | 3620.9 | 1630.7522 | -1630.7522 | 15.71% | 81.94% | 11 | 0 | 0 | 0 | 0
2013-02-12 | 12 | 34308.2166 | 2680.4839 | 2860.2429 | 179.7589 | 3313.3 | 453.0571 | -453.0571 | 4.365% | 15.84% | 3379.6 | 519.3571 | -519.3571 | 5.004% | 18.16% | 12 | 0 | 0 | 0 | 0
2013-02-12 | 13 | 33985.7947 | 3275.9997 | 3431.3775 | 155.3777 | 3148 | 283.3775 | 283.3775 | 2.73% | 8.258% | 3253.5 | 177.8775 | 177.8775 | 1.714% | 5.184% | 13 | 1 | 0 | 1 | 1
2013-02-12 | 14 | 33822.6611 | 3901.1658 | 3930.1931 | 29.0273 | 3496.4 | 433.7931 | 433.7931 | 4.18% | 11.04% | 3576.9 | 353.2931 | 353.2931 | 3.404% | 8.989% | 14 | 1 | 0 | 1 | 1
2013-02-12 | 15 | 33444.8508 | 4339.6003 | 4364.6342 | 25.0338 | 4092.2 | 272.4342 | 272.4342 | 2.625% | 6.242% | 4176.3 | 188.3342 | 188.3342 | 1.815% | 4.315% | 15 | 1 | 0 | 1 | 1
2013-02-12 | 16 | 33324.5378 | 5272.8135 | 5362.7354 | 89.9219 | 4642.3 | 720.4354 | 720.4354 | 6.942% | 13.43% | 4793.4 | 569.3354 | 569.3354 | 5.486% | 10.62% | 16 | 1 | 0 | 1 | 1
2013-02-12 | 17 | 33595.7289 | 6160.2241 | 6265.2291 | 105.005 | 5158.6 | 1106.6291 | 1106.6291 | 10.66% | 17.66% | 5282.5 | 982.7291 | 982.7291 | 9.469% | 15.69% | 17 | 1 | 0 | 1 | 1
2013-02-12 | 18 | 34235.3389 | 6317.7065 | 6335.3967 | 17.6902 | 4555 | 1780.3967 | 1780.3967 | 17.15% | 28.1% | 4770.2 | 1565.1967 | 1565.1967 | 15.08% | 24.71% | 18 | 1 | 1 | 1 | 1
2013-02-12 | 19 | 35930.1337 | 5207.092 | 5218.2217 | 11.1297 | 4699 | 519.2217 | 519.2217 | 5.003% | 9.95% | 4841 | 377.2217 | 377.2217 | 3.635% | 7.229% | 19 | 1 | 0 | 1 | 1
2013-02-12 | 20 | 36579.0059 | 4449.3247 | 4459.9631 | 10.6384 | 4600 | 140.0369 | -140.0369 | 1.349% | 3.14% | 4755.5 | 295.5369 | -295.5369 | 2.848% | 6.626% | 20 | 0 | 0 | 0 | 0
2013-02-12 | 21 | 36084.0069 | 3696.7921 | 3708.3428 | 11.5506 | 4492.4 | 784.0572 | -784.0572 | 7.555% | 21.14% | 4654.5 | 946.1572 | -946.1572 | 9.117% | 25.51% | 21 | 0 | 0 | 0 | 0
2013-02-12 | 22 | 34749.6724 | 2692.3383 | 2714.3739 | 22.0356 | 3771.7 | 1057.3261 | -1057.3261 | 10.19% | 38.95% | 3957.6 | 1243.2261 | -1243.2261 | 11.98% | 45.8% | 22 | 0 | 0 | 0 | 0
2013-02-12 | 23 | 32592.1998 | 1700.5067 | 1708.8664 | 8.3597 | 2855.2 | 1146.3336 | -1146.3336 | 11.05% | 67.08% | 3078.9 | 1370.0336 | -1370.0336 | 13.2% | 80.17% | 23 | 0 | 1 | 0 | 0
2013-02-12 | 24 | 30337.9065 | 1527.9941 | 1521.6906 | -6.3035 | 2621.1 | 1099.4094 | -1099.4094 | 10.59% | 72.25% | 2809.5 | 1287.8094 | -1287.8094 | 12.41% | 84.63% | 24 | 0 | 0 | 0 | 0
2013-02-13 | 1 | 28940.133 | 1391.4941 | 1391.0778 | -0.41627 | 2430.7 | 1039.6222 | -1039.6222 | 10.02% | 74.74% | 2718.1 | 1327.0222 | -1327.0222 | 12.79% | 95.4% | 1 | 0 | 1 | 0 | 0
2013-02-13 | 2 | 28368.3497 | 1306.6096 | 1305.3673 | -1.2423 | 2077 | 771.6327 | -771.6327 | 7.435% | 59.11% | 2376 | 1070.6327 | -1070.6327 | 10.32% | 82.02% | 2 | 0 | 1 | 0 | 0
2013-02-13 | 3 | 28296.9761 | 1252.1952 | 1262.9451 | 10.7499 | 2032.3 | 769.3549 | -769.3549 | 7.413% | 60.92% | 2319.8 | 1056.8549 | -1056.8549 | 10.18% | 83.68% | 3 | 0 | 1 | 0 | 0
2013-02-13 | 4 | 28640.5477 | 1501.1816 | 1499.3768 | -1.8048 | 1860.1 | 360.7232 | -360.7232 | 3.476% | 24.06% | 2165.4 | 666.0232 | -666.0232 | 6.417% | 44.42% | 4 | 0 | 1 | 0 | 0
2013-02-13 | 5 | 29765.3254 | 1791.4864 | 1790.8056 | -0.6808 | 1727.3 | 63.5056 | 63.5056 | 0.6119% | 3.546% | 1992.5 | 201.6944 | -201.6944 | 1.943% | 11.26% | 5 | 1 | 1 | 0 | 1
2013-02-13 | 6 | 32598.8151 | 1657.1762 | 1810.0427 | 152.8665 | 1712.6 | 97.4427 | 97.4427 | 0.9389% | 5.383% | 1960.3 | 150.2573 | -150.2573 | 1.448% | 8.301% | 6 | 1 | 1 | 0 | 1
2013-02-13 | 7 | 37173.955 | 1626.5502 | 1641.9754 | 15.4252 | 1829.4 | 187.4246 | -187.4246 | 1.806% | 11.41% | 2032.7 | 390.7246 | -390.7246 | 3.765% | 23.8% | 7 | 0 | 0 | 0 | 0
2013-02-13 | 8 | 38483.3541 | 1659.5381 | 1667.5278 | 7.9897 | 2121.7 | 454.1722 | -454.1722 | 4.376% | 27.24% | 2298.3 | 630.7722 | -630.7722 | 6.078% | 37.83% | 8 | 0 | 0 | 0 | 0
2013-02-13 | 9 | 37438.1631 | 1769.8897 | 1774.269 | 4.3793 | 2042.9 | 268.631 | -268.631 | 2.588% | 15.14% | 2227.2 | 452.931 | -452.931 | 4.364% | 25.53% | 9 | 0 | 0 | 0 | 0
2013-02-13 | 10 | 36683.4389 | 1365.1133 | 1375.3166 | 10.2033 | 1606.3 | 230.9834 | -230.9834 | 2.226% | 16.79% | 1745 | 369.6834 | -369.6834 | 3.562% | 26.88% | 10 | 0 | 0 | 0 | 0
2013-02-13 | 11 | 35816.1267 | 925.9873 | 941.1343 | 15.1471 | 1398 | 456.8657 | -456.8657 | 4.402% | 48.54% | 1508.8 | 567.6657 | -567.6657 | 5.47% | 60.32% | 11 | 0 | 0 | 0 | 0
2013-02-13 | 12 | 34562.3254 | 651.1701 | 662.0608 | 10.8908 | 1361 | 698.9392 | -698.9392 | 6.734% | 105.6% | 1445.5 | 783.4392 | -783.4392 | 7.549% | 118.3% | 12 | 0 | 0 | 0 | 0
2013-02-13 | 13 | 33291.3139 | 735.7287 | 741.2429 | 5.5142 | 1270.7 | 529.4571 | -529.4571 | 5.101% | 71.43% | 1349.8 | 608.5571 | -608.5571 | 5.864% | 82.1% | 13 | 0 | 0 | 0 | 0
2013-02-13 | 14 | 32521.3859 | 893.1832 | 894.6736 | 1.4904 | 1206 | 311.3264 | -311.3264 | 3% | 34.8% | 1277.8 | 383.1264 | -383.1264 | 3.692% | 42.82% | 14 | 0 | 0 | 0 | 0
2013-02-13 | 15 | 31829.4785 | 1037.0024 | 1034.7716 | -2.2307 | 1087.3 | 52.5284 | -52.5284 | 0.5061% | 5.076% | 1158.1 | 123.3284 | -123.3284 | 1.188% | 11.92% | 15 | 0 | 0 | 0 | 0
2013-02-13 | 16 | 31395.1765 | 1100.5512 | 1094.1527 | -6.3985 | 1038.6 | 55.5527 | 55.5527 | 0.5353% | 5.077% | 1086.2 | 7.9527 | 7.9527 | 0.07663% | 0.7268% | 16 | 1 | 0 | 1 | 1
2013-02-13 | 17 | 31342.4713 | 919.7905 | 918.1502 | -1.6403 | 1057 | 138.8498 | -138.8498 | 1.338% | 15.12% | 1120.2 | 202.0498 | -202.0498 | 1.947% | 22.01% | 17 | 0 | 0 | 0 | 0
2013-02-13 | 18 | 31742.1177 | 624.9653 | 623.9131 | -1.0522 | 908.9 | 284.9869 | -284.9869 | 2.746% | 45.68% | 974.4 | 350.4869 | -350.4869 | 3.377% | 56.18% | 18 | 0 | 0 | 0 | 0
2013-02-13 | 19 | 34050.7314 | 345.2337 | 349.9124 | 4.6787 | 957.6 | 607.6876 | -607.6876 | 5.855% | 173.7% | 1032.6 | 682.6876 | -682.6876 | 6.578% | 195.1% | 19 | 0 | 0 | 0 | 0
2013-02-13 | 20 | 35340.9745 | 349.2161 | 357.6653 | 8.4492 | 1010.1 | 652.4347 | -652.4347 | 6.286% | 182.4% | 1101.4 | 743.7347 | -743.7347 | 7.166% | 207.9% | 20 | 0 | 0 | 0 | 0
2013-02-13 | 21 | 35477.7951 | 607.2049 | 614.7697 | 7.5648 | 1271 | 656.2303 | -656.2303 | 6.323% | 106.7% | 1372.6 | 757.8303 | -757.8303 | 7.302% | 123.3% | 21 | 0 | 0 | 0 | 0
2013-02-13 | 22 | 34911.5243 | 1285.2412 | 1295.5468 | 10.3056 | 1401 | 105.4532 | -105.4532 | 1.016% | 8.14% | 1544.1 | 248.5532 | -248.5532 | 2.395% | 19.19% | 22 | 0 | 0 | 0 | 0
2013-02-13 | 23 | 33030.8316 | 1950.5506 | 1972.0748 | 21.5241 | 1758.3 | 213.7748 | 213.7748 | 2.06% | 10.84% | 1909.6 | 62.4748 | 62.4748 | 0.602% | 3.168% | 23 | 1 | 0 | 1 | 1
2013-02-13 | 24 | 30949.9191 | 2621.9188 | 2641.0848 | 19.166 | 2048.6 | 592.4848 | 592.4848 | 5.709% | 22.43% | 2187.7 | 453.3848 | 453.3848 | 4.368% | 17.17% | 24 | 1 | 0 | 1 | 1
2013-02-14 | 1 | 29719.3152 | 3244.8725 | 3261.5354 | 16.6629 | 2686.6 | 574.9354 | 574.9354 | 5.54% | 17.63% | 2830 | 431.5354 | 431.5354 | 4.158% | 13.23% | 1 | 1 | 0 | 1 | 1
2013-02-14 | 2 | 29345.6752 | 3890.8889 | 3895.3741 | 4.4852 | 2921 | 974.3741 | 974.3741 | 9.388% | 25.01% | 3011.8 | 883.5741 | 883.5741 | 8.514% | 22.68% | 2 | 1 | 0 | 1 | 1
2013-02-14 | 3 | 29430.5643 | 4167.5919 | 4172.5843 | 4.9924 | 3074.1 | 1098.4843 | 1098.4843 | 10.58% | 26.33% | 3113.2 | 1059.3843 | 1059.3843 | 10.21% | 25.39% | 3 | 1 | 0 | 1 | 1
2013-02-14 | 4 | 29950.9871 | 3937.4109 | 3941.0091 | 3.5982 | 3532 | 409.0091 | 409.0091 | 3.941% | 10.38% | 3543.2 | 397.8091 | 397.8091 | 3.833% | 10.09% | 4 | 1 | 0 | 1 | 1
2013-02-14 | 5 | 31194.9983 | 3611.622 | 3615.8017 | 4.1797 | 3983.8 | 367.9983 | -367.9983 | 3.546% | 10.18% | 3923.1 | 307.2983 | -307.2983 | 2.961% | 8.499% | 5 | 0 | 0 | 0 | 0
2013-02-14 | 6 | 34308.6097 | 3463.8875 | 3468.5065 | 4.619 | 4013.8 | 545.2935 | -545.2935 | 5.254% | 15.72% | 3916.2 | 447.6935 | -447.6935 | 4.314% | 12.91% | 6 | 0 | 0 | 0 | 0
2013-02-14 | 7 | 39172.0675 | 3362.0062 | 3366.7837 | 4.7774 | 3527.6 | 160.8163 | -160.8163 | 1.55% | 4.777% | 3471.4 | 104.6163 | -104.6163 | 1.008% | 3.107% | 7 | 0 | 0 | 0 | 0
2013-02-14 | 8 | 40021.0624 | 3439.1058 | 3441.9788 | 2.873 | 3436.2 | 5.7788 | 5.7788 | 0.05568% | 0.1679% | 3433.9 | 8.0788 | 8.0788 | 0.07784% | 0.2347% | 8 | 1 | 0 | 1 | 1
2013-02-14 | 9 | 37869.54 | 2862.5734 | 2865.9594 | 3.386 | 2571.4 | 294.5594 | 294.5594 | 2.838% | 10.28% | 2587.5 | 278.4594 | 278.4594 | 2.683% | 9.716% | 9 | 1 | 0 | 1 | 1
2013-02-14 | 10 | 36068.9113 | 2010.3817 | 2013.7941 | 3.4124 | 1757.4 | 256.3941 | 256.3941 | 2.47% | 12.73% | 1764.4 | 249.3941 | 249.3941 | 2.403% | 12.38% | 10 | 1 | 0 | 1 | 1
2013-02-14 | 11 | 34601.6335 | 1405.7828 | 1410.5017 | 4.7189 | 1580 | 169.4983 | -169.4983 | 1.633% | 12.02% | 1568.1 | 157.5983 | -157.5983 | 1.519% | 11.17% | 11 | 0 | 0 | 0 | 0
2013-02-14 | 12 | 33294.9522 | 971.3737 | 975.0945 | 3.7208 | 1450.4 | 475.3055 | -475.3055 | 4.58% | 48.74% | 1416.2 | 441.1055 | -441.1055 | 4.25% | 45.24% | 12 | 0 | 0 | 0 | 0
2013-02-14 | 13 | 32211.9122 | 849.9031 | 852.5165 | 2.6134 | 1162.8 | 310.2835 | -310.2835 | 2.99% | 36.4% | 1139.4 | 286.8835 | -286.8835 | 2.764% | 33.65% | 13 | 0 | 0 | 0 | 0
2013-02-14 | 14 | 31746.0366 | 874.7163 | 875.34 | 0.6237 | 1008.7 | 133.36 | -133.36 | 1.285% | 15.24% | 996.6 | 121.26 | -121.26 | 1.168% | 13.85% | 14 | 0 | 0 | 0 | 0
2013-02-14 | 15 | 31285.4593 | 1170.5941 | 1171.2675 | 0.6734 | 900.6 | 270.6675 | 270.6675 | 2.608% | 23.11% | 920 | 251.2675 | 251.2675 | 2.421% | 21.45% | 15 | 1 | 0 | 1 | 1
2013-02-14 | 16 | 30995.53 | 1243.7748 | 1248.1327 | 4.3579 | 1055.9 | 192.2327 | 192.2327 | 1.852% | 15.4% | 1086.5 | 161.6327 | 161.6327 | 1.557% | 12.95% | 16 | 1 | 0 | 1 | 1
2013-02-14 | 17 | 30916.8104 | 1143.6363 | 1150.8172 | 7.1809 | 1167.5 | 16.6828 | -16.6828 | 0.1607% | 1.45% | 1200 | 49.1828 | -49.1828 | 0.4739% | 4.274% | 17 | 0 | 0 | 0 | 0
2013-02-14 | 18 | 30998.6047 | 944.6091 | 956.3982 | 11.7891 | 1119.3 | 162.9018 | -162.9018 | 1.57% | 17.03% | 1192.5 | 236.1018 | -236.1018 | 2.275% | 24.69% | 18 | 0 | 0 | 0 | 0
2013-02-14 | 19 | 32738.1613 | 707.9012 | 721.668 | 13.7668 | 1108.4 | 386.732 | -386.732 | 3.726% | 53.59% | 1258.1 | 536.432 | -536.432 | 5.169% | 74.33% | 19 | 0 | 0 | 0 | 0
2013-02-14 | 20 | 33702.1774 | 948.666 | 983.0072 | 34.3412 | 1359.7 | 376.6928 | -376.6928 | 3.63% | 38.32% | 1568.4 | 585.3928 | -585.3928 | 5.64% | 59.55% | 20 | 0 | 1 | 0 | 0
2013-02-14 | 21 | 33391.2306 | 1728.1646 | 1782.7711 | 54.6065 | 1515.8 | 266.9711 | 266.9711 | 2.572% | 14.98% | 1764.1 | 18.6711 | 18.6711 | 0.1799% | 1.047% | 21 | 1 | 1 | 1 | 1
2013-02-14 | 22 | 32358.2306 | 2952.4671 | 2992.5231 | 40.056 | 2428.1 | 564.4231 | 564.4231 | 5.438% | 18.86% | 2659.8 | 332.7231 | 332.7231 | 3.206% | 11.12% | 22 | 1 | 1 | 1 | 1
2013-02-14 | 23 | 30571.2384 | 5039.5475 | 5071.3992 | 31.8517 | 4152.2 | 919.1992 | 919.1992 | 8.857% | 18.13% | 4374.6 | 696.7992 | 696.7992 | 6.714% | 13.74% | 23 | 1 | 1 | 1 | 1
2013-02-14 | 24 | 28758.4232 | 6655.5282 | 6763.9255 | 108.3973 | 5822.2 | 941.7255 | 941.7255 | 9.074% | 13.92% | 6065.9 | 698.0255 | 698.0255 | 6.726% | 10.32% | 24 | 1 | 1 | 1 | 1
2013-02-15 | 1 | 27716.6481 | 7054.268 | 7120.2645 | 65.9965 | 6096.2 | 1024.0645 | 1024.0645 | 9.867% | 14.38% | 6325.2 | 795.0645 | 795.0645 | 7.661% | 11.17% | 1 | 1 | 1 | 1 | 1
2013-02-15 | 2 | 27316.5961 | 7144.3111 | 7254.0301 | 109.719 | 6513.2 | 740.8301 | 740.8301 | 7.138% | 10.21% | 6672.8 | 581.2301 | 581.2301 | 5.6% | 8.013% | 2 | 1 | 0 | 1 | 1
2013-02-15 | 3 | 27299.8726 | 6993.7771 | 7297.1583 | 303.3812 | 6976.8 | 320.3583 | 320.3583 | 3.087% | 4.39% | 7108.1 | 189.0583 | 189.0583 | 1.822% | 2.591% | 3 | 1 | 0 | 1 | 1
2013-02-15 | 4 | 27599.5893 | 6912.9542 | 7148.526 | 235.5718 | 6797 | 351.526 | 351.526 | 3.387% | 4.917% | 6901.7 | 246.826 | 246.826 | 2.378% | 3.453% | 4 | 1 | 0 | 1 | 1
2013-02-15 | 5 | 28698.9501 | 6940.4631 | 7050.2235 | 109.7604 | 6556.7 | 493.5235 | 493.5235 | 4.755% | 7% | 6687.6 | 362.6235 | 362.6235 | 3.494% | 5.143% | 5 | 1 | 0 | 1 | 1
2013-02-15 | 6 | 31339.8481 | 6761.0988 | 6783.8825 | 22.7836 | 6262.8 | 521.0825 | 521.0825 | 5.021% | 7.681% | 6401.8 | 382.0825 | 382.0825 | 3.681% | 5.632% | 6 | 1 | 0 | 1 | 1
2013-02-15 | 7 | 35752.0661 | 6152.262 | 6178.7079 | 26.4459 | 5913.7 | 265.0079 | 265.0079 | 2.553% | 4.289% | 6043 | 135.7079 | 135.7079 | 1.308% | 2.196% | 7 | 1 | 0 | 1 | 1
2013-02-15 | 8 | 36994.0056 | 5257.2387 | 5272.0194 | 14.7806 | 5574.3 | 302.2806 | -302.2806 | 2.913% | 5.734% | 5657.7 | 385.6806 | -385.6806 | 3.716% | 7.316% | 8 | 0 | 0 | 0 | 0
2013-02-15 | 9 | 36105.563 | 4887.5141 | 4889.4267 | 1.9125 | 5335.7 | 446.2733 | -446.2733 | 4.3% | 9.127% | 5406 | 516.5733 | -516.5733 | 4.977% | 10.57% | 9 | 0 | 0 | 0 | 0
2013-02-15 | 10 | 35697.5908 | 4667.4611 | 4862.0257 | 194.5646 | 4667.7 | 194.3257 | 194.3257 | 1.872% | 3.997% | 4719.4 | 142.6257 | 142.6257 | 1.374% | 2.933% | 10 | 1 | 0 | 1 | 1
2013-02-15 | 11 | 35281.5195 | 4689.1653 | 4692.8741 | 3.7087 | 3860.3 | 832.5741 | 832.5741 | 8.022% | 17.74% | 3912.4 | 780.4741 | 780.4741 | 7.52% | 16.63% | 11 | 1 | 0 | 1 | 1
2013-02-15 | 12 | 34595.2234 | 4332.3045 | 4335.9795 | 3.675 | 3538.9 | 797.0795 | 797.0795 | 7.68% | 18.38% | 3538.8 | 797.1795 | 797.1795 | 7.681% | 18.39% | 12 | 1 | 0 | 1 | 1
2013-02-15 | 13 | 34016.9684 | 3679.3005 | 3680.3236 | 1.0231 | 3056.6 | 623.7236 | 623.7236 | 6.01% | 16.95% | 3059.2 | 621.1236 | 621.1236 | 5.985% | 16.88% | 13 | 1 | 0 | 1 | 1
2013-02-15 | 14 | 33725.3415 | 3147.8623 | 3147.2237 | -0.63858 | 2897.6 | 249.6237 | 249.6237 | 2.405% | 7.932% | 2943 | 204.2237 | 204.2237 | 1.968% | 6.489% | 14 | 1 | 0 | 1 | 1
2013-02-15 | 15 | 33315.187 | 2972.0069 | 2970.5136 | -1.4933 | 2611.7 | 358.8136 | 358.8136 | 3.457% | 12.08% | 2680.2 | 290.3136 | 290.3136 | 2.797% | 9.773% | 15 | 1 | 0 | 1 | 1
2013-02-15 | 16 | 32873.6963 | 2767.7885 | 2765.8875 | -1.9011 | 2366 | 399.8875 | 399.8875 | 3.853% | 14.46% | 2489.7 | 276.1875 | 276.1875 | 2.661% | 9.985% | 16 | 1 | 0 | 1 | 1
2013-02-15 | 17 | 32993.3205 | 2321.3228 | 2320.8212 | -0.50159 | 2025 | 295.8212 | 295.8212 | 2.85% | 12.75% | 2167.7 | 153.1212 | 153.1212 | 1.475% | 6.598% | 17 | 1 | 0 | 1 | 1
2013-02-15 | 18 | 33505.0257 | 1917.9525 | 1915.7153 | -2.2372 | 2019.6 | 103.8847 | -103.8847 | 1.001% | 5.423% | 2176.9 | 261.1847 | -261.1847 | 2.517% | 13.63% | 18 | 0 | 0 | 0 | 0
2013-02-15 | 19 | 35551.5662 | 1406.9586 | 1410.8339 | 3.8754 | 1684.6 | 273.7661 | -273.7661 | 2.638% | 19.4% | 1876.6 | 465.7661 | -465.7661 | 4.488% | 33.01% | 19 | 0 | 0 | 0 | 0
2013-02-15 | 20 | 36341.3697 | 758.7973 | 772.0387 | 13.2413 | 1321 | 548.9613 | -548.9613 | 5.289% | 71.11% | 1535.2 | 763.1613 | -763.1613 | 7.353% | 98.85% | 20 | 0 | 1 | 0 | 0
2013-02-15 | 21 | 36056.8367 | 612.2112 | 614.6768 | 2.4657 | 1207.8 | 593.1232 | -593.1232 | 5.715% | 96.49% | 1382.1 | 767.4232 | -767.4232 | 7.394% | 124.8% | 21 | 0 | 0 | 0 | 0
2013-02-15 | 22 | 35393.179 | 505.7944 | 515.1826 | 9.3883 | 1064.3 | 549.1174 | -549.1174 | 5.291% | 106.6% | 1216.9 | 701.7174 | -701.7174 | 6.761% | 136.2% | 22 | 0 | 0 | 0 | 0
2013-02-15 | 23 | 34165.6964 | 687.9993 | 696.6451 | 8.6457 | 1062 | 365.3549 | -365.3549 | 3.52% | 52.44% | 1232.3 | 535.6549 | -535.6549 | 5.161% | 76.89% | 23 | 0 | 0 | 0 | 0
2013-02-15 | 24 | 32676.6919 | 765.7457 | 782.7557 | 17.01 | 1192.9 | 410.1443 | -410.1443 | 3.952% | 52.4% | 1367.9 | 585.1443 | -585.1443 | 5.638% | 74.75% | 24 | 0 | 0 | 0 | 0
2013-02-16 | 1 | 31587.6639 | 1319.4801 | 1327.6259 | 8.1458 | 1462.5 | 134.8741 | -134.8741 | 1.3% | 10.16% | 1678.3 | 350.6741 | -350.6741 | 3.379% | 26.41% | 1 | 0 | 1 | 0 | 0
2013-02-16 | 2 | 31187.8438 | 1467.2363 | 1488.2287 | 20.9924 | 1903.6 | 415.3713 | -415.3713 | 4.002% | 27.91% | 2169.9 | 681.6713 | -681.6713 | 6.568% | 45.8% | 2 | 0 | 1 | 0 | 0
2013-02-16 | 3 | 31122.0498 | 1711.3396 | 1735.13 | 23.7904 | 2511.3 | 776.17 | -776.17 | 7.479% | 44.73% | 2753.7 | 1018.57 | -1018.57 | 9.814% | 58.7% | 3 | 0 | 1 | 0 | 0
2013-02-16 | 4 | 31415.8092 | 1838.174 | 1841.0841 | 2.91 | 2966.3 | 1125.2159 | -1125.2159 | 10.84% | 61.12% | 3178.3 | 1337.2159 | -1337.2159 | 12.88% | 72.63% | 4 | 0 | 1 | 0 | 0
2013-02-16 | 5 | 32183.2725 | 2013.0008 | 2020.5365 | 7.5356 | 2856.7 | 836.1635 | -836.1635 | 8.057% | 41.38% | 3023.8 | 1003.2635 | -1003.2635 | 9.667% | 49.65% | 5 | 0 | 0 | 0 | 0
2013-02-16 | 6 | 33758.896 | 2045.413 | 2055.3555 | 9.9426 | 2566.5 | 511.1445 | -511.1445 | 4.925% | 24.87% | 2703.5 | 648.1445 | -648.1445 | 6.245% | 31.53% | 6 | 0 | 0 | 0 | 0
2013-02-16 | 7 | 35886.7318 | 2014.0702 | 2013.8155 | -0.2547 | 2463.3 | 449.4845 | -449.4845 | 4.331% | 22.32% | 2579.9 | 566.0845 | -566.0845 | 5.454% | 28.11% | 7 | 0 | 0 | 0 | 0
2013-02-16 | 8 | 37356.0896 | 1925.0133 | 1949.1717 | 24.1584 | 2644.8 | 695.6283 | -695.6283 | 6.703% | 35.69% | 2749.4 | 800.2283 | -800.2283 | 7.71% | 41.05% | 8 | 0 | 0 | 0 | 0
2013-02-16 | 9 | 37498.913 | 1474.4946 | 1478.5699 | 4.0754 | 2229.2 | 750.6301 | -750.6301 | 7.233% | 50.77% | 2312 | 833.4301 | -833.4301 | 8.03% | 56.37% | 9 | 0 | 0 | 0 | 0
2013-02-16 | 10 | 36655.9602 | 1082.1379 | 1089.8344 | 7.6964 | 1476.4 | 386.5656 | -386.5656 | 3.725% | 35.47% | 1575.2 | 485.3656 | -485.3656 | 4.677% | 44.54% | 10 | 0 | 0 | 0 | 0
2013-02-16 | 11 | 35249.7728 | 879.0025 | 884.8487 | 5.8462 | 1126.7 | 241.8513 | -241.8513 | 2.33% | 27.33% | 1266.7 | 381.8513 | -381.8513 | 3.679% | 43.15% | 11 | 0 | 0 | 0 | 0
2013-02-16 | 12 | 33571.1095 | 836.6482 | 829.8603 | -6.7879 | 1409.5 | 579.6397 | -579.6397 | 5.585% | 69.85% | 1475.3 | 645.4397 | -645.4397 | 6.219% | 77.78% | 12 | 0 | 0 | 0 | 0
2013-02-16 | 13 | 31934.8138 | 1310.9632 | 1303.0958 | -7.8675 | 1803.9 | 500.8042 | -500.8042 | 4.825% | 38.43% | 1844.3 | 541.2042 | -541.2042 | 5.215% | 41.53% | 13 | 0 | 0 | 0 | 0
2013-02-16 | 14 | 30478.8735 | 2185.5231 | 2186.0916 | 0.56846 | 2208.2 | 22.1084 | -22.1084 | 0.213% | 1.011% | 2246.6 | 60.5084 | -60.5084 | 0.583% | 2.768% | 14 | 0 | 0 | 0 | 0
2013-02-16 | 15 | 29355.7111 | 2181.4549 | 2181.815 | 0.36009 | 2208.6 | 26.785 | -26.785 | 0.2581% | 1.228% | 2251.7 | 69.885 | -69.885 | 0.6734% | 3.203% | 15 | 0 | 0 | 0 | 0
2013-02-16 | 16 | 28775.4657 | 1751.4569 | 1753.1611 | 1.7042 | 2204.3 | 451.1389 | -451.1389 | 4.347% | 25.73% | 2240.7 | 487.5389 | -487.5389 | 4.698% | 27.81% | 16 | 0 | 0 | 0 | 0
2013-02-16 | 17 | 28649.7183 | 1467.124 | 1472.7948 | 5.6708 | 2213.4 | 740.6052 | -740.6052 | 7.136% | 50.29% | 2227 | 754.2052 | -754.2052 | 7.267% | 51.21% | 17 | 0 | 0 | 0 | 0
2013-02-16 | 18 | 29087.0182 | 1089.3442 | 1090.138 | 0.79379 | 1983.8 | 893.662 | -893.662 | 8.611% | 81.98% | 2010.3 | 920.162 | -920.162 | 8.866% | 84.41% | 18 | 0 | 0 | 0 | 0
2013-02-16 | 19 | 31284.3561 | 1082.8569 | 1088.6555 | 5.7986 | 1919.7 | 831.0445 | -831.0445 | 8.007% | 76.34% | 1949.1 | 860.4445 | -860.4445 | 8.291% | 79.04% | 19 | 0 | 0 | 0 | 0
2013-02-16 | 20 | 32741.2139 | 1788.1461 | 1794.6028 | 6.4568 | 2592.5 | 797.8972 | -797.8972 | 7.688% | 44.46% | 2673.4 | 878.7972 | -878.7972 | 8.467% | 48.97% | 20 | 0 | 0 | 0 | 0
2013-02-16 | 21 | 32803.9687 | 2681.1775 | 2733.6371 | 52.4596 | 3417.2 | 683.5629 | -683.5629 | 6.586% | 25.01% | 3548.2 | 814.5629 | -814.5629 | 7.849% | 29.8% | 21 | 0 | 0 | 0 | 0
2013-02-16 | 22 | 32529.9463 | 4521.1937 | 4560.9609 | 39.7672 | 4101.2 | 459.7609 | 459.7609 | 4.43% | 10.08% | 4264.5 | 296.4609 | 296.4609 | 2.856% | 6.5% | 22 | 1 | 0 | 1 | 1
2013-02-16 | 23 | 31704.4308 | 5980.4306 | 6018.349 | 37.9184 | 4901.9 | 1116.449 | 1116.449 | 10.76% | 18.55% | 5071.7 | 946.649 | 946.649 | 9.121% | 15.73% | 23 | 1 | 0 | 1 | 1
2013-02-16 | 24 | 30677.3681 | 6615.1835 | 6789.6977 | 174.5142 | 5615.3 | 1174.3977 | 1174.3977 | 11.32% | 17.3% | 5803.6 | 986.0977 | 986.0977 | 9.501% | 14.52% | 24 | 1 | 0 | 1 | 1
2013-02-17 | 1 | 29719.8085 | 6920.3849 | 7095.8184 | 175.4335 | 6491.2 | 604.6184 | 604.6184 | 5.826% | 8.521% | 6638.5 | 457.3184 | 457.3184 | 4.406% | 6.445% | 1 | 1 | 0 | 1 | 1
2013-02-17 | 2 | 29238.6153 | 7038.7146 | 7239.9584 | 201.2438 | 6845.9 | 394.0584 | 394.0584 | 3.797% | 5.443% | 6896.5 | 343.4584 | 343.4584 | 3.309% | 4.744% | 2 | 1 | 0 | 1 | 1
2013-02-17 | 3 | 29192.0492 | 7071.483 | 7117.6096 | 46.1266 | 6824.5 | 293.1096 | 293.1096 | 2.824% | 4.118% | 6994.9 | 122.7096 | 122.7096 | 1.182% | 1.724% | 3 | 1 | 0 | 1 | 1
2013-02-17 | 4 | 29332.4639 | 6915.503 | 6975.2749 | 59.7719 | 6752.7 | 222.5749 | 222.5749 | 2.145% | 3.191% | 6935.7 | 39.5749 | 39.5749 | 0.3813% | 0.5674% | 4 | 1 | 0 | 1 | 1
2013-02-17 | 5 | 29780.0143 | 6699.0963 | 6750.6474 | 51.5512 | 6642 | 108.6474 | 108.6474 | 1.047% | 1.609% | 6862.2 | 111.5526 | -111.5526 | 1.075% | 1.652% | 5 | 1 | 1 | 0 | 1
2013-02-17 | 6 | 30881.8671 | 6622.7004 | 6687.2426 | 64.5422 | 6589.5 | 97.7426 | 97.7426 | 0.9418% | 1.462% | 6808 | 120.7574 | -120.7574 | 1.164% | 1.806% | 6 | 1 | 1 | 0 | 1
2013-02-17 | 7 | 32308.0205 | 6409.6761 | 6454.5937 | 44.9176 | 6508.2 | 53.6063 | -53.6063 | 0.5165% | 0.8305% | 6743.4 | 288.8063 | -288.8063 | 2.783% | 4.474% | 7 | 0 | 1 | 0 | 0
2013-02-17 | 8 | 33185.7725 | 6356.0833 | 6394.1653 | 38.082 | 6395.3 | 1.1347 | -1.1347 | 0.01093% | 0.01775% | 6654.7 | 260.5347 | -260.5347 | 2.51% | 4.075% | 8 | 0 | 1 | 0 | 0
2013-02-17 | 9 | 33381.5473 | 5769.9897 | 5827.574 | 57.5843 | 6084.7 | 257.126 | -257.126 | 2.477% | 4.412% | 6286.7 | 459.126 | -459.126 | 4.424% | 7.879% | 9 | 0 | 0 | 0 | 0
2013-02-17 | 10 | 32558.0096 | 5285.4157 | 5304.1251 | 18.7094 | 5427.3 | 123.1749 | -123.1749 | 1.187% | 2.322% | 5629.8 | 325.6749 | -325.6749 | 3.138% | 6.14% | 10 | 0 | 0 | 0 | 0
2013-02-17 | 11 | 31306.6337 | 6036.5053 | 6049.4189 | 12.9136 | 5225.7 | 823.7189 | 823.7189 | 7.937% | 13.62% | 5454.8 | 594.6189 | 594.6189 | 5.729% | 9.829% | 11 | 1 | 1 | 1 | 1
2013-02-17 | 12 | 30230.5059 | 6812.1235 | 6819.2826 | 7.1591 | 5331.1 | 1488.1826 | 1488.1826 | 14.34% | 21.82% | 5579.3 | 1239.9826 | 1239.9826 | 11.95% | 18.18% | 12 | 1 | 1 | 1 | 1
2013-02-17 | 13 | 29453.6245 | 7148.6532 | 7162.6091 | 13.9559 | 5497.1 | 1665.5091 | 1665.5091 | 16.05% | 23.25% | 5763.9 | 1398.7091 | 1398.7091 | 13.48% | 19.53% | 13 | 1 | 1 | 1 | 1
2013-02-17 | 14 | 28801.8441 | 7376.026 | 7450.962 | 74.9361 | 6260.7 | 1190.262 | 1190.262 | 11.47% | 15.97% | 6530.6 | 920.362 | 920.362 | 8.868% | 12.35% | 14 | 1 | 1 | 1 | 1
2013-02-17 | 15 | 28416.4646 | 7698.8011 | 7866.4184 | 167.6173 | 6817 | 1049.4184 | 1049.4184 | 10.11% | 13.34% | 7093.6 | 772.8184 | 772.8184 | 7.446% | 9.824% | 15 | 1 | 1 | 1 | 1
2013-02-17 | 16 | 28201.2531 | 7748.2847 | 8224.1226 | 475.8379 | 7159.1 | 1065.0226 | 1065.0226 | 10.26% | 12.95% | 7447.3 | 776.8226 | 776.8226 | 7.485% | 9.446% | 16 | 1 | 1 | 1 | 1
2013-02-17 | 17 | 28356.0464 | 7812.6639 | 8495.9815 | 683.3176 | 7525.3 | 970.6815 | 970.6815 | 9.353% | 11.43% | 7819.5 | 676.4815 | 676.4815 | 6.518% | 7.962% | 17 | 1 | 1 | 1 | 1
2013-02-17 | 18 | 29010.4021 | 7842.5115 | 8516.27 | 673.7585 | 7683.4 | 832.87 | 832.87 | 8.025% | 9.78% | 7979.8 | 536.47 | 536.47 | 5.169% | 6.299% | 18 | 1 | 1 | 1 | 1
2013-02-17 | 19 | 31086.6369 | 7909.824 | 8444.514 | 534.69 | 8113.4 | 331.114 | 331.114 | 3.19% | 3.921% | 8398.1 | 46.414 | 46.414 | 0.4472% | 0.5496% | 19 | 1 | 1 | 1 | 1
2013-02-17 | 20 | 32262.4094 | 7964.7066 | 8654.1167 | 689.41 | 8714.3 | 60.1833 | -60.1833 | 0.5799% | 0.6954% | 9004.6 | 350.4833 | -350.4833 | 3.377% | 4.05% | 20 | 0 | 1 | 0 | 0
2013-02-17 | 21 | 31758.3252 | 7928.8113 | 8854.9324 | 926.1211 | 8950.2 | 95.2676 | -95.2676 | 0.9179% | 1.076% | 9236.9 | 381.9676 | -381.9676 | 3.68% | 4.314% | 21 | 0 | 1 | 0 | 0
2013-02-17 | 22 | 30780.4405 | 7877.6064 | 8821.7247 | 944.1183 | 8931.1 | 109.3753 | -109.3753 | 1.054% | 1.24% | 9236.7 | 414.9753 | -414.9753 | 3.998% | 4.704% | 22 | 0 | 1 | 0 | 0
2013-02-17 | 23 | 29067.6502 | 7839.8171 | 8781.6405 | 941.8234 | 8969.8 | 188.1595 | -188.1595 | 1.813% | 2.143% | 9263.8 | 482.1595 | -482.1595 | 4.646% | 5.491% | 23 | 0 | 1 | 0 | 0
2013-02-17 | 24 | 27044.6443 | 7566.434 | 8789.1393 | 1222.7052 | 9013.1 | 223.9607 | -223.9607 | 2.158% | 2.548% | 9301.1 | 511.9607 | -511.9607 | 4.933% | 5.825% | 24 | 0 | 1 | 0 | 0
2013-02-18 | 1 | 25594.286 | 7115.3729 | 8689.7058 | 1574.3329 | 8918.1 | 228.3942 | -228.3942 | 2.201% | 2.628% | 9115.2 | 425.4942 | -425.4942 | 4.1% | 4.897% | 1 | 0 | 0 | 0 | 0
2013-02-18 | 2 | 24798.7281 | 6973.4784 | 8441.3586 | 1467.8802 | 8817.7 | 376.3414 | -376.3414 | 3.626% | 4.458% | 9032.3 | 590.9414 | -590.9414 | 5.694% | 7.001% | 2 | 0 | 1 | 0 | 0
2013-02-18 | 3 | 24368.9297 | 6750.6862 | 8267.4805 | 1516.7943 | 8760.9 | 493.4195 | -493.4195 | 4.754% | 5.968% | 8937 | 669.5195 | -669.5195 | 6.451% | 8.098% | 3 | 0 | 0 | 0 | 0
2013-02-18 | 4 | 24379.3003 | 6680.445 | 8145.3806 | 1464.9356 | 8669.6 | 524.2194 | -524.2194 | 5.051% | 6.436% | 8840.4 | 695.0194 | -695.0194 | 6.697% | 8.533% | 4 | 0 | 0 | 0 | 0
2013-02-18 | 5 | 24927.7841 | 6893.5875 | 7847.7628 | 954.1753 | 8460.6 | 612.8372 | -612.8372 | 5.905% | 7.809% | 8645.5 | 797.7372 | -797.7372 | 7.686% | 10.17% | 5 | 0 | 0 | 0 | 0
2013-02-18 | 6 | 26829.7103 | 7094.0645 | 7521.1303 | 427.0658 | 8238.3 | 717.1697 | -717.1697 | 6.91% | 9.535% | 8428 | 906.8697 | -906.8697 | 8.738% | 12.06% | 6 | 0 | 0 | 0 | 0
2013-02-18 | 7 | 29899.2023 | 7200.363 | 7310.8371 | 110.4742 | 7836.8 | 525.9629 | -525.9629 | 5.068% | 7.194% | 8012.2 | 701.3629 | -701.3629 | 6.758% | 9.593% | 7 | 0 | 0 | 0 | 0
2013-02-18 | 8 | 31004.9298 | 6699.0735 | 6770.2892 | 71.2157 | 7245.7 | 475.4108 | -475.4108 | 4.581% | 7.022% | 7435.6 | 665.3108 | -665.3108 | 6.41% | 9.827% | 8 | 0 | 0 | 0 | 0
2013-02-18 | 9 | 31205.7907 | 5881.0016 | 5905.0886 | 24.087 | 6452 | 546.9114 | -546.9114 | 5.27% | 9.262% | 6683.8 | 778.7114 | -778.7114 | 7.503% | 13.19% | 9 | 0 | 1 | 0 | 0
2013-02-18 | 10 | 31821.2031 | 5949.3125 | 5959.9638 | 10.6512 | 5956.2 | 3.7638 | 3.7638 | 0.03626% | 0.06315% | 6205 | 245.0362 | -245.0362 | 2.361% | 4.111% | 10 | 1 | 1 | 0 | 1
2013-02-18 | 11 | 32588.4224 | 7331.9526 | 7490.6021 | 158.6495 | 5489.4 | 2001.2021 | 2001.2021 | 19.28% | 26.72% | 5681.9 | 1808.7021 | 1808.7021 | 17.43% | 24.15% | 11 | 1 | 0 | 1 | 1
2013-02-18 | 12 | 32783.4435 | 7170.43 | 7177.4566 | 7.0266 | 4707.5 | 2469.9566 | 2469.9566 | 23.8% | 34.41% | 4913.9 | 2263.5566 | 2263.5566 | 21.81% | 31.54% | 12 | 1 | 0 | 1 | 1
2013-02-18 | 13 | 32790.1194 | 6833.5769 | 6835.884 | 2.3071 | 4596.1 | 2239.784 | 2239.784 | 21.58% | 32.77% | 4854.4 | 1981.484 | 1981.484 | 19.09% | 28.99% | 13 | 1 | 1 | 1 | 1
2013-02-18 | 14 | 32957.6843 | 6393.9472 | 6396.1312 | 2.184 | 5212 | 1184.1312 | 1184.1312 | 11.41% | 18.51% | 5445.5 | 950.6312 | 950.6312 | 9.16% | 14.86% | 14 | 1 | 1 | 1 | 1
2013-02-18 | 15 | 32885.1656 | 6264.7856 | 6267.6222 | 2.8366 | 5194.2 | 1073.4222 | 1073.4222 | 10.34% | 17.13% | 5423.6 | 844.0222 | 844.0222 | 8.132% | 13.47% | 15 | 1 | 1 | 1 | 1
2013-02-18 | 16 | 32735.3588 | 5809.1299 | 5813.2331 | 4.1032 | 4930.3 | 882.9331 | 882.9331 | 8.507% | 15.19% | 5101.9 | 711.3331 | 711.3331 | 6.854% | 12.24% | 16 | 1 | 0 | 1 | 1
2013-02-18 | 17 | 32713.114 | 5325.4419 | 5331.9867 | 6.5448 | 4317.5 | 1014.4867 | 1014.4867 | 9.775% | 19.03% | 4493.4 | 838.5867 | 838.5867 | 8.08% | 15.73% | 17 | 1 | 0 | 1 | 1
2013-02-18 | 18 | 32702.1604 | 4498.7355 | 4504.1721 | 5.4365 | 3865.2 | 638.9721 | 638.9721 | 6.157% | 14.19% | 3999.1 | 505.0721 | 505.0721 | 4.867% | 11.21% | 18 | 1 | 0 | 1 | 1
2013-02-18 | 19 | 34080.938 | 3453.4091 | 3457.8739 | 4.4648 | 3356.2 | 101.6739 | 101.6739 | 0.9797% | 2.94% | 3451.8 | 6.0739 | 6.0739 | 0.05852% | 0.1757% | 19 | 1 | 0 | 1 | 1
2013-02-18 | 20 | 34902.3306 | 3708.352 | 3704.8486 | -3.5034 | 3179 | 525.8486 | 525.8486 | 5.067% | 14.19% | 3293.5 | 411.3486 | 411.3486 | 3.963% | 11.1% | 20 | 1 | 0 | 1 | 1
2013-02-18 | 21 | 34095.7725 | 4209.8467 | 4211.972 | 2.1253 | 3290.3 | 921.672 | 921.672 | 8.881% | 21.88% | 3439.2 | 772.772 | 772.772 | 7.446% | 18.35% | 21 | 1 | 0 | 1 | 1
2013-02-18 | 22 | 32626.8551 | 3817.7359 | 3819.934 | 2.1981 | 3279.3 | 540.634 | 540.634 | 5.209% | 14.15% | 3423 | 396.934 | 396.934 | 3.825% | 10.39% | 22 | 1 | 0 | 1 | 1
2013-02-18 | 23 | 30044.2953 | 3562.6678 | 3577.7466 | 15.0788 | 3514.5 | 63.2466 | 63.2466 | 0.6094% | 1.768% | 3645.3 | 67.5534 | -67.5534 | 0.6509% | 1.888% | 23 | 1 | 0 | 0 | 1
2013-02-18 | 24 | 27488.1479 | 3430.9532 | 3444.7385 | 13.7853 | 3821.9 | 377.1615 | -377.1615 | 3.634% | 10.95% | 3932.9 | 488.1615 | -488.1615 | 4.704% | 14.17% | 24 | 0 | 0 | 0 | 0
2013-02-19 | 1 | 25861.7462 | 3449.2382 | 3473.7049 | 24.4667 | 3925.7 | 451.9951 | -451.9951 | 4.355% | 13.01% | 4077.1 | 603.3951 | -603.3951 | 5.814% | 17.37% | 1 | 0 | 0 | 0 | 0
2013-02-19 | 2 | 25186.199 | 3262.5396 | 3274.5007 | 11.9611 | 3703.4 | 428.8993 | -428.8993 | 4.133% | 13.1% | 3844.9 | 570.3993 | -570.3993 | 5.496% | 17.42% | 2 | 0 | 0 | 0 | 0
2013-02-19 | 3 | 25002.1626 | 3208.1936 | 3214.8353 | 6.6417 | 3882.4 | 667.5647 | -667.5647 | 6.432% | 20.77% | 3975 | 760.1647 | -760.1647 | 7.324% | 23.65% | 3 | 0 | 0 | 0 | 0
2013-02-19 | 4 | 25325.1075 | 2827.0254 | 2843.3802 | 16.3548 | 3782.9 | 939.5198 | -939.5198 | 9.053% | 33.04% | 3931.1 | 1087.7198 | -1087.7198 | 10.48% | 38.25% | 4 | 0 | 0 | 0 | 0
2013-02-19 | 5 | 26403.545 | 2198.7018 | 2228.7818 | 30.0801 | 3711.9 | 1483.1182 | -1483.1182 | 14.29% | 66.54% | 3831 | 1602.2182 | -1602.2182 | 15.44% | 71.89% | 5 | 0 | 0 | 0 | 0
2013-02-19 | 6 | 29295.9879 | 2448.4099 | 2449.4288 | 1.019 | 3869.2 | 1419.7712 | -1419.7712 | 13.68% | 57.96% | 3935.6 | 1486.1712 | -1486.1712 | 14.32% | 60.67% | 6 | 0 | 0 | 0 | 0
2013-02-19 | 7 | 34106.3113 | 2817.3762 | 2813.3738 | -4.0024 | 3707.8 | 894.4262 | -894.4262 | 8.618% | 31.79% | 3843 | 1029.6262 | -1029.6262 | 9.921% | 36.6% | 7 | 0 | 0 | 0 | 0
2013-02-19 | 8 | 35396.8493 | 3437.8219 | 3428.5304 | -9.2915 | 3348.1 | 80.4304 | 80.4304 | 0.775% | 2.346% | 3596.1 | 167.5696 | -167.5696 | 1.615% | 4.888% | 8 | 1 | 1 | 0 | 1
2013-02-19 | 9 | 34385.5759 | 3809.4664 | 3858.499 | 49.0327 | 3525.8 | 332.699 | 332.699 | 3.206% | 8.622% | 3753.1 | 105.399 | 105.399 | 1.016% | 2.732% | 9 | 1 | 1 | 1 | 1
2013-02-19 | 10 | 33711.9914 | 4403.2955 | 4501.6726 | 98.377 | 3439 | 1062.6726 | 1062.6726 | 10.24% | 23.61% | 3637.2 | 864.4726 | 864.4726 | 8.329% | 19.2% | 10 | 1 | 0 | 1 | 1
2013-02-19 | 11 | 33302.0397 | 4368.5004 | 4425.6308 | 57.1304 | 3741.8 | 683.8308 | 683.8308 | 6.589% | 15.45% | 3891.8 | 533.8308 | 533.8308 | 5.144% | 12.06% | 11 | 1 | 0 | 1 | 1
2013-02-19 | 12 | 32769.8065 | 4319.5523 | 4332.0768 | 12.5244 | 3972.8 | 359.2768 | 359.2768 | 3.462% | 8.293% | 4095.4 | 236.6768 | 236.6768 | 2.28% | 5.463% | 12 | 1 | 0 | 1 | 1
2013-02-19 | 13 | 32336.2006 | 4551.3666 | 4548.7785 | -2.5881 | 4523.5 | 25.2785 | 25.2785 | 0.2436% | 0.5557% | 4660.5 | 111.7215 | -111.7215 | 1.076% | 2.456% | 13 | 1 | 0 | 0 | 1
2013-02-19 | 14 | 32092.776 | 5195.9658 | 5223.1337 | 27.1679 | 4737.9 | 485.2337 | 485.2337 | 4.675% | 9.29% | 4901.4 | 321.7337 | 321.7337 | 3.1% | 6.16% | 14 | 1 | 0 | 1 | 1
2013-02-19 | 15 | 31851.3386 | 6017.5089 | 6052.3471 | 34.8382 | 5053.3 | 999.0471 | 999.0471 | 9.626% | 16.51% | 5244.1 | 808.2471 | 808.2471 | 7.788% | 13.35% | 15 | 1 | 0 | 1 | 1
2013-02-19 | 16 | 31668.0608 | 6401.5728 | 6481.7917 | 80.219 | 5684.3 | 797.4917 | 797.4917 | 7.684% | 12.3% | 5872.9 | 608.8917 | 608.8917 | 5.867% | 9.394% | 16 | 1 | 0 | 1 | 1
2013-02-19 | 17 | 31699.3689 | 6601.6208 | 6711.3512 | 109.7304 | 5919.4 | 791.9512 | 791.9512 | 7.631% | 11.8% | 6143.1 | 568.2512 | 568.2512 | 5.475% | 8.467% | 17 | 1 | 1 | 1 | 1
2013-02-19 | 18 | 32141.1763 | 6290.2647 | 6353.0575 | 62.7928 | 6147.5 | 205.5575 | 205.5575 | 1.981% | 3.236% | 6362 | 8.9425 | -8.9425 | 0.08616% | 0.1408% | 18 | 1 | 1 | 0 | 1
2013-02-19 | 19 | 34338.7496 | 5652.1064 | 5693.4923 | 41.3859 | 6280.1 | 586.6077 | -586.6077 | 5.652% | 10.3% | 6520 | 826.5077 | -826.5077 | 7.964% | 14.52% | 19 | 0 | 1 | 0 | 0
2013-02-19 | 20 | 35110.6184 | 5243.3575 | 5269.4588 | 26.1014 | 6238.7 | 969.2412 | -969.2412 | 9.339% | 18.39% | 6503.8 | 1234.3412 | -1234.3412 | 11.89% | 23.42% | 20 | 0 | 1 | 0 | 0
2013-02-19 | 21 | 34599.7983 | 4721.4592 | 4761.4502 | 39.991 | 6392.8 | 1631.3498 | -1631.3498 | 15.72% | 34.26% | 6686.9 | 1925.4498 | -1925.4498 | 18.55% | 40.44% | 21 | 0 | 1 | 0 | 0
2013-02-19 | 22 | 33120.9712 | 3913.3323 | 3910.3516 | -2.9807 | 6364.5 | 2454.1484 | -2454.1484 | 23.65% | 62.76% | 6665.7 | 2755.3484 | -2755.3484 | 26.55% | 70.46% | 22 | 0 | 1 | 0 | 0
2013-02-19 | 23 | 30687.1983 | 3800.8269 | 3828.025 | 27.1981 | 6075.8 | 2247.775 | -2247.775 | 21.66% | 58.72% | 6374.9 | 2546.875 | -2546.875 | 24.54% | 66.53% | 23 | 0 | 1 | 0 | 0
2013-02-19 | 24 | 28325.0079 | 3573.3304 | 3599.9286 | 26.5982 | 6124.3 | 2524.3714 | -2524.3714 | 24.32% | 70.12% | 6319.5 | 2719.5714 | -2719.5714 | 26.2% | 75.55% | 24 | 0 | 0 | 0 | 0
2013-02-20 | 1 | 26717.1896 | 3714.0795 | 3723.1465 | 9.0671 | 6083.6 | 2360.4535 | -2360.4535 | 22.74% | 63.4% | 6295.9 | 2572.7535 | -2572.7535 | 24.79% | 69.1% | 1 | 0 | 1 | 0 | 0
2013-02-20 | 2 | 25973.9311 | 4222.3767 | 4221.6748 | -0.70187 | 5824.5 | 1602.8252 | -1602.8252 | 15.44% | 37.97% | 6036.1 | 1814.4252 | -1814.4252 | 17.48% | 42.98% | 2 | 0 | 1 | 0 | 0
2013-02-20 | 3 | 25816.0121 | 3667.1809 | 3646.6247 | -20.5563 | 5363 | 1716.3753 | -1716.3753 | 16.54% | 47.07% | 5602 | 1955.3753 | -1955.3753 | 18.84% | 53.62% | 3 | 0 | 1 | 0 | 0
2013-02-20 | 4 | 25973.5318 | 2374.5748 | 2400.3887 | 25.814 | 5007.5 | 2607.1113 | -2607.1113 | 25.12% | 108.6% | 5265.1 | 2864.7113 | -2864.7113 | 27.6% | 119.3% | 4 | 0 | 1 | 0 | 0
2013-02-20 | 5 | 26807.8435 | 3041.4423 | 3141.8009 | 100.3587 | 5550.7 | 2408.8991 | -2408.8991 | 23.21% | 76.67% | 5763.6 | 2621.7991 | -2621.7991 | 25.26% | 83.45% | 5 | 0 | 1 | 0 | 0
2013-02-20 | 6 | 29534.7975 | 3894.0937 | 3996.7522 | 102.6585 | 5512.4 | 1515.6478 | -1515.6478 | 14.6% | 37.92% | 5701 | 1704.2478 | -1704.2478 | 16.42% | 42.64% | 6 | 0 | 0 | 0 | 0
2013-02-20 | 7 | 33907.6443 | 4213.6493 | 4303.9579 | 90.3086 | 4980.6 | 676.6421 | -676.6421 | 6.52% | 15.72% | 5220.4 | 916.4421 | -916.4421 | 8.83% | 21.29% | 7 | 0 | 1 | 0 | 0
2013-02-20 | 8 | 35281.5515 | 4502.2955 | 4577.2642 | 74.9687 | 5199.7 | 622.4358 | -622.4358 | 5.997% | 13.6% | 5496.7 | 919.4358 | -919.4358 | 8.859% | 20.09% | 8 | 0 | 1 | 0 | 0
2013-02-20 | 9 | 35008.3751 | 4741.9265 | 4887.3293 | 145.4029 | 5660.7 | 773.3707 | -773.3707 | 7.452% | 15.82% | 5934.6 | 1047.2707 | -1047.2707 | 10.09% | 21.43% | 9 | 0 | 1 | 0 | 0
2013-02-20 | 10 | 35154.0403 | 4967.7603 | 5106.3904 | 138.6301 | 5767 | 660.6096 | -660.6096 | 6.365% | 12.94% | 6072.8 | 966.4096 | -966.4096 | 9.312% | 18.93% | 10 | 0 | 1 | 0 | 0
2013-02-20 | 11 | 35417.157 | 5243.1127 | 5397.0226 | 153.9099 | 5321.1 | 75.9226 | 75.9226 | 0.7315% | 1.407% | 5619.7 | 222.6774 | -222.6774 | 2.146% | 4.126% | 11 | 1 | 1 | 0 | 1
2013-02-20 | 12 | 35534.6348 | 5595.7755 | 5650.7264 | 54.9509 | 5350.7 | 300.0264 | 300.0264 | 2.891% | 5.31% | 5606.6 | 44.1264 | 44.1264 | 0.4252% | 0.7809% | 12 | 1 | 1 | 1 | 1
2013-02-20 | 13 | 35539.5403 | 5180.0931 | 5299.5041 | 119.411 | 5427.2 | 127.6959 | -127.6959 | 1.23% | 2.41% | 5793.9 | 494.3959 | -494.3959 | 4.764% | 9.329% | 13 | 0 | 1 | 0 | 0
2013-02-20 | 14 | 35488.2697 | 5154.4167 | 5288.4173 | 134.0007 | 5487.3 | 198.8827 | -198.8827 | 1.916% | 3.761% | 5744.7 | 456.2827 | -456.2827 | 4.396% | 8.628% | 14 | 0 | 1 | 0 | 0
2013-02-20 | 15 | 35182.9421 | 5345.2594 | 5472.5192 | 127.2599 | 5718.9 | 246.3808 | -246.3808 | 2.374% | 4.502% | 5964.3 | 491.7808 | -491.7808 | 4.738% | 8.986% | 15 | 0 | 1 | 0 | 0
2013-02-20 | 16 | 35380.9284 | 5420.2328 | 5570.222 | 149.9893 | 5672.8 | 102.578 | -102.578 | 0.9884% | 1.842% | 5944.2 | 373.978 | -373.978 | 3.603% | 6.714% | 16 | 0 | 1 | 0 | 0
2013-02-20 | 17 | 36019.0629 | 5553.4923 | 5718.5769 | 165.0845 | 5973.1 | 254.5231 | -254.5231 | 2.452% | 4.451% | 6282.2 | 563.6231 | -563.6231 | 5.431% | 9.856% | 17 | 0 | 1 | 0 | 0
2013-02-20 | 18 | 37088.6148 | 6040.1539 | 6252.5788 | 212.4249 | 6492.2 | 239.6212 | -239.6212 | 2.309% | 3.832% | 6796.4 | 543.8212 | -543.8212 | 5.24% | 8.698% | 18 | 0 | 1 | 0 | 0
2013-02-20 | 19 | 38709.4232 | 6703.7556 | 6878.8159 | 175.0603 | 7167.9 | 289.0841 | -289.0841 | 2.785% | 4.203% | 7467.5 | 588.6841 | -588.6841 | 5.672% | 8.558% | 19 | 0 | 1 | 0 | 0
2013-02-20 | 20 | 38924.051 | 7302.5007 | 7487.1595 | 184.6588 | 7493.3 | 6.1405 | -6.1405 | 0.05917% | 0.08201% | 7816.3 | 329.1405 | -329.1405 | 3.171% | 4.396% | 20 | 0 | 1 | 0 | 0
2013-02-20 | 21 | 38172.5693 | 7427.0938 | 7611.1501 | 184.0563 | 7638.7 | 27.5499 | -27.5499 | 0.2655% | 0.362% | 7963.1 | 351.9499 | -351.9499 | 3.391% | 4.624% | 21 | 0 | 1 | 0 | 0
2013-02-20 | 22 | 36577.3348 | 7333.8789 | 7482.5307 | 148.6518 | 7546.7 | 64.1693 | -64.1693 | 0.6183% | 0.8576% | 7988.7 | 506.1693 | -506.1693 | 4.877% | 6.765% | 22 | 0 | 1 | 0 | 0
2013-02-20 | 23 | 33767.8204 | 7000.0313 | 7096.4499 | 96.4185 | 7317.2 | 220.7501 | -220.7501 | 2.127% | 3.111% | 7658.9 | 562.4501 | -562.4501 | 5.419% | 7.926% | 23 | 0 | 1 | 0 | 0
2013-02-20 | 24 | 31092.9661 | 5848.9884 | 6002.1847 | 153.1964 | 6959.9 | 957.7153 | -957.7153 | 9.228% | 15.96% | 7287.3 | 1285.1153 | -1285.1153 | 12.38% | 21.41% | 24 | 0 | 1 | 0 | 0
2013-02-21 | 1 | 29313.1466 | 5352.4172 | 5406.359 | 53.9418 | 6214.3 | 807.941 | -807.941 | 7.785% | 14.94% | 6524.2 | 1117.841 | -1117.841 | 10.77% | 20.68% | 1 | 0 | 1 | 0 | 0
2013-02-21 | 2 | 28339.8329 | 4329.5872 | 4491.3533 | 161.7661 | 6497.3 | 2005.9467 | -2005.9467 | 19.33% | 44.66% | 6761.7 | 2270.3467 | -2270.3467 | 21.88% | 50.55% | 2 | 0 | 1 | 0 | 0
2013-02-21 | 3 | 27689.9018 | 4439.5693 | 4533.5548 | 93.9855 | 6304.4 | 1770.8452 | -1770.8452 | 17.06% | 39.06% | 6591.7 | 2058.1452 | -2058.1452 | 19.83% | 45.4% | 3 | 0 | 1 | 0 | 0
2013-02-21 | 4 | 27664.144 | 5205.6182 | 5272.3711 | 66.753 | 6281.6 | 1009.2289 | -1009.2289 | 9.724% | 19.14% | 6541.9 | 1269.5289 | -1269.5289 | 12.23% | 24.08% | 4 | 0 | 1 | 0 | 0
2013-02-21 | 5 | 28306.0981 | 4149.5597 | 4235.0528 | 85.4931 | 6128.3 | 1893.2472 | -1893.2472 | 18.24% | 44.7% | 6375.4 | 2140.3472 | -2140.3472 | 20.62% | 50.54% | 5 | 0 | 1 | 0 | 0
2013-02-21 | 6 | 30619.6675 | 3252.6393 | 3352.565 | 99.9257 | 7048.1 | 3695.535 | -3695.535 | 35.61% | 110.2% | 7254.6 | 3902.035 | -3902.035 | 37.6% | 116.4% | 6 | 0 | 0 | 0 | 0
2013-02-21 | 7 | 34428.0421 | 3506.8324 | 3499.997 | -6.8354 | 7567.2 | 4067.203 | -4067.203 | 39.19% | 116.2% | 7695.2 | 4195.203 | -4195.203 | 40.42% | 119.9% | 7 | 0 | 0 | 0 | 0
2013-02-21 | 8 | 35483.7664 | 4849.9013 | 4861.6068 | 11.7055 | 7354.5 | 2492.8932 | -2492.8932 | 24.02% | 51.28% | 7473.7 | 2612.0932 | -2612.0932 | 25.17% | 53.73% | 8 | 0 | 0 | 0 | 0
2013-02-21 | 9 | 35003.0821 | 5739.7254 | 5806.7324 | 67.0071 | 6851.8 | 1045.0676 | -1045.0676 | 10.07% | 18% | 6997.7 | 1190.9676 | -1190.9676 | 11.48% | 20.51% | 9 | 0 | 0 | 0 | 0
2013-02-21 | 10 | 34972.8318 | 6706.8642 | 6778.0956 | 71.2314 | 6997.8 | 219.7044 | -219.7044 | 2.117% | 3.241% | 7222 | 443.9044 | -443.9044 | 4.277% | 6.549% | 10 | 0 | 1 | 0 | 0
2013-02-21 | 11 | 34849.8463 | 7722.1449 | 7857.0813 | 134.9364 | 7347.7 | 509.3813 | 509.3813 | 4.908% | 6.483% | 7503.8 | 353.2813 | 353.2813 | 3.404% | 4.496% | 11 | 1 | 0 | 1 | 1
2013-02-21 | 12 | 34473.3919 | 7812.8726 | 7910.9499 | 98.0773 | 7503.8 | 407.1499 | 407.1499 | 3.923% | 5.147% | 7680.8 | 230.1499 | 230.1499 | 2.218% | 2.909% | 12 | 1 | 0 | 1 | 1
2013-02-21 | 13 | 34098.0858 | 7439.2273 | 7548.17 | 108.9427 | 7590.3 | 42.13 | -42.13 | 0.4059% | 0.5581% | 7770.3 | 222.13 | -222.13 | 2.14% | 2.943% | 13 | 0 | 0 | 0 | 0
2013-02-21 | 14 | 33768.6099 | 7189.0092 | 7382.5554 | 193.5462 | 7846.3 | 463.7446 | -463.7446 | 4.468% | 6.282% | 7989.8 | 607.2446 | -607.2446 | 5.851% | 8.225% | 14 | 0 | 0 | 0 | 0
2013-02-21 | 15 | 33357.2466 | 6916.9457 | 7099.2089 | 182.2631 | 7723.3 | 624.0911 | -624.0911 | 6.013% | 8.791% | 7876.9 | 777.6911 | -777.6911 | 7.493% | 10.95% | 15 | 0 | 0 | 0 | 0
2013-02-21 | 16 | 33070.9764 | 6696.6051 | 6871.3338 | 174.7287 | 7268.4 | 397.0662 | -397.0662 | 3.826% | 5.779% | 7423.3 | 551.9662 | -551.9662 | 5.318% | 8.033% | 16 | 0 | 0 | 0 | 0
2013-02-21 | 17 | 32833.7887 | 5838.8036 | 5999.9092 | 161.1056 | 6229.5 | 229.5908 | -229.5908 | 2.212% | 3.827% | 6421.7 | 421.7908 | -421.7908 | 4.064% | 7.03% | 17 | 0 | 0 | 0 | 0
2013-02-21 | 18 | 32550.4254 | 3647.1693 | 3700.071 | 52.9017 | 4272.4 | 572.329 | -572.329 | 5.515% | 15.47% | 4444.2 | 744.129 | -744.129 | 7.17% | 20.11% | 18 | 0 | 0 | 0 | 0
2013-02-21 | 19 | 33855.9947 | 1755.4905 | 1817.4309 | 61.9404 | 3626.1 | 1808.6691 | -1808.6691 | 17.43% | 99.52% | 3829.7 | 2012.2691 | -2012.2691 | 19.39% | 110.7% | 19 | 0 | 0 | 0 | 0
2013-02-21 | 20 | 34745.0563 | 1677.575 | 1742.5795 | 65.0045 | 3810 | 2067.4205 | -2067.4205 | 19.92% | 118.6% | 3960.8 | 2218.2205 | -2218.2205 | 21.37% | 127.3% | 20 | 0 | 0 | 0 | 0
2013-02-21 | 21 | 34259.0677 | 2338.1859 | 2395.4604 | 57.2745 | 3150.6 | 755.1396 | -755.1396 | 7.276% | 31.52% | 3365.9 | 970.4396 | -970.4396 | 9.35% | 40.51% | 21 | 0 | 1 | 0 | 0
2013-02-21 | 22 | 33065.0297 | 2889.7131 | 2911.3235 | 21.6104 | 2881.8 | 29.5235 | 29.5235 | 0.2845% | 1.014% | 3042.7 | 131.3765 | -131.3765 | 1.266% | 4.513% | 22 | 1 | 0 | 0 | 1
2013-02-21 | 23 | 30783.0845 | 3419.1717 | 3463.6266 | 44.4548 | 2791.8 | 671.8266 | 671.8266 | 6.473% | 19.4% | 2960.9 | 502.7266 | 502.7266 | 4.844% | 14.51% | 23 | 1 | 0 | 1 | 1
2013-02-21 | 24 | 28630.9963 | 3845.9419 | 3898.7543 | 52.8124 | 2996.4 | 902.3543 | 902.3543 | 8.694% | 23.14% | 3171 | 727.7543 | 727.7543 | 7.012% | 18.67% | 24 | 1 | 0 | 1 | 1
2013-02-22 | 1 | 27272.3334 | 4245.2275 | 4306.5147 | 61.2872 | 3226.9 | 1079.6147 | 1079.6147 | 10.4% | 25.07% | 3376.2 | 930.3147 | 930.3147 | 8.964% | 21.6% | 1 | 1 | 0 | 1 | 1
2013-02-22 | 2 | 26729.5037 | 3868.8033 | 3906.0598 | 37.2565 | 3225.3 | 680.7598 | 680.7598 | 6.559% | 17.43% | 3390.3 | 515.7598 | 515.7598 | 4.969% | 13.2% | 2 | 1 | 0 | 1 | 1
2013-02-22 | 3 | 26739.4942 | 3813.3264 | 3843.6227 | 30.2962 | 3204.1 | 639.5227 | 639.5227 | 6.162% | 16.64% | 3300.6 | 543.0227 | 543.0227 | 5.232% | 14.13% | 3 | 1 | 0 | 1 | 1
2013-02-22 | 4 | 27252.2229 | 3419.5312 | 3419.115 | -0.41622 | 3364.2 | 54.915 | 54.915 | 0.5291% | 1.606% | 3444.1 | 24.985 | -24.985 | 0.2407% | 0.7307% | 4 | 1 | 0 | 0 | 1
2013-02-22 | 5 | 28430.2245 | 2350.7944 | 2330.6783 | -20.1162 | 3006.5 | 675.8217 | -675.8217 | 6.512% | 29% | 3062.2 | 731.5217 | -731.5217 | 7.048% | 31.39% | 5 | 0 | 0 | 0 | 0
2013-02-22 | 6 | 31343.0455 | 2248.0332 | 2206.8431 | -41.1901 | 2619.3 | 412.4569 | -412.4569 | 3.974% | 18.69% | 2746.4 | 539.5569 | -539.5569 | 5.199% | 24.45% | 6 | 0 | 0 | 0 | 0
2013-02-22 | 7 | 36118.3548 | 2170.7351 | 2127.7741 | -42.961 | 2373.2 | 245.4259 | -245.4259 | 2.365% | 11.53% | 2477.8 | 350.0259 | -350.0259 | 3.373% | 16.45% | 7 | 0 | 0 | 0 | 0
2013-02-22 | 8 | 37649.0975 | 2308.4564 | 2278.4762 | -29.9802 | 2007.2 | 271.2762 | 271.2762 | 2.614% | 11.91% | 2106.6 | 171.8762 | 171.8762 | 1.656% | 7.543% | 8 | 1 | 0 | 1 | 1
2013-02-22 | 9 | 37238.016 | 2226.9347 | 2215.8604 | -11.0743 | 1979.8 | 236.0604 | 236.0604 | 2.275% | 10.65% | 2092.8 | 123.0604 | 123.0604 | 1.186% | 5.554% | 9 | 1 | 0 | 1 | 1
2013-02-22 | 10 | 37084.511 | 1869.5665 | 1852.1589 | -17.4076 | 1923.8 | 71.6411 | -71.6411 | 0.6903% | 3.868% | 2014.4 | 162.2411 | -162.2411 | 1.563% | 8.76% | 10 | 0 | 0 | 0 | 0
2013-02-22 | 11 | 36749.1432 | 1477.5713 | 1507.0762 | 29.5049 | 1880.4 | 373.3238 | -373.3238 | 3.597% | 24.77% | 1962.2 | 455.1238 | -455.1238 | 4.385% | 30.2% | 11 | 0 | 0 | 0 | 0
2013-02-22 | 12 | 36042.9641 | 1151.1204 | 1180.9578 | 29.8374 | 1722.5 | 541.5422 | -541.5422 | 5.218% | 45.86% | 1814.2 | 633.2422 | -633.2422 | 6.101% | 53.62% | 12 | 0 | 0 | 0 | 0
2013-02-22 | 13 | 35110.1887 | 1006.0906 | 1034.5628 | 28.4722 | 1358.1 | 323.5372 | -323.5372 | 3.117% | 31.27% | 1489.3 | 454.7372 | -454.7372 | 4.382% | 43.95% | 13 | 0 | 0 | 0 | 0
2013-02-22 | 14 | 34359.8095 | 817.3599 | 836.7063 | 19.3464 | 1154 | 317.2937 | -317.2937 | 3.057% | 37.92% | 1279.7 | 442.9937 | -442.9937 | 4.268% | 52.94% | 14 | 0 | 0 | 0 | 0
2013-02-22 | 15 | 33452.018 | 833.9833 | 858.6122 | 24.629 | 1078.5 | 219.8878 | -219.8878 | 2.119% | 25.61% | 1221.3 | 362.6878 | -362.6878 | 3.495% | 42.24% | 15 | 0 | 0 | 0 | 0
2013-02-22 | 16 | 32713.6392 | 970.5694 | 990.4935 | 19.9241 | 1083.8 | 93.3065 | -93.3065 | 0.899% | 9.42% | 1218.6 | 228.1065 | -228.1065 | 2.198% | 23.03% | 16 | 0 | 0 | 0 | 0
2013-02-22 | 17 | 32477.221 | 932.3823 | 945.2113 | 12.829 | 1026.4 | 81.1887 | -81.1887 | 0.7823% | 8.589% | 1202.6 | 257.3887 | -257.3887 | 2.48% | 27.23% | 17 | 0 | 0 | 0 | 0
2013-02-22 | 18 | 32867.2536 | 921.9034 | 931.2683 | 9.365 | 1082.1 | 150.8317 | -150.8317 | 1.453% | 16.2% | 1289.3 | 358.0317 | -358.0317 | 3.45% | 38.45% | 18 | 0 | 0 | 0 | 0
2013-02-22 | 19 | 34634.5192 | 997.231 | 1000.7552 | 3.5242 | 1438.1 | 437.3448 | -437.3448 | 4.214% | 43.7% | 1639.1 | 638.3448 | -638.3448 | 6.151% | 63.79% | 19 | 0 | 0 | 0 | 0
2013-02-22 | 20 | 35548.1973 | 1707.6022 | 1718.3454 | 10.7431 | 1999.2 | 280.8546 | -280.8546 | 2.706% | 16.34% | 2206.1 | 487.7546 | -487.7546 | 4.7% | 28.39% | 20 | 0 | 0 | 0 | 0
2013-02-22 | 21 | 35203.7563 | 2340.0551 | 2361.5021 | 21.447 | 2517.6 | 156.0979 | -156.0979 | 1.504% | 6.61% | 2733.6 | 372.0979 | -372.0979 | 3.585% | 15.76% | 21 | 0 | 1 | 0 | 0
2013-02-22 | 22 | 34542.1302 | 2838.4886 | 2862.7983 | 24.3097 | 2668.6 | 194.1983 | 194.1983 | 1.871% | 6.784% | 2902.3 | 39.5017 | -39.5017 | 0.3806% | 1.38% | 22 | 1 | 1 | 0 | 1
2013-02-22 | 23 | 33154.837 | 2787.1425 | 2810.618 | 23.4755 | 3480.2 | 669.582 | -669.582 | 6.452% | 23.82% | 3661.7 | 851.082 | -851.082 | 8.2% | 30.28% | 23 | 0 | 0 | 0 | 0
2013-02-22 | 24 | 31497.387 | 2584.8286 | 2598.3709 | 13.5423 | 2684 | 85.6291 | -85.6291 | 0.8251% | 3.295% | 2893.4 | 295.0291 | -295.0291 | 2.843% | 11.35% | 24 | 0 | 1 | 0 | 0
2013-02-23 | 1 | 30263.5955 | 2316.6869 | 2341.1609 | 24.4739 | 2647.1 | 305.9391 | -305.9391 | 2.948% | 13.07% | 2859 | 517.8391 | -517.8391 | 4.99% | 22.12% | 1 | 0 | 1 | 0 | 0
2013-02-23 | 2 | 29603.721 | 2151.3778 | 2172.711 | 21.3333 | 2464.3 | 291.589 | -291.589 | 2.81% | 13.42% | 2663.7 | 490.989 | -490.989 | 4.731% | 22.6% | 2 | 0 | 0 | 0 | 0
2013-02-23 | 3 | 29433.2799 | 1779.1756 | 1801.7943 | 22.6187 | 2321.9 | 520.1057 | -520.1057 | 5.011% | 28.87% | 2484.4 | 682.6057 | -682.6057 | 6.577% | 37.88% | 3 | 0 | 0 | 0 | 0
2013-02-23 | 4 | 29591.0257 | 1772.4258 | 1789.4698 | 17.044 | 2647.1 | 857.6302 | -857.6302 | 8.264% | 47.93% | 2787.9 | 998.4302 | -998.4302 | 9.62% | 55.79% | 4 | 0 | 0 | 0 | 0
2013-02-23 | 5 | 30152.1981 | 2222.9869 | 2217.0726 | -5.9143 | 2909.7 | 692.6274 | -692.6274 | 6.674% | 31.24% | 3045.9 | 828.8274 | -828.8274 | 7.986% | 37.38% | 5 | 0 | 0 | 0 | 0
2013-02-23 | 6 | 31457.8618 | 2383.7607 | 2402.5619 | 18.8012 | 2276.6 | 125.9619 | 125.9619 | 1.214% | 5.243% | 2410.7 | 8.1381 | -8.1381 | 0.07841% | 0.3387% | 6 | 1 | 0 | 0 | 1
2013-02-23 | 7 | 33530.685 | 2079.3854 | 2101.2511 | 21.8657 | 2334.7 | 233.4489 | -233.4489 | 2.249% | 11.11% | 2431.1 | 329.8489 | -329.8489 | 3.178% | 15.7% | 7 | 0 | 0 | 0 | 0
2013-02-23 | 8 | 34827.0369 | 1478.9617 | 1485.1946 | 6.2329 | 2368.3 | 883.1054 | -883.1054 | 8.509% | 59.46% | 2444.8 | 959.6054 | -959.6054 | 9.246% | 64.61% | 8 | 0 | 0 | 0 | 0
2013-02-23 | 9 | 35317.5403 | 1270.369 | 1284.2256 | 13.8566 | 2008.9 | 724.6744 | -724.6744 | 6.982% | 56.43% | 2059.9 | 775.6744 | -775.6744 | 7.474% | 60.4% | 9 | 0 | 0 | 0 | 0
2013-02-23 | 10 | 34870.2914 | 1237.8289 | 1248.6629 | 10.8339 | 1426.2 | 177.5371 | -177.5371 | 1.711% | 14.22% | 1456.9 | 208.2371 | -208.2371 | 2.006% | 16.68% | 10 | 0 | 0 | 0 | 0
2013-02-23 | 11 | 33953.9331 | 1683.2087 | 1684.9881 | 1.7794 | 1163.4 | 521.5881 | 521.5881 | 5.026% | 30.96% | 1212.1 | 472.8881 | 472.8881 | 4.556% | 28.06% | 11 | 1 | 0 | 1 | 1
2013-02-23 | 12 | 32842.0137 | 1915.5183 | 1929.7647 | 14.2463 | 1094.5 | 835.2647 | 835.2647 | 8.048% | 43.28% | 1127.4 | 802.3647 | 802.3647 | 7.731% | 41.58% | 12 | 1 | 0 | 1 | 1
2013-02-23 | 13 | 31653.4437 | 2064.3638 | 2072.8762 | 8.5124 | 1199.7 | 873.1762 | 873.1762 | 8.413% | 42.12% | 1247.5 | 825.3762 | 825.3762 | 7.953% | 39.82% | 13 | 1 | 0 | 1 | 1
2013-02-23 | 14 | 30484.7626 | 1957.4553 | 1966.0938 | 8.6386 | 1520.1 | 445.9938 | 445.9938 | 4.297% | 22.68% | 1542.6 | 423.4938 | 423.4938 | 4.08% | 21.54% | 14 | 1 | 0 | 1 | 1
2013-02-23 | 15 | 29681.2346 | 1686.4121 | 1692.3297 | 5.9176 | 1564.4 | 127.9297 | 127.9297 | 1.233% | 7.559% | 1600.1 | 92.2297 | 92.2297 | 0.8887% | 5.45% | 15 | 1 | 0 | 1 | 1
2013-02-23 | 16 | 29207.786 | 1443.2237 | 1454.1886 | 10.9648 | 1602 | 147.8114 | -147.8114 | 1.424% | 10.16% | 1627.7 | 173.5114 | -173.5114 | 1.672% | 11.93% | 16 | 0 | 0 | 0 | 0
2013-02-23 | 17 | 29039.4622 | 1135.4339 | 1138.3141 | 2.8802 | 1566.9 | 428.5859 | -428.5859 | 4.13% | 37.65% | 1588.1 | 449.7859 | -449.7859 | 4.334% | 39.51% | 17 | 0 | 0 | 0 | 0
2013-02-23 | 18 | 29320.1272 | 764.7779 | 773.1874 | 8.4095 | 1401.6 | 628.4126 | -628.4126 | 6.055% | 81.28% | 1424.7 | 651.5126 | -651.5126 | 6.278% | 84.26% | 18 | 0 | 0 | 0 | 0
2013-02-23 | 19 | 30970.6479 | 824.8791 | 835.506 | 10.627 | 1210.2 | 374.694 | -374.694 | 3.61% | 44.85% | 1238.9 | 403.394 | -403.394 | 3.887% | 48.28% | 19 | 0 | 0 | 0 | 0
2013-02-23 | 20 | 32278.5588 | 1696.6178 | 1706.1244 | 9.5066 | 1580.3 | 125.8244 | 125.8244 | 1.212% | 7.375% | 1635.8 | 70.3244 | 70.3244 | 0.6776% | 4.122% | 20 | 1 | 0 | 1 | 1
2013-02-23 | 21 | 32130.4143 | 3141.168 | 3146.6584 | 5.4905 | 2595.1 | 551.5584 | 551.5584 | 5.314% | 17.53% | 2671 | 475.6584 | 475.6584 | 4.583% | 15.12% | 21 | 1 | 0 | 1 | 1
2013-02-23 | 22 | 31653.1446 | 4713.5304 | 4715.1569 | 1.6265 | 3765.8 | 949.3569 | 949.3569 | 9.147% | 20.13% | 3864.6 | 850.5569 | 850.5569 | 8.195% | 18.04% | 22 | 1 | 0 | 1 | 1
2013-02-23 | 23 | 30601.9734 | 6288.0616 | 6470.8479 | 182.7862 | 4827.2 | 1643.6479 | 1643.6479 | 15.84% | 25.4% | 4937.5 | 1533.3479 | 1533.3479 | 14.77% | 23.7% | 23 | 1 | 0 | 1 | 1
2013-02-23 | 24 | 29407.2805 | 6888.9217 | 7267.9405 | 379.0189 | 5754.8 | 1513.1405 | 1513.1405 | 14.58% | 20.82% | 5837.8 | 1430.1405 | 1430.1405 | 13.78% | 19.68% | 24 | 1 | 0 | 1 | 1
2013-02-24 | 1 | 28512.7827 | 7126.0257 | 7308.1118 | 182.086 | 6190.9 | 1117.2118 | 1117.2118 | 10.76% | 15.29% | 6251.8 | 1056.3118 | 1056.3118 | 10.18% | 14.45% | 1 | 1 | 0 | 1 | 1
2013-02-24 | 2 | 28019.1227 | 7083.3214 | 7187.9234 | 104.602 | 6728.2 | 459.7234 | 459.7234 | 4.43% | 6.396% | 6775 | 412.9234 | 412.9234 | 3.979% | 5.745% | 2 | 1 | 0 | 1 | 1
2013-02-24 | 3 | 27939.1381 | 6958.6858 | 7064.0606 | 105.3748 | 6750 | 314.0606 | 314.0606 | 3.026% | 4.446% | 6780.1 | 283.9606 | 283.9606 | 2.736% | 4.02% | 3 | 1 | 0 | 1 | 1
2013-02-24 | 4 | 28021.302 | 6804.3405 | 6905.1486 | 100.8081 | 6495.1 | 410.0486 | 410.0486 | 3.951% | 5.938% | 6568.9 | 336.2486 | 336.2486 | 3.24% | 4.87% | 4 | 1 | 0 | 1 | 1
2013-02-24 | 5 | 28446.3295 | 6962.7988 | 7060.4863 | 97.6876 | 6365.8 | 694.6863 | 694.6863 | 6.694% | 9.839% | 6427.2 | 633.2863 | 633.2863 | 6.102% | 8.969% | 5 | 1 | 0 | 1 | 1
2013-02-24 | 6 | 29483.9501 | 6997.3455 | 7092.9797 | 95.6341 | 6459 | 633.9797 | 633.9797 | 6.109% | 8.938% | 6520.3 | 572.6797 | 572.6797 | 5.518% | 8.074% | 6 | 1 | 0 | 1 | 1
2013-02-24 | 7 | 30833.389 | 6624.0569 | 6750.407 | 126.3501 | 6562 | 188.407 | 188.407 | 1.815% | 2.791% | 6611.8 | 138.607 | 138.607 | 1.336% | 2.053% | 7 | 1 | 0 | 1 | 1
2013-02-24 | 8 | 31631.1029 | 6544.3876 | 6681.0807 | 136.6931 | 6581.3 | 99.7807 | 99.7807 | 0.9614% | 1.493% | 6643.5 | 37.5807 | 37.5807 | 0.3621% | 0.5625% | 8 | 1 | 0 | 1 | 1
2013-02-24 | 9 | 31963.6891 | 5975.0172 | 6044.1256 | 69.1083 | 6206.2 | 162.0744 | -162.0744 | 1.562% | 2.682% | 6259.9 | 215.7744 | -215.7744 | 2.079% | 3.57% | 9 | 0 | 0 | 0 | 0
2013-02-24 | 10 | 31526.7929 | 5750.139 | 5809.578 | 59.439 | 5723.9 | 85.678 | 85.678 | 0.8255% | 1.475% | 5789.9 | 19.678 | 19.678 | 0.1896% | 0.3387% | 10 | 1 | 0 | 1 | 1
2013-02-24 | 11 | 30670.0519 | 6178.9483 | 6232.172 | 53.2238 | 5431.4 | 800.772 | 800.772 | 7.716% | 12.85% | 5453.2 | 778.972 | 778.972 | 7.506% | 12.5% | 11 | 1 | 0 | 1 | 1
2013-02-24 | 12 | 29703.5986 | 5720.8749 | 5736.6369 | 15.762 | 4892.7 | 843.9369 | 843.9369 | 8.132% | 14.71% | 4945 | 791.6369 | 791.6369 | 7.628% | 13.8% | 12 | 1 | 0 | 1 | 1
2013-02-24 | 13 | 29108.5208 | 4548.0174 | 4547.321 | -0.69641 | 4757.1 | 209.779 | -209.779 | 2.021% | 4.613% | 4828.7 | 281.379 | -281.379 | 2.711% | 6.188% | 13 | 0 | 0 | 0 | 0
2013-02-24 | 14 | 28598.9055 | 3680.373 | 3678.132 | -2.2409 | 4764.3 | 1086.168 | -1086.168 | 10.47% | 29.53% | 4860.2 | 1182.068 | -1182.068 | 11.39% | 32.14% | 14 | 0 | 0 | 0 | 0
2013-02-24 | 15 | 28320.3554 | 3241.9456 | 3239.9664 | -1.9792 | 5034.3 | 1794.3336 | -1794.3336 | 17.29% | 55.38% | 5157.7 | 1917.7336 | -1917.7336 | 18.48% | 59.19% | 15 | 0 | 0 | 0 | 0
2013-02-24 | 16 | 28175.0441 | 3390.204 | 3403.44 | 13.236 | 4810 | 1406.56 | -1406.56 | 13.55% | 41.33% | 4950.3 | 1546.86 | -1546.86 | 14.9% | 45.45% | 16 | 0 | 0 | 0 | 0
2013-02-24 | 17 | 28458.4254 | 3831.6541 | 3853.48 | 21.8258 | 4288.1 | 434.62 | -434.62 | 4.188% | 11.28% | 4445.2 | 591.72 | -591.72 | 5.701% | 15.36% | 17 | 0 | 0 | 0 | 0
2013-02-24 | 18 | 29282.4711 | 4362.9445 | 4436.4379 | 73.4935 | 3938.1 | 498.3379 | 498.3379 | 4.802% | 11.23% | 4055.7 | 380.7379 | 380.7379 | 3.669% | 8.582% | 18 | 1 | 0 | 1 | 1
2013-02-24 | 19 | 31299.3971 | 4179.1306 | 4284.2382 | 105.1076 | 4274.8 | 9.4382 | 9.4382 | 0.09094% | 0.2203% | 4431.8 | 147.5618 | -147.5618 | 1.422% | 3.444% | 19 | 1 | 0 | 0 | 1
2013-02-24 | 20 | 32525.7982 | 5045.4022 | 5063.3433 | 17.9411 | 5176.6 | 113.2567 | -113.2567 | 1.091% | 2.237% | 5375.6 | 312.2567 | -312.2567 | 3.009% | 6.167% | 20 | 0 | 0 | 0 | 0
2013-02-24 | 21 | 32087.4572 | 6198.3072 | 6250.091 | 51.7838 | 5334.6 | 915.491 | 915.491 | 8.821% | 14.65% | 5545.5 | 704.591 | 704.591 | 6.789% | 11.27% | 21 | 1 | 1 | 1 | 1
2013-02-24 | 22 | 31025.7876 | 6864.3376 | 7072.2175 | 207.8799 | 5800.5 | 1271.7175 | 1271.7175 | 12.25% | 17.98% | 6010 | 1062.2175 | 1062.2175 | 10.23% | 15.02% | 22 | 1 | 1 | 1 | 1
2013-02-24 | 23 | 29015.4387 | 6883.4492 | 7246.2121 | 362.7629 | 6454.2 | 792.0121 | 792.0121 | 7.631% | 10.93% | 6627.7 | 618.5121 | 618.5121 | 5.96% | 8.536% | 23 | 1 | 0 | 1 | 1
2013-02-24 | 24 | 26987.5025 | 6721.3287 | 6945.8422 | 224.5136 | 6772.4 | 173.4422 | 173.4422 | 1.671% | 2.497% | 6902.7 | 43.1422 | 43.1422 | 0.4157% | 0.6211% | 24 | 1 | 0 | 1 | 1
2013-02-25 | 1 | 25432.4423 | 6663.8542 | 7007.6253 | 343.771 | 6801.4 | 206.2253 | 206.2253 | 1.987% | 2.943% | 6872 | 135.6253 | 135.6253 | 1.307% | 1.935% | 1 | 1 | 0 | 1 | 1
2013-02-25 | 2 | 24573.6818 | 6297.6581 | 6532.6465 | 234.9884 | 7058.7 | 526.0535 | -526.0535 | 5.069% | 8.053% | 7091.6 | 558.9535 | -558.9535 | 5.386% | 8.556% | 2 | 0 | 0 | 0 | 0
2013-02-25 | 3 | 24070.8425 | 5375.9902 | 5477.3153 | 101.3251 | 6588.3 | 1110.9847 | -1110.9847 | 10.7% | 20.28% | 6701.6 | 1224.2847 | -1224.2847 | 11.8% | 22.35% | 3 | 0 | 0 | 0 | 0
2013-02-25 | 4 | 24025.3587 | 3413.9581 | 3518.4315 | 104.4734 | 5797.9 | 2279.4685 | -2279.4685 | 21.96% | 64.79% | 5998.4 | 2479.9685 | -2479.9685 | 23.9% | 70.49% | 4 | 0 | 0 | 0 | 0
2013-02-25 | 5 | 24820.6626 | 2766.475 | 2885.8271 | 119.3521 | 5245.2 | 2359.3729 | -2359.3729 | 22.73% | 81.76% | 5544.3 | 2658.4729 | -2658.4729 | 25.62% | 92.12% | 5 | 0 | 1 | 0 | 0
2013-02-25 | 6 | 27149.6563 | 3224.0173 | 3426.2416 | 202.2243 | 5174.7 | 1748.4584 | -1748.4584 | 16.85% | 51.03% | 5457.7 | 2031.4584 | -2031.4584 | 19.57% | 59.29% | 6 | 0 | 1 | 0 | 0
2013-02-25 | 7 | 31252.5413 | 4155.1027 | 4259.8608 | 104.7581 | 5489.8 | 1229.9392 | -1229.9392 | 11.85% | 28.87% | 5821.4 | 1561.5392 | -1561.5392 | 15.05% | 36.66% | 7 | 0 | 1 | 0 | 0
2013-02-25 | 8 | 32741.3895 | 5144.9093 | 5278.5549 | 133.6456 | 5992.6 | 714.0451 | -714.0451 | 6.88% | 13.53% | 6325.4 | 1046.8451 | -1046.8451 | 10.09% | 19.83% | 8 | 0 | 1 | 0 | 0
2013-02-25 | 9 | 32567.9227 | 6153.6543 | 6661.3222 | 507.6679 | 6693.3 | 31.9778 | -31.9778 | 0.3081% | 0.4801% | 7036 | 374.6778 | -374.6778 | 3.61% | 5.625% | 9 | 0 | 1 | 0 | 0
2013-02-25 | 10 | 32950.995 | 6887.0661 | 8153.3196 | 1266.2536 | 7217.2 | 936.1196 | 936.1196 | 9.02% | 11.48% | 7555 | 598.3196 | 598.3196 | 5.765% | 7.338% | 10 | 1 | 1 | 1 | 1
2013-02-25 | 11 | 33312.3235 | 7339.7558 | 8331.9491 | 992.1933 | 7553.8 | 778.1491 | 778.1491 | 7.498% | 9.339% | 7882 | 449.9491 | 449.9491 | 4.335% | 5.4% | 11 | 1 | 1 | 1 | 1
2013-02-25 | 12 | 33237.1516 | 7633.9786 | 8444.5037 | 810.5251 | 8093 | 351.5037 | 351.5037 | 3.387% | 4.163% | 8337 | 107.5037 | 107.5037 | 1.036% | 1.273% | 12 | 1 | 1 | 1 | 1
2013-02-25 | 13 | 32991.5782 | 7602.6192 | 8098.6945 | 496.0753 | 8614.2 | 515.5055 | -515.5055 | 4.967% | 6.365% | 8882.9 | 784.2055 | -784.2055 | 7.556% | 9.683% | 13 | 0 | 1 | 0 | 0
2013-02-25 | 14 | 32850.8685 | 7475.9805 | 7902.2905 | 426.31 | 8638.5 | 736.2095 | -736.2095 | 7.094% | 9.316% | 8931.3 | 1029.0095 | -1029.0095 | 9.915% | 13.02% | 14 | 0 | 1 | 0 | 0
2013-02-25 | 15 | 32553.1723 | 7413.5689 | 7864.4052 | 450.8363 | 8570 | 705.5948 | -705.5948 | 6.799% | 8.972% | 8864.9 | 1000.4948 | -1000.4948 | 9.64% | 12.72% | 15 | 0 | 1 | 0 | 0
2013-02-25 | 16 | 32498.8966 | 7539.8173 | 7809.6877 | 269.8705 | 8470.7 | 661.0123 | -661.0123 | 6.369% | 8.464% | 8940.6 | 1130.9123 | -1130.9123 | 10.9% | 14.48% | 16 | 0 | 1 | 0 | 0
2013-02-25 | 17 | 32903.503 | 7776.2284 | 8149.8306 | 373.6022 | 8399.7 | 249.8694 | -249.8694 | 2.408% | 3.066% | 8749.9 | 600.0694 | -600.0694 | 5.782% | 7.363% | 17 | 0 | 1 | 0 | 0
2013-02-25 | 18 | 33812.291 | 8089.4667 | 8413.6018 | 324.1351 | 8304.3 | 109.3018 | 109.3018 | 1.053% | 1.299% | 8640.2 | 226.5982 | -226.5982 | 2.183% | 2.693% | 18 | 1 | 1 | 0 | 1
2013-02-25 | 19 | 36480.2327 | 8104.5321 | 8388.4067 | 283.8746 | 8033.3 | 355.1067 | 355.1067 | 3.422% | 4.233% | 8375.3 | 13.1067 | 13.1067 | 0.1263% | 0.1562% | 19 | 1 | 1 | 1 | 1
2013-02-25 | 20 | 38200.7685 | 7958.2746 | 8164.9976 | 206.723 | 7961.7 | 203.2976 | 203.2976 | 1.959% | 2.49% | 8284.8 | 119.8024 | -119.8024 | 1.154% | 1.467% | 20 | 1 | 1 | 0 | 1
2013-02-25 | 21 | 38125.3658 | 7888.566 | 8006.4819 | 117.9159 | 7629.7 | 376.7819 | 376.7819 | 3.63% | 4.706% | 8014.1 | 7.6181 | -7.6181 | 0.0734% | 0.09515% | 21 | 1 | 1 | 0 | 1
2013-02-25 | 22 | 37203.1752 | 7693.1904 | 7775.7434 | 82.553 | 7512.9 | 262.8434 | 262.8434 | 2.533% | 3.38% | 7841 | 65.2566 | -65.2566 | 0.6288% | 0.8392% | 22 | 1 | 1 | 0 | 1
2013-02-25 | 23 | 34985.7876 | 7159.8229 | 7258.5475 | 98.7246 | 7208 | 50.5475 | 50.5475 | 0.487% | 0.6964% | 7540.9 | 282.3525 | -282.3525 | 2.721% | 3.89% | 23 | 1 | 1 | 0 | 1
2013-02-25 | 24 | 32638.893 | 6726.8212 | 6855.8926 | 129.0714 | 6827.6 | 28.2926 | 28.2926 | 0.2726% | 0.4127% | 7162.4 | 306.5074 | -306.5074 | 2.953% | 4.471% | 24 | 1 | 1 | 0 | 1
2013-02-26 | 1 | 31297.2967 | 6117.9868 | 6213.4943 | 95.5075 | 6384.6 | 171.1057 | -171.1057 | 1.649% | 2.754% | 6664.1 | 450.6057 | -450.6057 | 4.342% | 7.252% | 1 | 0 | 1 | 0 | 0
2013-02-26 | 2 | 30675.3393 | 5609.3332 | 5671.0811 | 61.748 | 6049.6 | 378.5189 | -378.5189 | 3.647% | 6.675% | 6302.8 | 631.7189 | -631.7189 | 6.087% | 11.14% | 2 | 0 | 1 | 0 | 0
2013-02-26 | 3 | 30527.0505 | 5407.4037 | 5468.9094 | 61.5057 | 5618.8 | 149.8906 | -149.8906 | 1.444% | 2.741% | 5848.9 | 379.9906 | -379.9906 | 3.661% | 6.948% | 3 | 0 | 1 | 0 | 0
2013-02-26 | 4 | 30757.3262 | 4434.105 | 4511.7052 | 77.6002 | 4955 | 443.2948 | -443.2948 | 4.271% | 9.825% | 5145.1 | 633.3948 | -633.3948 | 6.103% | 14.04% | 4 | 0 | 0 | 0 | 0
2013-02-26 | 5 | 31949.114 | 3209.8672 | 3262.151 | 52.2838 | 4031.3 | 769.149 | -769.149 | 7.411% | 23.58% | 4234.3 | 972.149 | -972.149 | 9.367% | 29.8% | 5 | 0 | 0 | 0 | 0
2013-02-26 | 6 | 34888.0807 | 2552.4278 | 2592.1746 | 39.7469 | 3851.6 | 1259.4254 | -1259.4254 | 12.13% | 48.59% | 4032.8 | 1440.6254 | -1440.6254 | 13.88% | 55.58% | 6 | 0 | 0 | 0 | 0
2013-02-26 | 7 | 39542.3472 | 2195.7389 | 2235.8291 | 40.0902 | 3322.9 | 1087.0709 | -1087.0709 | 10.47% | 48.62% | 3482.7 | 1246.8709 | -1246.8709 | 12.01% | 55.77% | 7 | 0 | 0 | 0 | 0
2013-02-26 | 8 | 40293.6138 | 1840.013 | 1885.1726 | 45.1596 | 2679.9 | 794.7274 | -794.7274 | 7.657% | 42.16% | 2838.6 | 953.4274 | -953.4274 | 9.187% | 50.58% | 8 | 0 | 0 | 0 | 0
2013-02-26 | 9 | 38836.0289 | 1116.6222 | 1165.4488 | 48.8266 | 1687.5 | 522.0512 | -522.0512 | 5.03% | 44.79% | 1799.8 | 634.3512 | -634.3512 | 6.112% | 54.43% | 9 | 0 | 0 | 0 | 0
2013-02-26 | 10 | 37729.9222 | 566.3921 | 614.59 | 48.1979 | 1243.9 | 629.31 | -629.31 | 6.064% | 102.4% | 1299.2 | 684.61 | -684.61 | 6.596% | 111.4% | 10 | 0 | 0 | 0 | 0
2013-02-26 | 11 | 36478.6128 | 357.3032 | 406.2937 | 48.9905 | 970.2 | 563.9063 | -563.9063 | 5.433% | 138.8% | 996.6 | 590.3063 | -590.3063 | 5.688% | 145.3% | 11 | 0 | 0 | 0 | 0
2013-02-26 | 12 | 35137.5792 | 307.142 | 356.4037 | 49.2617 | 707.7 | 351.2963 | -351.2963 | 3.385% | 98.57% | 721 | 364.5963 | -364.5963 | 3.513% | 102.3% | 12 | 0 | 0 | 0 | 0
2013-02-26 | 13 | 33922.7458 | 291.8851 | 336.014 | 44.1289 | 594.8 | 258.786 | -258.786 | 2.493% | 77.02% | 592.2 | 256.186 | -256.186 | 2.468% | 76.24% | 13 | 0 | 0 | 0 | 0
2013-02-26 | 14 | 33034.6196 | 372.2873 | 418.7114 | 46.4241 | 699.9 | 281.1886 | -281.1886 | 2.709% | 67.16% | 669.1 | 250.3886 | -250.3886 | 2.413% | 59.8% | 14 | 0 | 0 | 0 | 0
2013-02-26 | 15 | 32197.3941 | 445.9569 | 496.4584 | 50.5015 | 716.5 | 220.0416 | -220.0416 | 2.12% | 44.32% | 718.4 | 221.9416 | -221.9416 | 2.138% | 44.7% | 15 | 0 | 0 | 0 | 0
2013-02-26 | 16 | 31618.1679 | 493.257 | 530.7622 | 37.5052 | 694.2 | 163.4378 | -163.4378 | 1.575% | 30.79% | 689.7 | 158.9378 | -158.9378 | 1.531% | 29.95% | 16 | 0 | 0 | 0 | 0
2013-02-26 | 17 | 31482.2658 | 689.2988 | 720.5127 | 31.2139 | 787.8 | 67.2873 | -67.2873 | 0.6483% | 9.339% | 810.9 | 90.3873 | -90.3873 | 0.8709% | 12.54% | 17 | 0 | 0 | 0 | 0
2013-02-26 | 18 | 31702.3774 | 901.873 | 967.8031 | 65.9301 | 773.1 | 194.7031 | 194.7031 | 1.876% | 20.12% | 835.6 | 132.2031 | 132.2031 | 1.274% | 13.66% | 18 | 1 | 0 | 1 | 1
2013-02-26 | 19 | 33849.0462 | 1621.2431 | 1673.8178 | 52.5746 | 1226.4 | 447.4178 | 447.4178 | 4.311% | 26.73% | 1301.2 | 372.6178 | 372.6178 | 3.59% | 22.26% | 19 | 1 | 0 | 1 | 1
2013-02-26 | 20 | 35391.2389 | 2451.51 | 2492.085 | 40.5751 | 1931.2 | 560.885 | 560.885 | 5.404% | 22.51% | 2024 | 468.085 | 468.085 | 4.51% | 18.78% | 20 | 1 | 0 | 1 | 1
2013-02-26 | 21 | 35299.5082 | 3658.0559 | 3701.9713 | 43.9155 | 2950.6 | 751.3713 | 751.3713 | 7.24% | 20.3% | 3025.1 | 676.8713 | 676.8713 | 6.522% | 18.28% | 21 | 1 | 0 | 1 | 1
2013-02-26 | 22 | 34192.0557 | 4976.8143 | 5068.2544 | 91.4401 | 3384.2 | 1684.0544 | 1684.0544 | 16.23% | 33.23% | 3538.9 | 1529.3544 | 1529.3544 | 14.74% | 30.18% | 22 | 1 | 0 | 1 | 1
2013-02-26 | 23 | 32108.3911 | 5804.9813 | 5926.7544 | 121.7731 | 4065.9 | 1860.8544 | 1860.8544 | 17.93% | 31.4% | 4214.8 | 1711.9544 | 1711.9544 | 16.5% | 28.89% | 23 | 1 | 0 | 1 | 1
2013-02-26 | 24 | 30002.5091 | 5991.0632 | 6034.5581 | 43.4949 | 4671.7 | 1362.8581 | 1362.8581 | 13.13% | 22.58% | 4762.2 | 1272.3581 | 1272.3581 | 12.26% | 21.08% | 24 | 1 | 0 | 1 | 1
2013-02-27 | 1 | 28783.5627 | 5089.5406 | 5114.3323 | 24.7917 | 4786.7 | 327.6323 | 327.6323 | 3.157% | 6.406% | 4857.3 | 257.0323 | 257.0323 | 2.477% | 5.026% | 1 | 1 | 0 | 1 | 1
2013-02-27 | 2 | 28368.0596 | 4939.531 | 5010.9231 | 71.3921 | 5111.8 | 100.8769 | -100.8769 | 0.972% | 2.013% | 5138.7 | 127.7769 | -127.7769 | 1.231% | 2.55% | 2 | 0 | 0 | 0 | 0
2013-02-27 | 3 | 28409.2591 | 5222.4971 | 5353.1172 | 130.6201 | 4859.5 | 493.6172 | 493.6172 | 4.756% | 9.221% | 4918.9 | 434.2172 | 434.2172 | 4.184% | 8.111% | 3 | 1 | 0 | 1 | 1
2013-02-27 | 4 | 28918.3907 | 6253.6254 | 6453.2112 | 199.5858 | 4611.2 | 1842.0112 | 1842.0112 | 17.75% | 28.54% | 4757.1 | 1696.1112 | 1696.1112 | 16.34% | 26.28% | 4 | 1 | 0 | 1 | 1
2013-02-27 | 5 | 30138.3021 | 5410.8699 | 5568.436 | 157.5661 | 5314.9 | 253.536 | 253.536 | 2.443% | 4.553% | 5371 | 197.436 | 197.436 | 1.902% | 3.546% | 5 | 1 | 0 | 1 | 1
2013-02-27 | 6 | 33129.6076 | 4444.27 | 4607.1782 | 162.9083 | 4825.2 | 218.0218 | -218.0218 | 2.101% | 4.732% | 4933.9 | 326.7218 | -326.7218 | 3.148% | 7.092% | 6 | 0 | 0 | 0 | 0
2013-02-27 | 7 | 37771.5201 | 4174.0942 | 4340.9937 | 166.8995 | 4646 | 305.0063 | -305.0063 | 2.939% | 7.026% | 4686.9 | 345.9063 | -345.9063 | 3.333% | 7.968% | 7 | 0 | 0 | 0 | 0
2013-02-27 | 8 | 38348.0729 | 4067.0175 | 4223.4305 | 156.4129 | 3860.6 | 362.8305 | 362.8305 | 3.496% | 8.591% | 3886.3 | 337.1305 | 337.1305 | 3.248% | 7.982% | 8 | 1 | 0 | 1 | 1
2013-02-27 | 9 | 36775.8158 | 3615.5188 | 3776.4331 | 160.9144 | 3448 | 328.4331 | 328.4331 | 3.165% | 8.697% | 3576.9 | 199.5331 | 199.5331 | 1.923% | 5.284% | 9 | 1 | 0 | 1 | 1
2013-02-27 | 10 | 35676.8496 | 4947.3226 | 5119.9774 | 172.6548 | 3773.7 | 1346.2774 | 1346.2774 | 12.97% | 26.29% | 3913.5 | 1206.4774 | 1206.4774 | 11.62% | 23.56% | 10 | 1 | 0 | 1 | 1
2013-02-27 | 11 | 34851.2324 | 4989.6617 | 5145.8814 | 156.2197 | 4262.4 | 883.4814 | 883.4814 | 8.513% | 17.17% | 4420 | 725.8814 | 725.8814 | 6.994% | 14.11% | 11 | 1 | 0 | 1 | 1
2013-02-27 | 12 | 34020.0653 | 5184.6139 | 5330.506 | 145.8921 | 4044.2 | 1286.306 | 1286.306 | 12.39% | 24.13% | 4210.5 | 1120.006 | 1120.006 | 10.79% | 21.01% | 12 | 1 | 0 | 1 | 1
2013-02-27 | 13 | 33270.3308 | 5146.6253 | 5294.4175 | 147.7922 | 4373.4 | 921.0175 | 921.0175 | 8.874% | 17.4% | 4538.5 | 755.9175 | 755.9175 | 7.283% | 14.28% | 13 | 1 | 0 | 1 | 1
2013-02-27 | 14 | 32778.2137 | 5125.8686 | 5271.5867 | 145.7181 | 4185.8 | 1085.7867 | 1085.7867 | 10.46% | 20.6% | 4366.9 | 904.6867 | 904.6867 | 8.717% | 17.16% | 14 | 1 | 0 | 1 | 1
2013-02-27 | 15 | 32254.3268 | 5197.6725 | 5338.1196 | 140.4471 | 4436.8 | 901.3196 | 901.3196 | 8.684% | 16.88% | 4643.6 | 694.5196 | 694.5196 | 6.692% | 13.01% | 15 | 1 | 0 | 1 | 1
2013-02-27 | 16 | 31874.7826 | 4940.1299 | 5060.3724 | 120.2425 | 4243 | 817.3724 | 817.3724 | 7.876% | 16.15% | 4445.4 | 614.9724 | 614.9724 | 5.925% | 12.15% | 16 | 1 | 0 | 1 | 1
2013-02-27 | 17 | 31973.9558 | 4375.3191 | 4451.4739 | 76.1548 | 4099.5 | 351.9739 | 351.9739 | 3.391% | 7.907% | 4310.6 | 140.8739 | 140.8739 | 1.357% | 3.165% | 17 | 1 | 1 | 1 | 1
2013-02-27 | 18 | 32429.9167 | 3947.5439 | 4012.9784 | 65.4344 | 3743.2 | 269.7784 | 269.7784 | 2.599% | 6.723% | 3935.4 | 77.5784 | 77.5784 | 0.7475% | 1.933% | 18 | 1 | 0 | 1 | 1
2013-02-27 | 19 | 34745.711 | 3043.1115 | 3100.7898 | 57.6783 | 3096.8 | 3.9898 | 3.9898 | 0.03844% | 0.1287% | 3308.8 | 208.0102 | -208.0102 | 2.004% | 6.708% | 19 | 1 | 1 | 0 | 1
2013-02-27 | 20 | 36640.0957 | 2605.8029 | 2657.4659 | 51.663 | 2954.5 | 297.0341 | -297.0341 | 2.862% | 11.18% | 3107 | 449.5341 | -449.5341 | 4.331% | 16.92% | 20 | 0 | 0 | 0 | 0
2013-02-27 | 21 | 36636.1596 | 2458.0992 | 2501.8537 | 43.7545 | 2792.5 | 290.6463 | -290.6463 | 2.8% | 11.62% | 2954.5 | 452.6463 | -452.6463 | 4.361% | 18.09% | 21 | 0 | 0 | 0 | 0
2013-02-27 | 22 | 35666.8778 | 2325.9086 | 2344.0299 | 18.1213 | 2340.1 | 3.9299 | 3.9299 | 0.03787% | 0.1677% | 2565.9 | 221.8701 | -221.8701 | 2.138% | 9.465% | 22 | 1 | 1 | 0 | 1
2013-02-27 | 23 | 33712.888 | 2448.4928 | 2483.4708 | 34.978 | 1938.9 | 544.5708 | 544.5708 | 5.247% | 21.93% | 2212.9 | 270.5708 | 270.5708 | 2.607% | 10.89% | 23 | 1 | 1 | 1 | 1
2013-02-27 | 24 | 31667.9323 | 2544.2869 | 2589.2299 | 44.943 | 1823.8 | 765.4299 | 765.4299 | 7.375% | 29.56% | 2062.6 | 526.6299 | 526.6299 | 5.074% | 20.34% | 24 | 1 | 1 | 1 | 1
2013-02-28 | 1 | 30668.8242 | 2279.1801 | 2307.6518 | 28.4717 | 1702.6 | 605.0518 | 605.0518 | 5.83% | 26.22% | 1926.3 | 381.3518 | 381.3518 | 3.674% | 16.53% | 1 | 1 | 1 | 1 | 1
2013-02-28 | 2 | 30415.7135 | 2007.557 | 2060.7251 | 53.1681 | 1729.7 | 331.0251 | 331.0251 | 3.19% | 16.06% | 1968.3 | 92.4251 | 92.4251 | 0.8905% | 4.485% | 2 | 1 | 1 | 1 | 1
2013-02-28 | 3 | 30471.7114 | 1799.015 | 1863.7199 | 64.7049 | 1908.3 | 44.5801 | -44.5801 | 0.4295% | 2.392% | 2132 | 268.2801 | -268.2801 | 2.585% | 14.39% | 3 | 0 | 1 | 0 | 0
2013-02-28 | 4 | 31001.7407 | 1656.5428 | 1722.0771 | 65.5342 | 1527.1 | 194.9771 | 194.9771 | 1.879% | 11.32% | 1780.1 | 58.0229 | -58.0229 | 0.5591% | 3.369% | 4 | 1 | 1 | 0 | 1
2013-02-28 | 5 | 32336.4968 | 1707.4311 | 1774.3965 | 66.9654 | 1748.3 | 26.0965 | 26.0965 | 0.2514% | 1.471% | 1985.4 | 211.0035 | -211.0035 | 2.033% | 11.89% | 5 | 1 | 1 | 0 | 1
2013-02-28 | 6 | 35388.0959 | 1736.8735 | 1806.1571 | 69.2836 | 1751.1 | 55.0571 | 55.0571 | 0.5305% | 3.048% | 2014.9 | 208.7429 | -208.7429 | 2.011% | 11.56% | 6 | 1 | 1 | 0 | 1
2013-02-28 | 7 | 40081.2223 | 1587.7821 | 1660.2065 | 72.4244 | 1749.6 | 89.3935 | -89.3935 | 0.8613% | 5.384% | 2006 | 345.7935 | -345.7935 | 3.332% | 20.83% | 7 | 0 | 1 | 0 | 0
2013-02-28 | 8 | 40736.9259 | 1501.5728 | 1583.2983 | 81.7255 | 1576.7 | 6.5983 | 6.5983 | 0.06358% | 0.4167% | 1795 | 211.7017 | -211.7017 | 2.04% | 13.37% | 8 | 1 | 1 | 0 | 1
2013-02-28 | 9 | 39013.6688 | 1387.9523 | 1457.5163 | 69.564 | 1447 | 10.5163 | 10.5163 | 0.1013% | 0.7215% | 1641.6 | 184.0837 | -184.0837 | 1.774% | 12.63% | 9 | 1 | 0 | 0 | 1
2013-02-28 | 10 | 37929.9673 | 1379.1101 | 1449.6789 | 70.5688 | 1209.2 | 240.4789 | 240.4789 | 2.317% | 16.59% | 1384.5 | 65.1789 | 65.1789 | 0.628% | 4.496% | 10 | 1 | 0 | 1 | 1
2013-02-28 | 11 | 36850.0684 | 1577.9597 | 1640.2344 | 62.2747 | 875.1 | 765.1344 | 765.1344 | 7.372% | 46.65% | 1036.2 | 604.0344 | 604.0344 | 5.82% | 36.83% | 11 | 1 | 0 | 1 | 1
2013-02-28 | 12 | 35654.2976 | 1440.7163 | 1493.2397 | 52.5235 | 910.7 | 582.5397 | 582.5397 | 5.613% | 39.01% | 1042.1 | 451.1397 | 451.1397 | 4.347% | 30.21% | 12 | 1 | 0 | 1 | 1
2013-02-28 | 13 | 34429.5681 | 1216.8857 | 1266.2054 | 49.3196 | 858.1 | 408.1054 | 408.1054 | 3.932% | 32.23% | 995 | 271.2054 | 271.2054 | 2.613% | 21.42% | 13 | 1 | 0 | 1 | 1
2013-02-28 | 14 | 33398.1186 | 1078.4228 | 1135.9324 | 57.5096 | 990.3 | 145.6324 | 145.6324 | 1.403% | 12.82% | 1115.5 | 20.4324 | 20.4324 | 0.1969% | 1.799% | 14 | 1 | 0 | 1 | 1
2013-02-28 | 15 | 32486.3833 | 1066.0537 | 1115.0131 | 48.9594 | 1056.3 | 58.7131 | 58.7131 | 0.5657% | 5.266% | 1186.4 | 71.3869 | -71.3869 | 0.6878% | 6.402% | 15 | 1 | 0 | 0 | 1
2013-02-28 | 16 | 31882.8706 | 1375.9293 | 1419.0404 | 43.1111 | 942 | 477.0404 | 477.0404 | 4.596% | 33.62% | 1060.4 | 358.6404 | 358.6404 | 3.456% | 25.27% | 16 | 1 | 0 | 1 | 1
2013-02-28 | 17 | 31848.4338 | 1540.6148 | 1588.1049 | 47.4901 | 903.1 | 685.0049 | 685.0049 | 6.6% | 43.13% | 1040.2 | 547.9049 | 547.9049 | 5.279% | 34.5% | 17 | 1 | 0 | 1 | 1
2013-02-28 | 18 | 32441.5538 | 1296.7393 | 1346.4567 | 49.7174 | 803.4 | 543.0567 | 543.0567 | 5.233% | 40.33% | 923.2 | 423.2567 | 423.2567 | 4.078% | 31.43% | 18 | 1 | 0 | 1 | 1
2013-02-28 | 19 | 34824.421 | 739.117 | 785.2832 | 46.1662 | 918.8 | 133.5168 | -133.5168 | 1.286% | 17% | 1012.8 | 227.5168 | -227.5168 | 2.192% | 28.97% | 19 | 0 | 0 | 0 | 0
2013-02-28 | 20 | 36881.83 | 393.0292 | 441.9124 | 48.8832 | 1169.6 | 727.6876 | -727.6876 | 7.011% | 164.7% | 1237.8 | 795.8876 | -795.8876 | 7.669% | 180.1% | 20 | 0 | 0 | 0 | 0
2013-02-28 | 21 | 37045.7765 | 372.8689 | 423.0513 | 50.1824 | 1157.8 | 734.7487 | -734.7487 | 7.08% | 173.7% | 1214.7 | 791.6487 | -791.6487 | 7.628% | 187.1% | 21 | 0 | 0 | 0 | 0
2013-02-28 | 22 | 36205.1348 | 471.4444 | 527.1787 | 55.7342 | 904.9 | 377.7213 | -377.7213 | 3.639% | 71.65% | 1020.4 | 493.2213 | -493.2213 | 4.752% | 93.56% | 22 | 0 | 0 | 0 | 0
2013-02-28 | 23 | 34179.6043 | 598.9939 | 640.4822 | 41.4884 | 779.1 | 138.6178 | -138.6178 | 1.336% | 21.64% | 892.5 | 252.0178 | -252.0178 | 2.428% | 39.35% | 23 | 0 | 0 | 0 | 0
2013-02-28 | 24 | 32235.7768 | 508.2068 | 549.2178 | 41.011 | 867.2 | 317.9822 | -317.9822 | 3.064% | 57.9% | 922.1 | 372.8822 | -372.8822 | 3.593% | 67.89% | 24 | 0 | 0 | 0 | 0

## RAW AGG DATA SUMMARY
February 2013
Operating Day (CPT) | Operating Hour (CPT) | Hour Ending (CPT) | Real Time - Actual |  |  |  | Day Ahead 1430 | [6 empty] | Hour Ahead
|  |  | ERCOT Load [MW] | Total ERCOT Wind Plant Power Output (EMS Calculation for RT MONI) | Aggregated Wind Plants Power Output [MW] (Sum of Individual Wind Plant MWs) | Aggregated Wind Plants HSL [MW] (Sum of Individual Wind Plant HSL) | Aggregated COP HSL [MW] (Sum of Individual Wind Plant DA 1430 COP HSL) | Aggregated COP HSL [MW] (COGNOS) | Aggregated STWPF for WGRs that where ONLINE in Real-Time [MW] (Sum of Individual Wind Plant DA 1430 STWPF) USE THIS IN MAPE | Aggregated STWPF [MW] (Sum of Individual Wind Plant DA 1430 STWPF) | Aggregated STWPF [MW] (COGNOS) | Aggregated WGRPP [MW] (Sum of Individual Wind Plant DA 1430 WGRPP) | Aggregated WGRPP [MW] (COGNOS) | Aggregated COP HSL [MW] (Sum of Individual Wind Plant HA COP HSL) | Aggregated COP HSL [MW] (COGNOS) | Aggregated STWPFfor WGRs that where ONLINE in real-time [MW] (Sum of Individual Wind Plant HA STWPF) USE THIS IN MAPE | Aggregated STWPF [MW] (Sum of Individual Wind Plant HA STWPF) | Aggregated STWPF [MW] (COGNOS) | Aggregated WGRPP [MW] (Sum of Individual Wind Plant HA WGRPP) | Aggregated WGRPP [MW] (COGNOS)
|  | PI TAGS | ERCOT.LOAD | WINDFARMS.RTOTMW
2013-02-01 | 1 | 2013-02-01 01:00 | 28903.2237 | 3523.4184 | 3176.1174 | 3185.6333 | 3034.7 | 3191.5 | 2847.9 | 3022.8 | 3170.7 | 2194.4 | 2294.3 | 3220.1 | 3384.2 | 3046.4 | 3231.2 | 3388.1 | 2445.7 | 2554.7
2013-02-01 | 2 | 2013-02-01 02:00 | 28565.4173 | 3195.2233 | 2903.9421 | 2912.5707 | 3059.9 | 3211.1 | 2916.8 | 3079.7 | 3214.6 | 2246.7 | 2333.5 | 2850.8 | 2971.4 | 2698.4 | 2855.6 | 2964.9 | 2037.4 | 2098.7
2013-02-01 | 3 | 2013-02-01 03:00 | 28719.4526 | 2566.3891 | 2296.8456 | 2300.1776 | 2913.4 | 3037.4 | 2785 | 2929.9 | 3037.3 | 2108.1 | 2167.7 | 2909.2 | 2995.6 | 2818.3 | 2934.7 | 3016.4 | 2112.3 | 2145.9
2013-02-01 | 4 | 2013-02-01 04:00 | 29209.5197 | 2406.1569 | 2107.0549 | 2112.7068 | 2592.3 | 2697.8 | 2458.8 | 2596.5 | 2688.6 | 1781.9 | 1827.7 | 2968.3 | 3048.5 | 2914.5 | 3012.7 | 3083.6 | 2190.7 | 2213.6
2013-02-01 | 5 | 2013-02-01 05:00 | 30503.9308 | 2154.4558 | 1861.1293 | 1872.3455 | 2431.6 | 2530.7 | 2270.1 | 2399.2 | 2485.5 | 1588.1 | 1628.3 | 2319.6 | 2390.8 | 2227.8 | 2342.1 | 2406 | 1521.5 | 1537.5
2013-02-01 | 6 | 2013-02-01 06:00 | 33457.6174 | 2081.5178 | 1842.8186 | 1855.7023 | 2476.3 | 2572.5 | 2317.2 | 2429 | 2509.8 | 1618.9 | 1653.7 | 1993.2 | 2062.9 | 1886.1 | 1999 | 2054.9 | 1178.1 | 1187.4
2013-02-01 | 7 | 2013-02-01 07:00 | 38169.9799 | 2067.9825 | 1842.1573 | 1856.1608 | 2408.9 | 2497.6 | 2248.4 | 2352.7 | 2425.7 | 1542 | 1569.6 | 1910.9 | 1971 | 1797.7 | 1907.2 | 1954 | 1085.6 | 1089.3
2013-02-01 | 8 | 2013-02-01 08:00 | 39596.6815 | 2024.5876 | 1771.4323 | 1796.1919 | 2484.4 | 2575.6 | 2311.5 | 2411.7 | 2488.5 | 1597.2 | 1630.2 | 1828.9 | 1884.4 | 1743.5 | 1847.1 | 1894.8 | 1026.9 | 1030.4
2013-02-01 | 9 | 2013-02-01 09:00 | 38139.0816 | 1788.2789 | 1546.2695 | 1563.9631 | 2608.4 | 2692.7 | 2498.2 | 2567.7 | 2639.6 | 1750.2 | 1778.1 | 1723.6 | 1772.5 | 1647.9 | 1722.6 | 1764.3 | 907.5 | 910.2
2013-02-01 | 10 | 2013-02-01 10:00 | 36747.1527 | 1116.5518 | 974.4528 | 982.002 | 2023.3 | 2076 | 1952.8 | 1997.8 | 2041.8 | 1191.5 | 1199.7 | 1446.1 | 1484.3 | 1406.9 | 1445.1 | 1474 | 652.5 | 652.6
2013-02-01 | 11 | 2013-02-01 11:00 | 35470.6573 | 1318.3804 | 1167.7999 | 1174.3049 | 1918.4 | 1973.4 | 1840.4 | 1898.7 | 1946.5 | 1087.9 | 1101.3 | 1285 | 1317 | 1234.9 | 1271.3 | 1298.3 | 494.7 | 494.7
2013-02-01 | 12 | 2013-02-01 12:00 | 34103.5191 | 1872.045 | 1701.6092 | 1698.8609 | 2048 | 2122.5 | 1961.7 | 2030.3 | 2093 | 1206.6 | 1227.3 | 1446.4 | 1482 | 1416.8 | 1466.5 | 1496 | 708.6 | 708.6
2013-02-01 | 13 | 2013-02-01 13:00 | 32920.1769 | 2828.2101 | 2650.61 | 2646.5781 | 2330 | 2423.1 | 2233.9 | 2318.7 | 2394.6 | 1489 | 1516.8 | 1716.5 | 1769.7 | 1651.5 | 1712.8 | 1761.6 | 906.2 | 914.7
2013-02-01 | 14 | 2013-02-01 14:00 | 32258.5193 | 3999.2492 | 3791.3046 | 3784.776 | 2563.8 | 2680.1 | 2453.5 | 2543.7 | 2642.8 | 1715.7 | 1766.6 | 2120.3 | 2183.9 | 2019.5 | 2100.6 | 2167.6 | 1289.4 | 1314
2013-02-01 | 15 | 2013-02-01 15:00 | 31634.0832 | 5017.9498 | 4793.1525 | 4785.2925 | 2927.9 | 3058.3 | 2808.4 | 2904.6 | 3018.4 | 2075.2 | 2140.9 | 2578.4 | 2652.7 | 2460.5 | 2552.4 | 2639.4 | 1730.7 | 1775.3
2013-02-01 | 16 | 2013-02-01 16:00 | 31086.6036 | 5068.6767 | 4821.9216 | 4818.3999 | 3051.8 | 3200.1 | 2933.3 | 3038.8 | 3170.4 | 2209.3 | 2292.9 | 3258.8 | 3348.6 | 3151.4 | 3257.8 | 3360.3 | 2430.4 | 2485.3
2013-02-01 | 17 | 2013-02-01 17:00 | 30819.4854 | 5690.1198 | 5391.8369 | 5394.7412 | 2850.2 | 3011 | 2725.3 | 2851.1 | 2993.4 | 2021.1 | 2115.3 | 3941 | 4046.5 | 3822.3 | 3961.9 | 4093 | 3134.6 | 3217.8
2013-02-01 | 18 | 2013-02-01 18:00 | 31053.0181 | 5197.7739 | 4874.8601 | 4881.562 | 2558.8 | 2707.4 | 2432.8 | 2566.4 | 2697.9 | 1736.4 | 1819.9 | 4276.1 | 4384.6 | 4170.2 | 4304.6 | 4429.2 | 3477 | 3553.6
2013-02-01 | 19 | 2013-02-01 19:00 | 33039.3482 | 4696.7836 | 4407.9627 | 4420.8684 | 3135.4 | 3331 | 2980.9 | 3139.7 | 3312.2 | 2305.3 | 2429.9 | 4654.7 | 4777.1 | 4589.3 | 4721.5 | 4847.5 | 3893.6 | 3971.7
2013-02-01 | 20 | 2013-02-01 20:00 | 33403.3872 | 6321.7684 | 5905.9255 | 5975.0626 | 4099.1 | 4348.6 | 3922.4 | 4101.5 | 4318.6 | 3264.4 | 3433.4 | 5503.6 | 5658.8 | 5432.6 | 5562.1 | 5726.6 | 4735.8 | 4852.3
2013-02-01 | 21 | 2013-02-01 21:00 | 33109.2029 | 7149.9643 | 6660.6719 | 6850.3465 | 5084.7 | 5350.4 | 4890.7 | 5082 | 5310.4 | 4243.9 | 4424.3 | 5878 | 6060.2 | 5693.3 | 5845.7 | 6029.5 | 5018.2 | 5154
2013-02-01 | 22 | 2013-02-01 22:00 | 32452.2227 | 7476.2027 | 6984.9051 | 7292.1243 | 5484.2 | 5759.7 | 5304.2 | 5490.8 | 5724.9 | 4652 | 4838.2 | 5839.1 | 6025.6 | 5677.6 | 5829.8 | 6017.3 | 5004.6 | 5144
2013-02-01 | 23 | 2013-02-01 23:00 | 31061.5721 | 7554.0892 | 7017.4619 | 7402.0304 | 5645.7 | 5928.5 | 5488 | 5670.1 | 5910.7 | 4830.8 | 5023.3 | 6511.8 | 6677.2 | 6385.7 | 6539.1 | 6700.2 | 5713.2 | 5826.3
2013-02-01 | 24 | 2013-02-02 | 29386.8325 | 7335.7565 | 6846.7748 | 6903.4861 | 5601.8 | 5888 | 5463.2 | 5635.3 | 5881.6 | 4796.7 | 4995.1 | 6661.3 | 6809 | 6530.7 | 6674.6 | 6820.7 | 5848.4 | 5946.3
2013-02-02 | 1 | 2013-02-02 01:00 | 27878.9467 | 6974.3577 | 6490.5691 | 6490.108 | 5255.1 | 5395.8 | 5235.4 | 5330.3 | 5449.9 | 4504.3 | 4585.3 | 6694.9 | 6839.3 | 6631.7 | 6757.1 | 6905.5 | 5930.7 | 6031.2
2013-02-02 | 2 | 2013-02-02 02:00 | 27069.7084 | 6619.4629 | 6133.4399 | 6143.7593 | 5028.7 | 5147.7 | 5024.9 | 5100.5 | 5203.5 | 4274.4 | 4331.2 | 6447.3 | 6588.7 | 6321 | 6434.5 | 6590.5 | 5608 | 5716
2013-02-02 | 3 | 2013-02-02 03:00 | 26605.6481 | 6051.1079 | 5566.7216 | 5571.0564 | 4779.2 | 4894.8 | 4803.2 | 4853 | 4957.9 | 4029.8 | 4086.8 | 5766.1 | 5889.9 | 5661.5 | 5766.6 | 5894.7 | 4941.9 | 5021.8
2013-02-02 | 4 | 2013-02-02 04:00 | 26544.8923 | 5442.135 | 5032.4626 | 5046.3782 | 4544.8 | 4673 | 4558.2 | 4607.4 | 4724.8 | 3790.7 | 3862.6 | 5286.9 | 5409.1 | 5227.2 | 5319.5 | 5427.2 | 4494.1 | 4555.7
2013-02-02 | 5 | 2013-02-02 05:00 | 26879.1872 | 4530.1145 | 4176.7663 | 4186.2765 | 4028.6 | 4169 | 4013.8 | 4074.9 | 4202.7 | 3260.6 | 3345.5 | 4939.4 | 5070.3 | 4897.5 | 4978.6 | 5084.1 | 4154.3 | 4215.6
2013-02-02 | 6 | 2013-02-02 06:00 | 28071.9553 | 3718.0351 | 3420.9208 | 3429.8217 | 3602.3 | 3736.1 | 3599.3 | 3665.5 | 3782.6 | 2847.4 | 2925.7 | 4023.1 | 4182.7 | 3992.3 | 4063 | 4189.7 | 3237.5 | 3320.8
2013-02-02 | 7 | 2013-02-02 07:00 | 29641.7545 | 2727.4698 | 2482.8561 | 2492.9852 | 3230.9 | 3365.4 | 3220.9 | 3285.7 | 3402.7 | 2466.7 | 2550 | 3569.9 | 3761.4 | 3541.7 | 3612.2 | 3769.7 | 2786.7 | 2904
2013-02-02 | 8 | 2013-02-02 08:00 | 30885.7539 | 2648.2234 | 2436.9042 | 2446.5822 | 2609.5 | 2739.8 | 2577.5 | 2635.8 | 2746.9 | 1821.6 | 1901.1 | 3281.8 | 3470.6 | 3246.3 | 3329.8 | 3487.1 | 2506.2 | 2623.7
2013-02-02 | 9 | 2013-02-02 09:00 | 31622.2274 | 3213.2014 | 3032.7336 | 3040.6248 | 2065.6 | 2179.8 | 2025.4 | 2059 | 2157.1 | 1254.1 | 1326.6 | 2985.1 | 3143.6 | 2931.4 | 2996.6 | 3129.3 | 2172.2 | 2268.5
2013-02-02 | 10 | 2013-02-02 10:00 | 31543.065 | 3591.4009 | 3467.4311 | 3466.3619 | 1696.8 | 1763.6 | 1670.8 | 1683.9 | 1740.9 | 898.4 | 932.1 | 2540.6 | 2656 | 2489.7 | 2532.4 | 2631.1 | 1716.3 | 1786.2
2013-02-02 | 11 | 2013-02-02 11:00 | 31173.0258 | 4604.9408 | 4456.7679 | 4456.9822 | 1680.6 | 1712.8 | 1664.5 | 1666.8 | 1692.2 | 889.3 | 895.5 | 2791.2 | 2892.6 | 2786.4 | 2814.1 | 2903 | 1999.5 | 2060.8
2013-02-02 | 12 | 2013-02-02 12:00 | 30601.4203 | 4846.6928 | 4693.9226 | 4695.3365 | 1710.1 | 1733.8 | 1706.3 | 1702.8 | 1721.4 | 925.4 | 925.4 | 3027.4 | 3101.8 | 3040.9 | 3051.9 | 3115.5 | 2242.9 | 2279.3
2013-02-02 | 13 | 2013-02-02 13:00 | 30036.3124 | 4112.0263 | 3998.8734 | 4001.6153 | 1682 | 1701 | 1689.3 | 1680.9 | 1696.8 | 906.7 | 906.7 | 3164.6 | 3228.9 | 3175.9 | 3181.2 | 3238.1 | 2385.3 | 2415.8
2013-02-02 | 14 | 2013-02-02 14:00 | 29517.5566 | 3648.7907 | 3550.2428 | 3553.0769 | 1649 | 1667.6 | 1652.7 | 1649.4 | 1665.7 | 864.8 | 864.8 | 3547.8 | 3598.4 | 3561.1 | 3559.7 | 3604.4 | 2752 | 2767.9
2013-02-02 | 15 | 2013-02-02 15:00 | 29229.8271 | 3568.4058 | 3449.0174 | 3440.5 | 1473.4 | 1493.1 | 1462.9 | 1478.8 | 1496.8 | 689.9 | 689.9 | 3533.6 | 3572.2 | 3548.7 | 3553.4 | 3587 | 2747.6 | 2747.6
2013-02-02 | 16 | 2013-02-02 16:00 | 29131.8985 | 3622.6027 | 3477.2609 | 3448.7004 | 1346.4 | 1371.6 | 1329.1 | 1350 | 1374.3 | 566.8 | 567.2 | 3068.4 | 3112.4 | 3070.2 | 3096.9 | 3136.5 | 2292.4 | 2301.3
2013-02-02 | 17 | 2013-02-02 17:00 | 29208.9046 | 2991.9525 | 2814.1586 | 2813.8832 | 1239.3 | 1265.9 | 1213.9 | 1243.2 | 1268.9 | 473.8 | 476.9 | 2310.4 | 2366.9 | 2263.8 | 2317.6 | 2368.3 | 1503.6 | 1528.3
2013-02-02 | 18 | 2013-02-02 18:00 | 29489.3291 | 2122.4212 | 1974.0312 | 1977.6161 | 1155.6 | 1181 | 1126.2 | 1158.8 | 1183.5 | 401 | 403.7 | 1884.1 | 1928.6 | 1844.1 | 1884.9 | 1923.4 | 1085.4 | 1105.1
2013-02-02 | 19 | 2013-02-02 19:00 | 31246.7644 | 1527.7386 | 1401.0812 | 1408.0817 | 1257.1 | 1279.2 | 1224.3 | 1256.9 | 1277.7 | 478.9 | 478.9 | 1988.3 | 2024.5 | 1970.4 | 2006 | 2034.9 | 1206.2 | 1217.1
2013-02-02 | 20 | 2013-02-02 20:00 | 31544.0224 | 1226.2159 | 1097.3471 | 1098.7455 | 1331.9 | 1366.6 | 1288.7 | 1334.9 | 1365.7 | 565.7 | 565.7 | 1741.1 | 1772 | 1707.7 | 1753.8 | 1782.5 | 974.3 | 978.3
2013-02-02 | 21 | 2013-02-02 21:00 | 31005.7798 | 943.3451 | 835.8227 | 839.0936 | 1433 | 1498.9 | 1393.2 | 1453.6 | 1510.2 | 688.9 | 710.9 | 1560.2 | 1593.4 | 1485.8 | 1560.1 | 1598.4 | 793.5 | 807.2
2013-02-02 | 22 | 2013-02-02 22:00 | 30196.05 | 799.9945 | 693.6634 | 701.5625 | 1530.4 | 1595.6 | 1498.2 | 1554.6 | 1604.7 | 789.7 | 812.2 | 1361.6 | 1393.7 | 1256.7 | 1337.6 | 1392.1 | 591.2 | 621.1
2013-02-02 | 23 | 2013-02-02 23:00 | 28915.9602 | 755.1936 | 636.967 | 651.7683 | 1637.7 | 1714.7 | 1611.4 | 1668.8 | 1726.7 | 896.9 | 928.5 | 1129 | 1152 | 1052.4 | 1131.2 | 1145.8 | 490 | 490
2013-02-02 | 24 | 2013-02-03 | 27408.647 | 793.0289 | 677.4041 | 684.0232 | 1790.1 | 1881.7 | 1768.4 | 1821.5 | 1893.8 | 1038.5 | 1085.4 | 975.9 | 997.4 | 866.4 | 928.7 | 990.5 | 367.4 | 408.8
2013-02-03 | 1 | 2013-02-03 01:00 | 26305.8048 | 815.8098 | 680.0233 | 684.6273 | 1212.5 | 1286.6 | 1140.9 | 1202.1 | 1264.9 | 494.7 | 533.4 | 928.8 | 957.7 | 814.8 | 876.4 | 948.3 | 345.5 | 389.5
2013-02-03 | 2 | 2013-02-03 02:00 | 25654.4219 | 829.2551 | 659.7585 | 671.6533 | 1271.2 | 1351.8 | 1210.1 | 1262.2 | 1330.1 | 539.6 | 577.5 | 959.7 | 1001.9 | 839.7 | 901.1 | 986.4 | 350.8 | 403.4
2013-02-03 | 3 | 2013-02-03 03:00 | 25413.7978 | 746.083 | 596.6463 | 601.5307 | 1298.3 | 1383.4 | 1240.7 | 1297 | 1367.3 | 577 | 618.3 | 969.5 | 1015 | 867.9 | 922.3 | 1015.9 | 313.2 | 377.1
2013-02-03 | 4 | 2013-02-03 04:00 | 25479.8261 | 958.3315 | 808.467 | 811.0769 | 1384.5 | 1476.1 | 1335.2 | 1385.8 | 1461.9 | 636.6 | 680.4 | 1132.2 | 1188.6 | 1032.5 | 1081.5 | 1182.5 | 407.5 | 475
2013-02-03 | 5 | 2013-02-03 05:00 | 25860.1781 | 1218.4933 | 1067.5778 | 1068.5545 | 1583.2 | 1690.5 | 1535.8 | 1587.5 | 1678.6 | 805.7 | 857.5 | 1490.6 | 1553.1 | 1395 | 1448.5 | 1545 | 672.9 | 727.6
2013-02-03 | 6 | 2013-02-03 06:00 | 26777.7699 | 1462.7776 | 1310.0743 | 1316.4932 | 1762.7 | 1889.2 | 1705.5 | 1760.3 | 1872.3 | 950.5 | 1021 | 1628.3 | 1698.9 | 1560.6 | 1614 | 1719.9 | 795.9 | 860
2013-02-03 | 7 | 2013-02-03 07:00 | 28163.6435 | 1785.6638 | 1646.2459 | 1648.5286 | 2002.4 | 2129.5 | 1934 | 1982.8 | 2094.5 | 1159.9 | 1228.2 | 1684 | 1744 | 1618.1 | 1658.3 | 1751.9 | 848.2 | 903.7
2013-02-03 | 8 | 2013-02-03 08:00 | 29405.3214 | 2145.9928 | 2003.5307 | 2005.316 | 2268.1 | 2381.6 | 2229.1 | 2266.5 | 2367 | 1444.3 | 1498.7 | 1981.8 | 2035.2 | 1926.3 | 1956.8 | 2038.4 | 1151.8 | 1195
2013-02-03 | 9 | 2013-02-03 09:00 | 30479.5242 | 2456.8359 | 2300.0943 | 2302.4091 | 2359.9 | 2456 | 2308.6 | 2343.9 | 2428.5 | 1520 | 1560.4 | 2223.5 | 2263.6 | 2183.2 | 2196.3 | 2255 | 1397.5 | 1426.4
2013-02-03 | 10 | 2013-02-03 10:00 | 30581.6688 | 2290.1793 | 2156.117 | 2162.6435 | 2191.7 | 2267.2 | 2145.1 | 2190.7 | 2257.1 | 1368.4 | 1386.7 | 2034.1 | 2056.1 | 1982.3 | 1983.5 | 2016.9 | 1205.4 | 1218.9
2013-02-03 | 11 | 2013-02-03 11:00 | 30015.6169 | 3214.2103 | 3107.1968 | 3113.3459 | 2015.4 | 2069.2 | 1989.4 | 2027.8 | 2070.2 | 1213.1 | 1222.2 | 2077.6 | 2091.6 | 2066.8 | 2059.5 | 2082.4 | 1283.2 | 1293.7
2013-02-03 | 12 | 2013-02-03 12:00 | 29536.7907 | 4795.3616 | 4616.2409 | 4617.2281 | 2165.5 | 2222.8 | 2144.1 | 2178.1 | 2221.8 | 1362.1 | 1371.5 | 2305.2 | 2322 | 2314.9 | 2308.7 | 2330.7 | 1520.4 | 1527.1
2013-02-03 | 13 | 2013-02-03 13:00 | 29325.8769 | 5639.0282 | 5362.4148 | 5354.1343 | 2245.1 | 2318.8 | 2235.6 | 2279.3 | 2338.8 | 1458.4 | 1471.1 | 2629.2 | 2664 | 2627.2 | 2629.3 | 2662.6 | 1822.3 | 1829.3
2013-02-03 | 14 | 2013-02-03 14:00 | 29083.2635 | 5525.9527 | 5162.1937 | 5139.3084 | 2354.6 | 2449.2 | 2339.4 | 2390.8 | 2468.4 | 1565.6 | 1595.1 | 3445 | 3503.7 | 3465.7 | 3487.9 | 3543.3 | 2670.9 | 2685.1
2013-02-03 | 15 | 2013-02-03 15:00 | 29140.2239 | 5646.5732 | 5281.8599 | 5263.7545 | 2602.6 | 2722.2 | 2574.8 | 2627.9 | 2724.5 | 1802.7 | 1851.3 | 4194.3 | 4298.4 | 4239.3 | 4302 | 4405.2 | 3478 | 3533.1
2013-02-03 | 16 | 2013-02-03 16:00 | 29237.0841 | 6215.8875 | 5796.9883 | 5794.7537 | 2950 | 3083.8 | 2917.2 | 2991.8 | 3098.9 | 2166.8 | 2226 | 4485 | 4623.4 | 4552.2 | 4649.8 | 4779.2 | 3825.3 | 3906.7
2013-02-03 | 17 | 2013-02-03 17:00 | 29330.7828 | 6278.2918 | 5789.0055 | 5814.9711 | 3093.5 | 3226.7 | 3051.7 | 3136.4 | 3240.8 | 2311.4 | 2367.7 | 4379.2 | 4548.5 | 4377.5 | 4518.6 | 4684.7 | 3693.9 | 3812
2013-02-03 | 18 | 2013-02-03 18:00 | 29421.7777 | 5330.5993 | 4854.2721 | 4860.8497 | 2950.4 | 3091.6 | 2894.6 | 2991.5 | 3104.7 | 2166.2 | 2231.5 | 4528.9 | 4707.2 | 4476.1 | 4639.3 | 4819.2 | 3816.5 | 3948.4
2013-02-03 | 19 | 2013-02-03 19:00 | 30801.081 | 5086.6061 | 4644.675 | 4650.7126 | 3366.7 | 3530.4 | 3317.7 | 3425.8 | 3562.9 | 2600.8 | 2689.9 | 5435.5 | 5666.5 | 5384.4 | 5556.6 | 5788.7 | 4734.4 | 4918.4
2013-02-03 | 20 | 2013-02-03 20:00 | 31124.222 | 6309.9139 | 5800.7068 | 5798.0338 | 4120.6 | 4334.3 | 4051 | 4188.7 | 4372.6 | 3364.3 | 3500.1 | 6092.8 | 6371.9 | 6014.3 | 6221.9 | 6491.9 | 5398 | 5620
2013-02-03 | 21 | 2013-02-03 21:00 | 30906.9563 | 7445.5281 | 6910.91 | 6913.7396 | 5152.2 | 5434.3 | 5068.8 | 5231.2 | 5472.6 | 4407.8 | 4601.1 | 6585.6 | 6900.5 | 6364.5 | 6614.8 | 6923.8 | 5790.4 | 6051.4
2013-02-03 | 22 | 2013-02-03 22:00 | 29938.1846 | 7931.8584 | 7344.414 | 7346.0854 | 5755.9 | 6076.1 | 5675 | 5854.8 | 6131.7 | 5028.7 | 5257.6 | 6836.5 | 7173.7 | 6578.4 | 6836.4 | 7166.3 | 6011.5 | 6293.3
2013-02-03 | 23 | 2013-02-03 23:00 | 29057.3629 | 7743.904 | 7131.7504 | 7138.5474 | 6043.4 | 6390.1 | 5943.7 | 6116.8 | 6420.4 | 5290.6 | 5546.3 | 7172.4 | 7496 | 6946.4 | 7179.7 | 7509.7 | 6356 | 6638
2013-02-03 | 24 | 2013-02-04 | 26615.0456 | 7221.5434 | 6572.2799 | 6574.9948 | 6174.7 | 6536.4 | 6086.3 | 6251.7 | 6565.6 | 5426.9 | 5692.8 | 7430.9 | 7742.1 | 7259.5 | 7471.8 | 7789.4 | 6646.7 | 6916.3
2013-02-04 | 1 | 2013-02-04 01:00 | 24890.9166 | 6571.5014 | 5908.5078 | 5910.9356 | 6795.4 | 7182.5 | 6759.1 | 7000.5 | 7340 | 6176.2 | 6467.6 | 7291.3 | 7591.6 | 7070.5 | 7294.7 | 7603.6 | 6470.1 | 6730.9
2013-02-04 | 2 | 2013-02-04 02:00 | 23937.541 | 6010.6258 | 5354.5929 | 5357.8685 | 6404.7 | 6778.1 | 6392.8 | 6609.8 | 6942.6 | 5785 | 6069.9 | 6690.6 | 6968.5 | 6458.1 | 6691.9 | 6983.8 | 5866.5 | 6110.3
2013-02-04 | 3 | 2013-02-04 03:00 | 23611.8924 | 5688.8157 | 5035.0563 | 5041.0477 | 6387.4 | 6737.9 | 6380 | 6591.4 | 6913 | 5767 | 6040.6 | 5930.4 | 6208 | 5688.7 | 5918.1 | 6202 | 5093.1 | 5328.9
2013-02-04 | 4 | 2013-02-04 04:00 | 23668.521 | 5201.6554 | 4592.5687 | 4601.1593 | 6529.1 | 6858.2 | 6512.2 | 6738.5 | 7044.7 | 5914.2 | 6172.3 | 6049.2 | 6312 | 5856.4 | 6063.5 | 6327.7 | 5236.9 | 5453
2013-02-04 | 5 | 2013-02-04 05:00 | 24382.2297 | 4713.3175 | 4180.3616 | 4194.3853 | 5864.9 | 6144.4 | 5836.4 | 6032.3 | 6291.4 | 5217.7 | 5428.7 | 5698.5 | 5937.8 | 5531.9 | 5719.6 | 5956.6 | 4903.8 | 5092.8
2013-02-04 | 6 | 2013-02-04 06:00 | 26667.8482 | 4746.2654 | 4287.4076 | 4302.0949 | 5588.9 | 5840.3 | 5564.7 | 5760.6 | 5998.1 | 4946 | 5135.4 | 5457.4 | 5708.4 | 5301.6 | 5481.9 | 5723.8 | 4666 | 4859.9
2013-02-04 | 7 | 2013-02-04 07:00 | 30636.634 | 4410.3 | 4012.1782 | 4010.3017 | 5303.1 | 5552.5 | 5290.4 | 5496.3 | 5727.6 | 4681.1 | 4864.4 | 5271.4 | 5502.5 | 5124.8 | 5311.6 | 5526.8 | 4497.4 | 4664.6
2013-02-04 | 8 | 2013-02-04 08:00 | 32207.8746 | 4222.9601 | 3839.748 | 3843.5795 | 4846.8 | 5072.8 | 4880.3 | 5073 | 5278.1 | 4257.3 | 4419.8 | 4921.5 | 5125.6 | 4770.8 | 4949.7 | 5137.7 | 4134.5 | 4274.5
2013-02-04 | 9 | 2013-02-04 09:00 | 31741.641 | 3586.3631 | 3311.7498 | 3318.4081 | 4190.3 | 4397.9 | 4149.4 | 4362.1 | 4545.6 | 3547.4 | 3688.7 | 4303.5 | 4483.7 | 4154.8 | 4347.6 | 4513.4 | 3535.8 | 3656
2013-02-04 | 10 | 2013-02-04 10:00 | 32060.5536 | 3045.8312 | 2790.7125 | 2797.035 | 3483.3 | 3724.2 | 3359.1 | 3583.7 | 3801.4 | 2769.5 | 2947.5 | 3701.6 | 3900.6 | 3505.4 | 3731.6 | 3910.3 | 2918.9 | 3056.5
2013-02-04 | 11 | 2013-02-04 11:00 | 32202.06 | 3098.8195 | 2782.5156 | 2834.0324 | 2907.4 | 3177.7 | 2755.4 | 2988.9 | 3236.2 | 2174.4 | 2381.5 | 2999.3 | 3197.4 | 2837.2 | 3032.1 | 3201.2 | 2218.7 | 2347.9
2013-02-04 | 12 | 2013-02-04 12:00 | 32255.2395 | 2259.7882 | 1956.0868 | 2031.4368 | 2698.8 | 2967.4 | 2535.7 | 2759.3 | 3009.6 | 1944.8 | 2155.1 | 2407.7 | 2587.2 | 2289.9 | 2436.1 | 2595.4 | 1624.3 | 1751.1
2013-02-04 | 13 | 2013-02-04 13:00 | 32231.2884 | 1943.7862 | 1689.8074 | 1749.8047 | 2704.9 | 2957.2 | 2543.9 | 2752.2 | 2988.8 | 1937.2 | 2134 | 2143.3 | 2303.6 | 2071 | 2170.6 | 2314.1 | 1362.6 | 1475.3
2013-02-04 | 14 | 2013-02-04 14:00 | 32268.1277 | 2314.7509 | 2084.1914 | 2097.2131 | 2753.6 | 2999.7 | 2591.2 | 2804.1 | 3032.8 | 1989.4 | 2177.5 | 2334.9 | 2484.4 | 2259.3 | 2345.4 | 2482.7 | 1541.3 | 1642.2
2013-02-04 | 15 | 2013-02-04 15:00 | 32255.3367 | 2602.8166 | 2424.6632 | 2450.5385 | 3090.2 | 3343.7 | 2985.5 | 3185.4 | 3416.5 | 2375.5 | 2562.2 | 2141.9 | 2292.6 | 2060 | 2142.8 | 2284.3 | 1344.3 | 1441.6
2013-02-04 | 16 | 2013-02-04 16:00 | 32277.3375 | 2772.3836 | 2613.4128 | 2621.623 | 3004.5 | 3245.3 | 2930 | 3121.9 | 3341.1 | 2312.6 | 2484.5 | 2176.8 | 2343.4 | 2098.5 | 2187.6 | 2346.1 | 1383.2 | 1493.6
2013-02-04 | 17 | 2013-02-04 17:00 | 32390.3207 | 2593.7606 | 2421.7103 | 2414.89 | 2894.7 | 3105.8 | 2834 | 3007.9 | 3200.2 | 2196.8 | 2342.1 | 2280.4 | 2434.5 | 2211.5 | 2293.4 | 2434.1 | 1483.4 | 1576.1
2013-02-04 | 18 | 2013-02-04 18:00 | 32621.8877 | 2423.3669 | 2216.5702 | 2216.8676 | 2737.9 | 2923.4 | 2670.1 | 2837.1 | 3010.6 | 2025.8 | 2153.3 | 2511.7 | 2676.1 | 2436.4 | 2532.6 | 2678.6 | 1723.2 | 1828.2
2013-02-04 | 19 | 2013-02-04 19:00 | 34330.5697 | 2225.3823 | 1942.7284 | 1947.8911 | 2725.9 | 2900.4 | 2628 | 2802.6 | 2970 | 1991.1 | 2110.4 | 2711.9 | 2885 | 2615.2 | 2729.3 | 2892.3 | 1915.1 | 2037.3
2013-02-04 | 20 | 2013-02-04 20:00 | 34664.6416 | 2267.572 | 1942.1996 | 1958.785 | 2855.9 | 3028.9 | 2764.9 | 2930.2 | 3097.8 | 2119.1 | 2238.4 | 2894.4 | 3053 | 2795.8 | 2898.7 | 3051.1 | 2086.1 | 2197.6
2013-02-04 | 21 | 2013-02-04 21:00 | 33758.0269 | 2219.5681 | 1858.6212 | 1875.6864 | 3087.5 | 3252.2 | 3008.2 | 3159.2 | 3319.2 | 2347 | 2459.1 | 3148.2 | 3294.2 | 2969.5 | 3094.9 | 3235.4 | 2285.9 | 2386.2
2013-02-04 | 22 | 2013-02-04 22:00 | 32192.5779 | 2029.7593 | 1692.4282 | 1703.7297 | 3213.6 | 3374.4 | 3122.8 | 3271.6 | 3426.3 | 2456.8 | 2563.3 | 2805.6 | 2930.9 | 2694.9 | 2808 | 2929.9 | 1999.3 | 2080.4
2013-02-04 | 23 | 2013-02-04 23:00 | 29499.635 | 2094.8787 | 1798.4626 | 1804.795 | 3186.7 | 3378.5 | 3074.2 | 3225.3 | 3408.9 | 2411.2 | 2546.8 | 2410.9 | 2518.8 | 2333.7 | 2414.9 | 2515.9 | 1647.7 | 1708.9
2013-02-04 | 24 | 2013-02-05 | 26971.0347 | 2199.5936 | 1948.6111 | 1946.8059 | 3064.7 | 3236.8 | 2956.7 | 3096 | 3261 | 2283.1 | 2400 | 1927.2 | 2022.7 | 1774.1 | 1885.3 | 1984.4 | 1109.5 | 1161.7
2013-02-05 | 1 | 2013-02-05 01:00 | 25242.3479 | 1982.5693 | 1789.8665 | 1787.1869 | 1943.1 | 2082.5 | 1756.2 | 1873.2 | 2009.9 | 1101.4 | 1193.4 | 1575 | 1654.7 | 1423.5 | 1545.1 | 1642.9 | 797.1 | 849.9
2013-02-05 | 2 | 2013-02-05 02:00 | 24361.1331 | 1429.213 | 1274.8193 | 1278.3024 | 1620.3 | 1738.4 | 1461.2 | 1561.9 | 1677.9 | 815.9 | 890.9 | 1385 | 1453.8 | 1249.9 | 1355 | 1457.9 | 647 | 705.5
2013-02-05 | 3 | 2013-02-05 03:00 | 23958.4144 | 1016.1779 | 840.7356 | 844.0309 | 1337.7 | 1442.2 | 1181.7 | 1288.9 | 1392.1 | 582.3 | 644.8 | 1431.3 | 1498.8 | 1332.9 | 1424.9 | 1520.6 | 711 | 763.4
2013-02-05 | 4 | 2013-02-05 04:00 | 23934.8524 | 708.7601 | 546.9935 | 549.1649 | 1078.3 | 1170.2 | 942.1 | 1043.2 | 1133.1 | 417 | 471.3 | 1176.5 | 1234.4 | 1070.1 | 1155.3 | 1246.9 | 492.7 | 547.6
2013-02-05 | 5 | 2013-02-05 05:00 | 24570.2447 | 532.7912 | 390.4942 | 393.6511 | 944 | 1019.4 | 839.9 | 920 | 992.9 | 380.9 | 423.3 | 920.8 | 965.2 | 829.9 | 904.5 | 978.8 | 307 | 346.8
2013-02-05 | 6 | 2013-02-05 06:00 | 26826.795 | 487.3166 | 356.8095 | 365.7525 | 894.3 | 953.8 | 816.9 | 886.3 | 940.5 | 372.9 | 405 | 835.7 | 870.8 | 727.6 | 788.2 | 839.2 | 229.5 | 243.7
2013-02-05 | 7 | 2013-02-05 07:00 | 30875.4234 | 571.119 | 467.8347 | 480.4111 | 889.5 | 940.2 | 836.9 | 897.3 | 938.7 | 394 | 414.9 | 815.1 | 842.4 | 713 | 768.6 | 803.2 | 215.8 | 217.2
2013-02-05 | 8 | 2013-02-05 08:00 | 32312.7929 | 612.3358 | 538.6193 | 555.4865 | 959.2 | 1015.6 | 911.9 | 962.2 | 1005.5 | 426.2 | 439.1 | 994.7 | 1029.8 | 944 | 996.2 | 1031.4 | 305.1 | 305.1
2013-02-05 | 9 | 2013-02-05 09:00 | 31905.7771 | 504.4812 | 468.7664 | 483.2921 | 1083.8 | 1126.7 | 1053.1 | 1089.8 | 1120.6 | 480.6 | 482.7 | 1024.9 | 1045.4 | 1006.6 | 1027.3 | 1049.7 | 335 | 337.5
2013-02-05 | 10 | 2013-02-05 10:00 | 32079.6836 | 499.6224 | 481.8668 | 496.9967 | 1062 | 1088.2 | 1044.5 | 1063.8 | 1083.5 | 417.5 | 419.6 | 894.8 | 904.4 | 883.3 | 896.3 | 906.4 | 272.3 | 272.3
2013-02-05 | 11 | 2013-02-05 11:00 | 32546.3122 | 355.1775 | 315.0159 | 326.932 | 835.7 | 844.5 | 813.7 | 827.6 | 834.7 | 257 | 257 | 592.7 | 600.4 | 585.9 | 591.1 | 599.7 | 101.1 | 101.1
2013-02-05 | 12 | 2013-02-05 12:00 | 32851.1331 | 232.8226 | 212.7565 | 216.1149 | 769.5 | 776.1 | 746.2 | 759.7 | 765.4 | 216.1 | 216.1 | 492.5 | 496 | 476.5 | 473.8 | 477.4 | 85.1 | 85.1
2013-02-05 | 13 | 2013-02-05 13:00 | 33166.4823 | 158.4851 | 155.6117 | 162.9123 | 717.9 | 723 | 694.6 | 710.3 | 714.6 | 181.3 | 181.3 | 461.5 | 462.8 | 459.2 | 459.6 | 459.6 | 120.1 | 120.1
2013-02-05 | 14 | 2013-02-05 14:00 | 33562.6492 | 139.8263 | 135.1685 | 143.8527 | 686.7 | 691.8 | 662.1 | 682.6 | 686.6 | 167.4 | 167.4 | 380.6 | 382.6 | 368.8 | 374.7 | 375.6 | 66 | 66
2013-02-05 | 15 | 2013-02-05 15:00 | 33750.5329 | 293.8578 | 276.9715 | 269.9006 | 682.1 | 690.2 | 662.7 | 679.1 | 685.8 | 165.6 | 165.6 | 376.6 | 386.7 | 346.9 | 377.5 | 386.9 | 66.9 | 66.9
2013-02-05 | 16 | 2013-02-05 16:00 | 33949.7471 | 653.1982 | 528.7421 | 531.4117 | 680.6 | 694.9 | 654.2 | 676.6 | 689.5 | 174.1 | 174.1 | 458.3 | 488.1 | 394.8 | 455.1 | 483.9 | 131.5 | 143.5
2013-02-05 | 17 | 2013-02-05 17:00 | 34025.0913 | 951.2285 | 770.9189 | 782.0844 | 667.9 | 687.3 | 642.3 | 663.1 | 681.2 | 162.1 | 162.4 | 544.9 | 598.4 | 460.7 | 550.3 | 602.6 | 185.4 | 219.9
2013-02-05 | 18 | 2013-02-05 18:00 | 33963.1682 | 954.1855 | 788.2129 | 799.2726 | 684.4 | 704.4 | 657 | 682.4 | 701.2 | 160.6 | 160.6 | 984 | 1057.7 | 875.2 | 995.1 | 1068.4 | 349.4 | 400.6
2013-02-05 | 19 | 2013-02-05 19:00 | 35337.276 | 1385.2549 | 1154.2942 | 1157.4004 | 962.8 | 992.8 | 930.2 | 959.4 | 988.6 | 285.2 | 288.7 | 1663.7 | 1751.9 | 1541.1 | 1672.9 | 1763.8 | 921.7 | 979.5
2013-02-05 | 20 | 2013-02-05 20:00 | 35542.6911 | 2417.674 | 2152.116 | 2164.4325 | 1454.7 | 1504.1 | 1423.3 | 1461.8 | 1510 | 718.6 | 736.3 | 2212.7 | 2294.4 | 2090.7 | 2210.3 | 2300.6 | 1434 | 1483.8
2013-02-05 | 21 | 2013-02-05 21:00 | 34737.8211 | 3422.4267 | 3171.564 | 3206.8321 | 1982.6 | 2052.1 | 1944.4 | 1998.6 | 2063.1 | 1217.1 | 1246.2 | 2670.9 | 2761.4 | 2549 | 2672 | 2771.7 | 1877.9 | 1932.4
2013-02-05 | 22 | 2013-02-05 22:00 | 33078.8062 | 4234.2134 | 3944.2496 | 3992.0898 | 2420.1 | 2524.7 | 2395.4 | 2454.9 | 2547.8 | 1647.9 | 1696 | 3120.7 | 3218.4 | 2990.9 | 3124.1 | 3229.2 | 2314.5 | 2371.6
2013-02-05 | 23 | 2013-02-05 23:00 | 30498.1686 | 4413.5287 | 4116.3935 | 4124.8779 | 2945.8 | 3084.9 | 2912.1 | 2974.3 | 3097 | 2160 | 2234.6 | 3471.2 | 3573.9 | 3356.6 | 3471.7 | 3573.7 | 2661.5 | 2715.4
2013-02-05 | 24 | 2013-02-06 | 27775.5302 | 4469.5252 | 4144.9534 | 4147.1953 | 3498 | 3658.6 | 3451.3 | 3519.3 | 3657.6 | 2704.5 | 2794.7 | 4110.5 | 4215.9 | 4043.3 | 4135.2 | 4234.2 | 3324.5 | 3375.7
2013-02-06 | 1 | 2013-02-06 01:00 | 25925.042 | 3860.2925 | 3623.6332 | 3627.5148 | 3203.3 | 3326.5 | 3235 | 3307.8 | 3421.9 | 2498.5 | 2564.6 | 4171 | 4282.5 | 4235.9 | 4316 | 4416.2 | 3503.9 | 3555.9
2013-02-06 | 2 | 2013-02-06 02:00 | 24927.7028 | 3946.2938 | 3743.8942 | 3746.3413 | 3301 | 3415.3 | 3307.7 | 3382.5 | 3486.9 | 2577.8 | 2634.3 | 4174.3 | 4288.1 | 4188.7 | 4280.3 | 4388.5 | 3469.2 | 3529.3
2013-02-06 | 3 | 2013-02-06 03:00 | 24419.9018 | 3884.6502 | 3671.444 | 3673.9111 | 3162.8 | 3270.8 | 3178.6 | 3240.9 | 3337.7 | 2441.8 | 2493.1 | 3776 | 3868.4 | 3667.1 | 3748.2 | 107.3 | 2937.5 | 90.1
2013-02-06 | 4 | 2013-02-06 04:00 | 24304.2386 | 4024.8769 | 3836.9741 | 3837.4178 | 2745.4 | 2840 | 2697.9 | 2791.9 | 2876.9 | 1994.9 | 2037.6 | 3422 | 3509.7 | 3327.3 | 3419.7 | 3842.2 | 2607.5 | 2983.5
2013-02-06 | 5 | 2013-02-06 05:00 | 24860.8766 | 4242.0282 | 4047.776 | 4052.1918 | 2596.9 | 2678.6 | 2548.6 | 2640.6 | 2714.1 | 1841.8 | 1874.8 | 3678.6 | 3752.8 | 3619.5 | 3682.6 | 94 | 2872.4 | 76.8
2013-02-06 | 6 | 2013-02-06 06:00 | 26954.9423 | 3930.683 | 3773.459 | 3785.396 | 2723.8 | 2807.2 | 2722.2 | 2797.1 | 2875.4 | 1998.1 | 2032.2 | 3798.3 | 3896.5 | 3733.6 | 3794.1 | 3506.2 | 2983.5 | 2646
2013-02-06 | 7 | 2013-02-06 07:00 | 30913.6438 | 3582.5148 | 3436.406 | 3448.4954 | 2705.5 | 2793.1 | 2710.6 | 2798.8 | 2883.6 | 2003.3 | 2045.4 | 3913.8 | 4000.5 | 3843.9 | 3897.7 | 78.8 | 3091 | 61.7
2013-02-06 | 8 | 2013-02-06 08:00 | 32448.8541 | 3204.0829 | 3097.205 | 3092.6042 | 3099.2 | 3193.1 | 3179.7 | 3269.9 | 3362.7 | 2471.4 | 2520.7 | 4350.4 | 4439.2 | 4305.3 | 4335.2 | 3759.6 | 3530.3 | 2901.3
2013-02-06 | 9 | 2013-02-06 09:00 | 32079.9853 | 2768.7289 | 2677.4008 | 2676.4785 | 2998.1 | 3084.2 | 3066.3 | 3146.7 | 3230.9 | 2347 | 2384.4 | 4340.2 | 4436.8 | 4324.7 | 4342.2 | 66.3 | 3535.2 | 49.1
2013-02-06 | 10 | 2013-02-06 10:00 | 32381.66 | 2498.2211 | 2396.0519 | 2400.7922 | 2899.8 | 2974.1 | 2967 | 3006.4 | 3078.1 | 2205.7 | 2240.4 | 3578.6 | 3661.3 | 3570.5 | 3595.2 | 3898.9 | 2786.3 | 3040.2
2013-02-06 | 11 | 2013-02-06 11:00 | 32746.0646 | 3214.0701 | 3053.8407 | 3060.6141 | 2687.1 | 2755.1 | 2739.2 | 2766.9 | 2832.3 | 1977.2 | 2009.1 | 3047.2 | 3148.2 | 2978.8 | 3053.3 | 59.7 | 2241.2 | 42.5
2013-02-06 | 12 | 2013-02-06 12:00 | 32879.0259 | 3054.6056 | 2823.2963 | 2843.5418 | 2725.5 | 2800 | 2764.5 | 2805.1 | 2877.1 | 2006.6 | 2041.7 | 2669.6 | 2784.8 | 2570.4 | 2655.8 | 3995.3 | 1847.9 | 3140.7
2013-02-06 | 13 | 2013-02-06 13:00 | 32907.044 | 2547.3146 | 2288.921 | 2299.3689 | 2633.6 | 2730.9 | 2621.6 | 2708.1 | 2803.5 | 1907.1 | 1955.9 | 2553.2 | 2679.7 | 2457.7 | 2550.3 | 59 | 1748.6 | 41.9
2013-02-06 | 14 | 2013-02-06 14:00 | 33075.5516 | 2334.4104 | 2041.1339 | 2053.2321 | 2501.3 | 2609 | 2464.8 | 2563.2 | 2669.7 | 1769.9 | 1831.1 | 2635.5 | 2762 | 2559.6 | 2652.7 | 4431.4 | 1863.5 | 3578.5
2013-02-06 | 15 | 2013-02-06 15:00 | 32979.2423 | 2903.5383 | 2631.6168 | 2644.109 | 2410.2 | 2530.4 | 2368.1 | 2460.6 | 2579.8 | 1668.8 | 1741.4 | 2194.7 | 2317.9 | 2133.5 | 2198.1 | 70.4 | 1429.2 | 53.3
2013-02-06 | 16 | 2013-02-06 16:00 | 32930.4021 | 3580.5259 | 3316.2815 | 3311.2319 | 2358.7 | 2466 | 2340.7 | 2405.5 | 2512.4 | 1617.4 | 1676.4 | 1852.6 | 1950.9 | 1803.6 | 1846.2 | 4442.6 | 1087.2 | 3587.5
2013-02-06 | 17 | 2013-02-06 17:00 | 32819.386 | 3579.4874 | 3321.451 | 3326.706 | 2329.9 | 2429.7 | 2314.8 | 2380.8 | 2479.9 | 1599.5 | 1650.6 | 1933.9 | 2000.9 | 1869.3 | 1899.5 | 82.7 | 1136.8 | 65.5
2013-02-06 | 18 | 2013-02-06 18:00 | 32955.4063 | 3060.6536 | 2779.9706 | 2786.6249 | 2111.5 | 2214.3 | 2093.4 | 2156.1 | 2258.2 | 1374.1 | 1428.1 | 2113.2 | 2190.5 | 2034.5 | 2080 | 3675.9 | 1292.7 | 2820
2013-02-06 | 19 | 2013-02-06 19:00 | 34467.0357 | 2459.3202 | 2119.8275 | 2132.1187 | 2283.9 | 2417.1 | 2257.8 | 2339.8 | 2471.4 | 1546.2 | 1629.7 | 2895.6 | 3014.3 | 2889.1 | 2974.4 | 77.2 | 2174.6 | 60
2013-02-06 | 20 | 2013-02-06 20:00 | 34642.0874 | 2474.315 | 2063.6154 | 2066.5492 | 2686.5 | 2866.5 | 2655.7 | 2780.5 | 2954.9 | 1968.5 | 2094.9 | 3501.5 | 3674.6 | 3267.6 | 3419.4 | 3141.6 | 2610.6 | 2287.9
2013-02-06 | 21 | 2013-02-06 21:00 | 33795.0075 | 2865.8901 | 2370.3551 | 2394.1367 | 3043.2 | 3276.2 | 3016.4 | 3147.9 | 3371.3 | 2331.4 | 2506.8 | 3595.6 | 3841 | 3379 | 3552.8 | 76 | 2738.4 | 58.9
2013-02-06 | 22 | 2013-02-06 22:00 | 32355.1999 | 3282.9459 | 2750.0626 | 2831.6407 | 3279.3 | 3508.8 | 3238.4 | 3357.4 | 3571.5 | 2541.2 | 2707.2 | 3654.1 | 3894.6 | 3409.4 | 3572.6 | 2763.8 | 2756.2 | 1912.2
2013-02-06 | 23 | 2013-02-06 23:00 | 29752.8892 | 3988.4628 | 3479.9252 | 3553.6746 | 3423.4 | 3647.6 | 3385.7 | 3486.8 | 3689.4 | 2671.1 | 2825.8 | 4244.7 | 4485.4 | 4020.6 | 4178.2 | 70 | 3361.1 | 52.8
2013-02-06 | 24 | 2013-02-07 | 27142.2329 | 4882.6196 | 4368.8941 | 4451.7952 | 3688.5 | 3909.3 | 3673.5 | 3768.8 | 3961.2 | 2953.3 | 3097.7 | 5001 | 5259.9 | 4885.7 | 5013.4 | 2678.3 | 4195.7 | 1833.6
2013-02-07 | 1 | 2013-02-07 01:00 | 25347.8937 | 5347.6453 | 4870.5205 | 5062.8643 | 4771.2 | 5009.8 | 4691.2 | 4787.1 | 83.8 | 3974.1 | 66.6 | 4848 | 5093 | 4769.8 | 4899.8 | 83.8 | 4083.1 | 66.6
2013-02-07 | 2 | 2013-02-07 02:00 | 24457.3209 | 5324.4343 | 4893.5587 | 5021.3118 | 4993.7 | 5202.8 | 5025.7 | 5110.3 | 5013.7 | 4293.8 | 4163.3 | 5064.2 | 5309.6 | 5003.8 | 5127.9 | 5148.2 | 4309.8 | 4288.7
2013-02-07 | 3 | 2013-02-07 03:00 | 23984.2033 | 5215.0136 | 4810.5782 | 4868.0297 | 5225.8 | 5424.2 | 5269.2 | 5350.9 | 90.5 | 4534.2 | 73.4 | 5241.4 | 5468.4 | 5222.5 | 5301.3 | 90.5 | 4494.2 | 73.4
2013-02-07 | 4 | 2013-02-07 04:00 | 23917.7483 | 5119.1238 | 4777.0694 | 4859.0503 | 5237.3 | 5413.5 | 5197.5 | 5280 | 5301.9 | 4462.4 | 4449.6 | 5455.6 | 5677.6 | 5422.3 | 5487.2 | 5365.5 | 4679.9 | 4505.5
2013-02-07 | 5 | 2013-02-07 05:00 | 24452.3871 | 4972.558 | 4608.8987 | 4698.2457 | 5231.4 | 5404.4 | 5173.2 | 5258.2 | 115.4 | 4440.9 | 98.3 | 5369.2 | 5568.2 | 5373.2 | 5430.1 | 115.4 | 4626.6 | 98.3
2013-02-07 | 6 | 2013-02-07 06:00 | 26437.4943 | 4751.3275 | 4359.0832 | 4447.6651 | 5202.4 | 5390.9 | 5170.6 | 5232.4 | 5528.1 | 4417.4 | 4674.2 | 5125.5 | 5344.7 | 5092 | 5173.4 | 5503.1 | 4362.3 | 4664.9
2013-02-07 | 7 | 2013-02-07 07:00 | 30348.1355 | 4679.4233 | 4305.5332 | 4383.7069 | 4975.4 | 5161.9 | 4974.6 | 5015.2 | 121.3 | 4199.8 | 104.1 | 5006.6 | 5227 | 5024.8 | 5096.9 | 121.3 | 4289.1 | 104.1
2013-02-07 | 8 | 2013-02-07 08:00 | 31703.7274 | 4554.7042 | 4209.2005 | 4298.8149 | 4635.9 | 4852.4 | 4668.4 | 4683.4 | 5430.2 | 3868.1 | 4578.5 | 4685.4 | 4914.8 | 4685.4 | 4767 | 5677.8 | 3972.7 | 4839.1
2013-02-07 | 9 | 2013-02-07 09:00 | 31438.4421 | 3968.3665 | 3672.2759 | 3761.0341 | 3819.1 | 4023.5 | 3781.9 | 3813 | 114.5 | 3013.9 | 97.4 | 4037.9 | 4264.1 | 4036.2 | 4095.6 | 114.5 | 3332.5 | 97.4
2013-02-07 | 10 | 2013-02-07 10:00 | 31789.2742 | 3939.3454 | 3586.8986 | 3668.6201 | 2963 | 3169.7 | 2901.7 | 2940.2 | 5402.8 | 2148.1 | 4550.7 | 3621.8 | 3853.5 | 3603.5 | 3678.5 | 5608.5 | 2928.4 | 4775.7
2013-02-07 | 11 | 2013-02-07 11:00 | 32372.5942 | 4285.3343 | 3949.3464 | 4049.6241 | 2621.5 | 2820.4 | 2561.1 | 2594.2 | 104.6 | 1800.7 | 87.4 | 3615 | 3834.3 | 3592.9 | 3653.9 | 104.6 | 2896.4 | 87.4
2013-02-07 | 12 | 2013-02-07 12:00 | 32591.5782 | 3642.3934 | 3309.3661 | 3413.9416 | 2568.4 | 2766 | 2576.8 | 2607.6 | 5384.7 | 1816.3 | 4534.3 | 3637.5 | 3849.3 | 3601.3 | 3658.6 | 5361.1 | 2888.2 | 4520
2013-02-07 | 13 | 2013-02-07 13:00 | 32822.9764 | 4141.047 | 3784.9037 | 3888.8584 | 2693.9 | 2896.6 | 2709.3 | 2749.7 | 81.4 | 1958.4 | 64.2 | 3727.5 | 3944.9 | 3696.7 | 3754.7 | 81.4 | 2968.1 | 64.2
2013-02-07 | 14 | 2013-02-07 14:00 | 33307.7706 | 4604.1409 | 4207.1987 | 4296.7575 | 2800.5 | 3015.1 | 2792.4 | 2840 | 5162.3 | 2046.5 | 4309.9 | 4065.4 | 4292.6 | 4036 | 4090.6 | 5280 | 3286.1 | 4442.8
2013-02-07 | 15 | 2013-02-07 15:00 | 33402.322 | 4418.0993 | 3974.435 | 4056.0885 | 2892.1 | 3144.8 | 2905 | 2959.7 | 76.2 | 2163.8 | 59.1 | 3931.9 | 4184.5 | 3880.5 | 3949 | 76.2 | 3139.8 | 59.1
2013-02-07 | 16 | 2013-02-07 16:00 | 33431.5088 | 4622.0651 | 4149.6482 | 4231.363 | 2894.7 | 3158.2 | 2895.2 | 2981 | 4863.1 | 2172.2 | 4010.4 | 4264.8 | 4544 | 4179.4 | 4289.7 | 4974.3 | 3476.3 | 4147.1
2013-02-07 | 17 | 2013-02-07 17:00 | 33414.5693 | 4751.3588 | 4207.1025 | 4271.7606 | 2859.3 | 3118.6 | 2816.7 | 2939.6 | 64.9 | 2125.9 | 47.7 | 4210.7 | 4479.6 | 4087.2 | 4222.6 | 64.9 | 3411.2 | 47.7
2013-02-07 | 18 | 2013-02-07 18:00 | 33233.515 | 4295.2074 | 3731.6461 | 3772.2384 | 2667.7 | 2923 | 2600.9 | 2737.8 | 3984 | 1924 | 3156.1 | 3692.7 | 3973.4 | 3544.8 | 3692.3 | 4288.1 | 2887.8 | 3501
2013-02-07 | 19 | 2013-02-07 19:00 | 34487.0449 | 3479.5253 | 2986.5092 | 2995.6444 | 2648.4 | 2895.9 | 2568.6 | 2701.6 | 56 | 1891.2 | 38.8 | 3659.5 | 3931.9 | 3498.7 | 3644.9 | 56 | 2837 | 38.8
2013-02-07 | 20 | 2013-02-07 20:00 | 34883.5663 | 3524.7392 | 3119.3448 | 3123.6187 | 2739.7 | 2962.9 | 2679.9 | 2810.5 | 3115.7 | 2004.5 | 2294.8 | 3787.3 | 4061.5 | 3600.8 | 3750.8 | 3880.5 | 2945.9 | 3102.3
2013-02-07 | 21 | 2013-02-07 21:00 | 34175.7921 | 3763.6747 | 3453.1871 | 3453.8543 | 2935.4 | 3194.2 | 2842.6 | 2964.6 | 51.7 | 2160.1 | 34.5 | 3893 | 4077.4 | 3703.3 | 3838.6 | 51.7 | 3032.9 | 34.5
2013-02-07 | 22 | 2013-02-07 22:00 | 32625.4483 | 3631.0147 | 3357.6651 | 3357.9996 | 3067.8 | 3322 | 2999.8 | 3106.2 | 2770.3 | 2300.9 | 1949.1 | 3532.2 | 3703.9 | 3323.9 | 3451.5 | 3844.4 | 2650.2 | 3057.7
2013-02-07 | 23 | 2013-02-07 23:00 | 30024.5661 | 3681.6386 | 3370.737 | 3370.7546 | 3117.2 | 3354 | 3083.9 | 3174.8 | 72.1 | 2368.9 | 55 | 3617.2 | 3773.4 | 3435.3 | 3543.5 | 72.1 | 2767.9 | 55
2013-02-07 | 24 | 2013-02-08 | 27368.2718 | 3680.3803 | 3368.8791 | 3371.022 | 3161.6 | 3378.7 | 3165.1 | 3233.4 | 2787 | 2431.6 | 1966.8 | 3831.7 | 3969.7 | 3704 | 3771.1 | 3854.5 | 3017.1 | 3051.9
2013-02-08 | 1 | 2013-02-08 01:00 | 25652.9017 | 3806.0545 | 3478.7096 | 3479.1849 | 4055.2 | 4313 | 3938.3 | 4065 | 4290.5 | 3252.3 | 3429.7 | 3874.5 | 4004.5 | 3736.6 | 3803.7 | 3998.3 | 3022.1 | 3178.4
2013-02-08 | 2 | 2013-02-08 02:00 | 24683.7991 | 3900.9239 | 3561.7203 | 3561.8071 | 4041.9 | 4293 | 3930.3 | 4065.4 | 4291.4 | 3253.1 | 3431 | 3903.5 | 4020.3 | 3738.7 | 3818.3 | 4003.1 | 3036.6 | 3181.6
2013-02-08 | 3 | 2013-02-08 03:00 | 24299.721 | 4128.6096 | 3797.6023 | 3798.8661 | 4092.5 | 4325.4 | 3977.4 | 4112.1 | 4327.4 | 3296 | 3463.3 | 3712.7 | 3803.1 | 3572.9 | 3651.2 | 3800.9 | 2847 | 2962.7
2013-02-08 | 4 | 2013-02-08 04:00 | 24324.7217 | 4305.9466 | 3944.3567 | 3947.5387 | 3995 | 4207.3 | 3869.9 | 4028.8 | 4223.7 | 3213.6 | 3360.5 | 3776.9 | 3851 | 3653.3 | 3738.6 | 3863.3 | 2921.2 | 3011.4
2013-02-08 | 5 | 2013-02-08 05:00 | 25032.3177 | 4265.1364 | 3969.6774 | 3969.9061 | 3748.6 | 3930.8 | 3635.6 | 3795 | 3961.8 | 2979.2 | 3098 | 3793.1 | 3863.2 | 3670 | 3767.7 | 3868.7 | 2950.4 | 3013.2
2013-02-08 | 6 | 2013-02-08 06:00 | 27370.2614 | 4047.0408 | 3792.7036 | 3799.5622 | 3540.3 | 3670 | 3380.4 | 3580.8 | 3695.7 | 2765.3 | 2832.1 | 3722.8 | 3802.6 | 3608.9 | 3738.9 | 3808 | 2920.9 | 2946.8
2013-02-08 | 7 | 2013-02-08 07:00 | 31760.9368 | 3986.4481 | 3734.3304 | 3743.4438 | 3221.2 | 3377.7 | 3044.6 | 3256 | 3381.5 | 2440.9 | 2522.7 | 3688.4 | 3803.2 | 3531.2 | 3722.5 | 3815.8 | 2905.2 | 2953.5
2013-02-08 | 8 | 2013-02-08 08:00 | 33241.7953 | 3638.2045 | 3385.5765 | 3375.0727 | 2737.3 | 2909.7 | 2564.3 | 2770.9 | 2892.9 | 1953.8 | 2035.9 | 3563.2 | 3710.6 | 3394 | 3598.6 | 3708.9 | 2781 | 2846.3
2013-02-08 | 9 | 2013-02-08 09:00 | 32861.3686 | 2811.8398 | 2484.923 | 2464.2731 | 2202.1 | 2377.3 | 2037.4 | 2225.6 | 2328.8 | 1412.5 | 1484 | 3034.2 | 3193.4 | 2859.8 | 3047.1 | 3155.8 | 2230.6 | 2296.2
2013-02-08 | 10 | 2013-02-08 10:00 | 32809.2171 | 2058.0891 | 1705.7463 | 1702.735 | 1816.7 | 2001.6 | 1675.2 | 1836.1 | 1921.8 | 1027.7 | 1083.5 | 2608.9 | 2791.1 | 2476.5 | 2637.7 | 2719.3 | 1822.3 | 1875.6
2013-02-08 | 11 | 2013-02-08 11:00 | 32650.4938 | 1882.1158 | 1606.9479 | 1599.1577 | 1670.1 | 1877 | 1570.2 | 1690.2 | 1760.7 | 877.8 | 916.6 | 2566 | 2779.1 | 2442.8 | 2586.3 | 2664.9 | 1771.6 | 1824.5
2013-02-08 | 12 | 2013-02-08 12:00 | 32294.5245 | 1650.1325 | 1460.7497 | 1453.9253 | 1574.6 | 1772.8 | 1509.2 | 1599.9 | 1653.3 | 793.2 | 819.5 | 2217.9 | 2442.6 | 2024.7 | 2161.8 | 2305.6 | 1354 | 1458.7
2013-02-08 | 13 | 2013-02-08 13:00 | 31818.1137 | 1422.0576 | 1270.2105 | 1268.9152 | 1529.8 | 1724.1 | 1471.1 | 1552.1 | 1597.7 | 746.4 | 764.8 | 1770.7 | 2002.8 | 1649.5 | 1792.2 | 1950.9 | 1001.2 | 1122.2
2013-02-08 | 14 | 2013-02-08 14:00 | 31803.0493 | 1288.4317 | 1179.2044 | 1193.0865 | 1584.6 | 1742.4 | 1544 | 1610.8 | 1647.6 | 807.9 | 819.8 | 1845.1 | 2027.9 | 1752 | 1875.6 | 2024 | 1083.1 | 1191.4
2013-02-08 | 15 | 2013-02-08 15:00 | 31645.9608 | 1379.8599 | 1296.2292 | 1311.0909 | 1781.6 | 1921.5 | 1748.3 | 1810.6 | 1846.1 | 1006.5 | 1015 | 1783.8 | 1890.6 | 1762.6 | 1821 | 1892.1 | 1074.6 | 1107.1
2013-02-08 | 16 | 2013-02-08 16:00 | 31433.4554 | 1714.5086 | 1610.1605 | 1609.3756 | 2025 | 2152.9 | 1995.4 | 2058.3 | 2097.6 | 1252.2 | 1260.6 | 2029.3 | 2132.6 | 2000.9 | 2060 | 2130.2 | 1303.8 | 1331.3
2013-02-08 | 17 | 2013-02-08 17:00 | 31310.2462 | 2355.2887 | 2186.6664 | 2188.2553 | 2340.2 | 2487.3 | 2312.3 | 2377.3 | 2427.7 | 1567.9 | 1580.5 | 2331.8 | 2459.3 | 2247.8 | 2336.9 | 2479.4 | 1532.3 | 1616
2013-02-08 | 18 | 2013-02-08 18:00 | 31164.1501 | 2826.4317 | 2609.4316 | 2610.215 | 2505.6 | 2665.5 | 2473.2 | 2537.6 | 2599.8 | 1723.4 | 1744.1 | 2495.1 | 2638 | 2396.4 | 2494.2 | 2649.8 | 1682.8 | 1775.7
2013-02-08 | 19 | 2013-02-08 19:00 | 32539.0751 | 2835.1628 | 2565.4722 | 2568.5242 | 2823 | 3008.9 | 2788.2 | 2850.1 | 2926.3 | 2034.7 | 2065 | 2910.9 | 3064.3 | 2834.5 | 2924 | 3072.1 | 2112.6 | 2196.2
2013-02-08 | 20 | 2013-02-08 20:00 | 32794.6821 | 3417.7812 | 3069.92 | 3076.3646 | 3523.8 | 3741.7 | 3479 | 3546.2 | 3648.8 | 2730.4 | 2788.4 | 3693.5 | 3884.8 | 3603.4 | 3705.1 | 3874.6 | 2893 | 2997.8
2013-02-08 | 21 | 2013-02-08 21:00 | 32238.5375 | 4621.5928 | 4125.6482 | 4162.4754 | 4495.3 | 4751.7 | 4471.5 | 4551.7 | 4686.6 | 3736.3 | 3825.8 | 4417.1 | 4618 | 4323.7 | 4432.7 | 4622.2 | 3621.5 | 3746.4
2013-02-08 | 22 | 2013-02-08 22:00 | 31371.2466 | 5502.1193 | 4921.1336 | 5007.392 | 5095.5 | 5396.8 | 5056.9 | 5157.7 | 5331.2 | 4341.6 | 4467.3 | 4706.3 | 4925.9 | 4591.3 | 4722.3 | 4939.3 | 3910.9 | 4063.3
2013-02-08 | 23 | 2013-02-08 23:00 | 29931.9508 | 6476.9745 | 5831.402 | 5912.9687 | 5546.4 | 5899.2 | 5481.8 | 5599.6 | 5809.9 | 4783 | 4945.4 | 5314.8 | 5563.8 | 5158.7 | 5320.3 | 5569.5 | 4508.7 | 4693.3
2013-02-08 | 24 | 2013-02-09 | 28156.3442 | 7214.3083 | 6560.2477 | 6623.7785 | 5938.9 | 6329.6 | 5849.7 | 5985.1 | 6219.6 | 5169.4 | 5356 | 5939.1 | 6217.7 | 5781.9 | 5940.8 | 6217.4 | 5128.9 | 5341
2013-02-09 | 1 | 2013-02-09 01:00 | 26746.2565 | 7157.468 | 6498.6347 | 6576.8002 | 5954.1 | 6278.2 | 5884.5 | 6020.1 | 6294.1 | 5207.4 | 5416.8 | 6341.6 | 6614 | 6208.3 | 6349 | 6608.1 | 5536.8 | 5731.4
2013-02-09 | 2 | 2013-02-09 02:00 | 25916.2932 | 7360.5224 | 6734.0204 | 6825.5516 | 6168 | 6473.4 | 6068.7 | 6201.4 | 6462.5 | 5389.6 | 5586.1 | 6757 | 7007.2 | 6659.6 | 6778.8 | 7017.7 | 5965.9 | 6140.3
2013-02-09 | 3 | 2013-02-09 03:00 | 25481.2976 | 7516.3589 | 6966.4739 | 7129.0606 | 6414.9 | 6721.5 | 6340.1 | 6454.2 | 6713.2 | 5643.7 | 5838.1 | 7171.4 | 7443.3 | 7080.7 | 7200.9 | 7457.3 | 6387.5 | 6579.4
2013-02-09 | 4 | 2013-02-09 04:00 | 25275.6193 | 7468.5701 | 6971.464 | 7209.1939 | 6558.9 | 6860.1 | 6504.2 | 6619.8 | 6872.1 | 5808.4 | 5996 | 7429.9 | 7733.2 | 7356.4 | 7471 | 7744 | 6658.2 | 6866.5
2013-02-09 | 5 | 2013-02-09 05:00 | 25472.0603 | 7647.8566 | 7129.6311 | 7182.4698 | 6662.8 | 6955.7 | 6607.8 | 6722.4 | 6968.3 | 5911.2 | 6092.6 | 7573.4 | 7871.9 | 7476.9 | 7601.4 | 7870.9 | 6788.7 | 6993.8
2013-02-09 | 6 | 2013-02-09 06:00 | 26332.4562 | 7797.7365 | 7211.3343 | 7308.2703 | 6718.3 | 7003.6 | 6650.6 | 6772.1 | 7011.9 | 5960.7 | 6135.8 | 7751.5 | 8062.6 | 7638.3 | 7774.4 | 8054.7 | 6963.2 | 7179
2013-02-09 | 7 | 2013-02-09 07:00 | 27852.6056 | 7910.4668 | 7313.9236 | 7408.5101 | 6841 | 7144.1 | 6716.9 | 6852.7 | 7111 | 6040.4 | 6234 | 7846.8 | 8167.5 | 7734.1 | 7879.5 | 8172.1 | 7067.3 | 7295.1
2013-02-09 | 8 | 2013-02-09 08:00 | 29232.4853 | 8001.9282 | 7373.215 | 7451.5629 | 7015.9 | 7321.1 | 6886.4 | 7018.7 | 7269.2 | 6205.6 | 6391.3 | 7818.4 | 8152.8 | 7682.1 | 7838.7 | 8138.4 | 7026 | 7261.1
2013-02-09 | 9 | 2013-02-09 09:00 | 30753.0811 | 8175.9472 | 7495.6746 | 7545.9575 | 7337.7 | 7646.6 | 7252 | 7354.6 | 7601.6 | 6542.7 | 6725.3 | 7899 | 8309 | 7787.5 | 7947.6 | 8268.6 | 7134.7 | 7391.1
2013-02-09 | 10 | 2013-02-09 10:00 | 32056.2716 | 8462.018 | 7719.0917 | 7755.5476 | 7490.5 | 7858.6 | 7396.7 | 7505.1 | 7783 | 6692.1 | 6905.6 | 8111.6 | 8552.5 | 7996.3 | 8172.7 | 8531 | 7360 | 7653.7
2013-02-09 | 11 | 2013-02-09 11:00 | 32751.4603 | 8735.0255 | 7958.8734 | 7992.3402 | 7525 | 7918.1 | 7383.1 | 7514.5 | 7816.7 | 6701.7 | 6939.2 | 8146.1 | 8636.4 | 8007.3 | 8186.2 | 8577.4 | 7373 | 7699.7
2013-02-09 | 12 | 2013-02-09 12:00 | 32822.7783 | 8883.4336 | 8143.3364 | 8253.9319 | 7539.7 | 8011.5 | 7359.1 | 7526.8 | 7914.6 | 6713.9 | 7037 | 8252.7 | 8786.7 | 8127.7 | 8308.1 | 8754.4 | 7494.8 | 7876.6
2013-02-09 | 13 | 2013-02-09 13:00 | 32520.2619 | 8882.8362 | 8175.6932 | 8370.7173 | 7523.7 | 8062.1 | 7351.3 | 7542.6 | 8019.7 | 6729.8 | 7142.5 | 8318.8 | 8865.4 | 8166.9 | 8378.4 | 8849.5 | 7565.6 | 7972.3
2013-02-09 | 14 | 2013-02-09 14:00 | 32012.2157 | 9038.2756 | 8336.0705 | 8496.8283 | 7547.4 | 8103.5 | 7377.2 | 7584.6 | 8083.5 | 6771.9 | 7206.3 | 8548.6 | 9120.4 | 8359.4 | 8584.2 | 9100.6 | 7771.4 | 8223.2
2013-02-09 | 15 | 2013-02-09 15:00 | 31745.1077 | 9153.7852 | 8342.6684 | 8521.2482 | 7633.2 | 8223.3 | 7444.1 | 7674.6 | 8204.9 | 6860.8 | 7326.5 | 8574.3 | 9168.1 | 8388.9 | 8610.6 | 9150.7 | 7797.6 | 8273.1
2013-02-09 | 16 | 2013-02-09 16:00 | 31624.1969 | 9151.2861 | 8294.173 | 8475.1879 | 7712.5 | 8315.8 | 7503.6 | 7746.5 | 8286.5 | 6933.1 | 7408.6 | 8678.4 | 9282.5 | 8450.4 | 8696.4 | 9285.3 | 7883.4 | 8407.6
2013-02-09 | 17 | 2013-02-09 17:00 | 31888.0463 | 9245.6221 | 8385.0973 | 8524.2439 | 7479.7 | 8084.9 | 7237.2 | 7488.8 | 8036.7 | 6676.2 | 7159.6 | 8479.1 | 9108.9 | 8230.8 | 8482.3 | 9093.6 | 7668.9 | 8215.7
2013-02-09 | 18 | 2013-02-09 18:00 | 32599.5027 | 9305.9113 | 8421.9493 | 8489.4419 | 6714.2 | 7306.2 | 6404.7 | 6683.3 | 7228.9 | 5870.3 | 6351.4 | 8325.5 | 8964.5 | 8044.1 | 8314.6 | 8960.6 | 7502.6 | 8084.1
2013-02-09 | 19 | 2013-02-09 19:00 | 33865.5417 | 9304.4526 | 8407.6902 | 8462.8834 | 6706.4 | 7328.4 | 6355.1 | 6653.3 | 7234.1 | 5840.2 | 6356.4 | 8427.2 | 9054.6 | 8142.5 | 8432.2 | 9056.8 | 7619.8 | 8179.8
2013-02-09 | 20 | 2013-02-09 20:00 | 33739.6155 | 9421.3444 | 8526.8431 | 8594.4452 | 7032 | 7702.2 | 6659.1 | 6966.5 | 7603.1 | 6153.8 | 6725.9 | 8567.4 | 9202.2 | 8274.3 | 8572.1 | 9210.6 | 7762.4 | 8336.2
2013-02-09 | 21 | 2013-02-09 21:00 | 32953.6341 | 9165.968 | 8241.2146 | 8299.4275 | 7264.3 | 7965 | 6898.1 | 7212.5 | 7882.4 | 6400 | 7005.4 | 8342.9 | 8970.5 | 8045 | 8349.3 | 8995.5 | 7539.9 | 8121.6
2013-02-09 | 22 | 2013-02-09 22:00 | 31836.251 | 8330.4208 | 7346.7211 | 7379.3771 | 6809.8 | 7505.6 | 6416.3 | 6744.6 | 7401.2 | 5931.7 | 6523.9 | 7847.3 | 8478.9 | 7507.5 | 7834.1 | 8500.5 | 7023.9 | 7625.7
2013-02-09 | 23 | 2013-02-09 23:00 | 30186.2783 | 7583.7631 | 6623.5242 | 6651.7389 | 6655.6 | 7357.8 | 6205.5 | 6557.3 | 7216.1 | 5744 | 6338.4 | 7589.4 | 8228.3 | 7246 | 7582.5 | 8244.7 | 6770.1 | 7367.6
2013-02-09 | 24 | 2013-02-10 | 28311.0593 | 7499.63 | 6600.7607 | 6644.7739 | 6571.8 | 7272.6 | 6184.3 | 6529.6 | 7189.6 | 5717.5 | 6312.8 | 7461.1 | 8083.4 | 7167 | 7468.5 | 8089.5 | 6655.6 | 7211.9
2013-02-10 | 1 | 2013-02-10 01:00 | 26712.4644 | 7708.3719 | 6869.3889 | 6900.8414 | 7463.1 | 8144.5 | 7283.7 | 7554 | 8207.5 | 6741.4 | 7330.3 | 7006.4 | 7603.7 | 6804.5 | 7064.6 | 7630.4 | 6251.6 | 6752.8
2013-02-10 | 2 | 2013-02-10 02:00 | 25516.4264 | 7287.2412 | 6450.4008 | 6504.636 | 7285.3 | 7938.6 | 7135.8 | 7418.5 | 8060.4 | 6605.6 | 7183 | 6636.3 | 7236.6 | 6421.1 | 6684.7 | 7246 | 5871.4 | 6368.1
2013-02-10 | 3 | 2013-02-10 03:00 | 24825.1621 | 7350.7017 | 6539.8304 | 6594.126 | 7225.2 | 7896.4 | 6970.4 | 7267.3 | 7920.8 | 6455.4 | 7044.3 | 6488.5 | 7062.8 | 6218.1 | 6501.9 | 7037.7 | 5688.8 | 6160
2013-02-10 | 4 | 2013-02-10 04:00 | 24532.2155 | 7169.3822 | 6426.271 | 6483.1583 | 7381.8 | 8101.3 | 7126.5 | 7411.4 | 8106.2 | 6599.9 | 7230.1 | 6707.1 | 7266.2 | 6405.3 | 6658.6 | 7207.7 | 5845.6 | 6329.9
2013-02-10 | 5 | 2013-02-10 05:00 | 24485.119 | 6917.7913 | 6291.0743 | 6356.3449 | 7550.2 | 8275.1 | 7372.8 | 7624.4 | 8307.1 | 6812.4 | 7430.5 | 6619.7 | 7137.3 | 6401.5 | 6603.7 | 7121.8 | 5790.5 | 6244
2013-02-10 | 6 | 2013-02-10 06:00 | 24893.8244 | 7003.3245 | 6228.7277 | 6293.4695 | 7581.4 | 8263.5 | 7437 | 7639.4 | 8249.5 | 6826.5 | 7372 | 6785.8 | 7282.5 | 6593.4 | 6768.2 | 7258.4 | 5954.7 | 6380.3
2013-02-10 | 7 | 2013-02-10 07:00 | 25580.1285 | 6934.5437 | 6074.666 | 6125.4961 | 7568.4 | 8185.4 | 7446.6 | 7624 | 8155.3 | 6811.2 | 7277.8 | 6737.5 | 7215.6 | 6570.9 | 6747.5 | 7229.9 | 5935.1 | 6353.1
2013-02-10 | 8 | 2013-02-10 08:00 | 26482.9648 | 6504.0025 | 5702.0088 | 5752.9998 | 7411.3 | 7984.9 | 7268.7 | 7463.1 | 7960.4 | 6651 | 7083.8 | 6590.8 | 7090.3 | 6400.5 | 6599.3 | 7071.7 | 5786.2 | 6194
2013-02-10 | 9 | 2013-02-10 09:00 | 27924.1473 | 6112.9229 | 5275.2573 | 5317.3209 | 6935.3 | 7486 | 6784.1 | 6996.5 | 7466.5 | 6184.7 | 6590 | 5978.8 | 6492.1 | 5769.7 | 5973.8 | 6414 | 5160.8 | 5536.4
2013-02-10 | 10 | 2013-02-10 10:00 | 29338.3127 | 6795.9191 | 5984.6903 | 6010.7354 | 6574.2 | 7118.4 | 6494.6 | 6661.6 | 7065.5 | 5849.8 | 6189 | 5385.4 | 5877.5 | 5229 | 5400 | 5778.8 | 4587.2 | 4901.5
2013-02-10 | 11 | 2013-02-10 11:00 | 30081.0474 | 6530.235 | 5782.9963 | 5808.6325 | 6132.5 | 6629.2 | 6098.6 | 6219.7 | 6546.2 | 5407.4 | 5669.5 | 4860.4 | 5294.8 | 4739.1 | 4878.3 | 5203.4 | 4066 | 4326.5
2013-02-10 | 12 | 2013-02-10 12:00 | 30003.0742 | 5191.3939 | 4548.8174 | 4561.8845 | 5932.4 | 6371.6 | 5920.8 | 5985 | 6261.6 | 5174.9 | 5406.8 | 4376.4 | 4725.3 | 4322.1 | 4411.2 | 4631.2 | 3599 | 3759.6
2013-02-10 | 13 | 2013-02-10 13:00 | 29897.6551 | 4273.7084 | 3737.0958 | 3737.9493 | 5853.4 | 6240.7 | 5833.7 | 5893 | 6151.4 | 5091.3 | 5315 | 4230.9 | 4539.4 | 4178.2 | 4252.6 | 4415.9 | 3442 | 3557.1
2013-02-10 | 14 | 2013-02-10 14:00 | 29644.0652 | 3963.5618 | 3488.7381 | 3476.2158 | 5676.3 | 6009 | 5579.9 | 5643.1 | 5889.8 | 4837.2 | 5045 | 4233.2 | 4460.5 | 4208.7 | 4269.3 | 4402.5 | 3464.3 | 3557.7
2013-02-10 | 15 | 2013-02-10 15:00 | 29289.443 | 3347.4186 | 2985.4122 | 2979.0988 | 5364.6 | 5652.6 | 5318.7 | 5381.7 | 5617.3 | 4568.9 | 4757 | 3716.5 | 3908.1 | 3678.3 | 3740.8 | 3855.1 | 2930.4 | 2997.8
2013-02-10 | 16 | 2013-02-10 16:00 | 29062.7799 | 2860.3874 | 2571.5699 | 2577.9871 | 4917.1 | 5178.4 | 4846.7 | 4917.9 | 5153.2 | 4105.1 | 4275.8 | 3176.4 | 3399.4 | 3132.1 | 3197.3 | 3301.1 | 2387.1 | 2434
2013-02-10 | 17 | 2013-02-10 17:00 | 29112.732 | 2410.8684 | 2139.8524 | 2130.8084 | 4269.3 | 4523.4 | 4193.1 | 4253.7 | 4485.7 | 3441.8 | 3611.4 | 2969.8 | 3209.7 | 2937.1 | 2990.6 | 3072.6 | 2180.8 | 2211
2013-02-10 | 18 | 2013-02-10 18:00 | 29819.7887 | 2077.8885 | 1757.9852 | 1748.7542 | 3339.4 | 3592 | 3263.4 | 3303.3 | 3479.7 | 2490.7 | 2607.1 | 2259 | 2454.5 | 2173.7 | 2248.7 | 2325.6 | 1439.6 | 1460.5
2013-02-10 | 19 | 2013-02-10 19:00 | 31933.4953 | 1489.1658 | 1168.0728 | 1173.4026 | 3077.7 | 3370.4 | 2936.4 | 2990.9 | 3135.3 | 2185.7 | 2267.6 | 2119.3 | 2346.8 | 1956 | 2092.3 | 2249.8 | 1284.4 | 1381.7
2013-02-10 | 20 | 2013-02-10 20:00 | 32804.3336 | 1258.1031 | 935.6593 | 949.3263 | 3086.4 | 3371.7 | 2811.3 | 2899.8 | 3051.1 | 2099.7 | 2188.5 | 1838.8 | 2062 | 1669.7 | 1817.9 | 1936.9 | 1019 | 1076.1
2013-02-10 | 21 | 2013-02-10 21:00 | 32226.7038 | 861.2224 | 690.6573 | 700.6417 | 3106.1 | 3382.6 | 2868.4 | 2975 | 3147.5 | 2178.8 | 2286.9 | 1651.7 | 1786.2 | 1487.2 | 1613.8 | 1756.1 | 878.1 | 961.7
2013-02-10 | 22 | 2013-02-10 22:00 | 31216.1287 | 720.4454 | 529.4312 | 536.5122 | 2996.1 | 3243.5 | 2751.8 | 2868 | 3051.9 | 2071.7 | 2190.8 | 1438.4 | 1537.9 | 1260.3 | 1362.7 | 1486.7 | 754.4 | 821.3
2013-02-10 | 23 | 2013-02-10 23:00 | 29346.2102 | 539.4852 | 350.0362 | 363.9087 | 2960.2 | 3183.3 | 2750.1 | 2872.3 | 3057 | 2081.2 | 2201.3 | 1542.6 | 1686.8 | 1364.2 | 1493.1 | 1658.3 | 760.1 | 864.4
2013-02-10 | 24 | 2013-02-11 | 27240.3691 | 587.84 | 390.5262 | 406.8878 | 3081.7 | 3291.2 | 2904.4 | 3037.9 | 3232.6 | 2235.7 | 2365.9 | 1557 | 1709.5 | 1390.7 | 1510.4 | 1684.1 | 788.2 | 897.4
2013-02-11 | 1 | 2013-02-11 01:00 | 25689.441 | 860.0769 | 536.8234 | 556.6251 | 2465.5 | 2604.7 | 2367 | 2465.7 | 2579 | 1663.3 | 1719.5 | 2107.5 | 2255.7 | 1925.4 | 2081.6 | 2247.6 | 1286.2 | 1391.7
2013-02-11 | 2 | 2013-02-11 02:00 | 24808.1212 | 1176.6809 | 757.9784 | 778.1881 | 2774.2 | 2944.6 | 2678 | 2797.2 | 2954.7 | 1991.8 | 2089.1 | 2151.8 | 2334.3 | 1943.9 | 2136 | 2343.9 | 1336.1 | 1479.3
2013-02-11 | 3 | 2013-02-11 03:00 | 24465.6573 | 1570.7933 | 1221.9155 | 1235.3615 | 2774.7 | 2956 | 2672.5 | 2799.5 | 2989.2 | 1992.2 | 2118.3 | 2124.5 | 2315 | 1865.8 | 2082.8 | 2287.6 | 1280 | 1420.1
2013-02-11 | 4 | 2013-02-11 04:00 | 24533.2269 | 1658.8627 | 1415.3844 | 1420.1413 | 2791.1 | 2995.2 | 2691.9 | 2806.2 | 3006.1 | 1998.6 | 2133.8 | 2474.3 | 2740.2 | 2192 | 2451.9 | 2733.2 | 1647.5 | 1864.1
2013-02-11 | 5 | 2013-02-11 05:00 | 25420.966 | 1878.3972 | 1642.9822 | 1646.7922 | 2940.7 | 3141.2 | 2837.2 | 2953 | 3141.6 | 2144.6 | 2270.6 | 2791.4 | 3071.8 | 2554.7 | 2791.1 | 3081.9 | 1997.7 | 2224
2013-02-11 | 6 | 2013-02-11 06:00 | 27964.07 | 2006.3063 | 1791.2217 | 1793.2962 | 3447.3 | 3619.6 | 3302.4 | 3425.3 | 3585.9 | 2617.9 | 2718.1 | 3199.6 | 3425 | 3008.3 | 3211.9 | 3438.8 | 2406.3 | 2569.1
2013-02-11 | 7 | 2013-02-11 07:00 | 32131.3857 | 2289.5953 | 2067.6166 | 2073.8874 | 4013 | 4229.8 | 3897.2 | 4025.4 | 4220.3 | 3217.5 | 3352.6 | 3076.3 | 3269.7 | 2871.1 | 3041.3 | 3235.8 | 2242.8 | 2377.6
2013-02-11 | 8 | 2013-02-11 08:00 | 33672.0568 | 2792.8395 | 2560.044 | 2571.1315 | 4139.6 | 4343.9 | 4018.7 | 4152.8 | 4320.9 | 3344.2 | 3453.7 | 3168.8 | 3365.7 | 2966.6 | 3114.2 | 3319.1 | 2314.4 | 2454.9
2013-02-11 | 9 | 2013-02-11 09:00 | 33289.7412 | 2602.9403 | 2366.729 | 2370.3175 | 4213.9 | 4403.3 | 4159.4 | 4248.8 | 4387.3 | 3440.5 | 3530.6 | 2773.6 | 2909 | 2626 | 2756.6 | 2942.7 | 1952.1 | 2073.6
2013-02-11 | 10 | 2013-02-11 10:00 | 33557.5626 | 2349.9216 | 2170.7583 | 2174.9785 | 3853.2 | 4047.3 | 3856.2 | 3907.1 | 4041.5 | 3098.7 | 3193.6 | 2465.3 | 2586.6 | 2365 | 2477.2 | 2646.6 | 1674.8 | 1779.6
2013-02-11 | 11 | 2013-02-11 11:00 | 33879.2156 | 2429.7206 | 2238.8604 | 2254.3801 | 3849.4 | 4046.8 | 3903.6 | 3914.3 | 4048 | 3106.2 | 3204.1 | 2326 | 2415.5 | 2249.6 | 2324.7 | 2452.5 | 1519.9 | 1583
2013-02-11 | 12 | 2013-02-11 12:00 | 33901.4716 | 2091.7119 | 1919.2083 | 1921.0084 | 3991.4 | 4176.2 | 4054.7 | 4061.3 | 4186.5 | 3253 | 3341.1 | 2314.5 | 2387.7 | 2249 | 2292.9 | 2383.6 | 1495.4 | 1522.6
2013-02-11 | 13 | 2013-02-11 13:00 | 33746.3065 | 1858.9805 | 1727.898 | 1727.1438 | 4118.3 | 4293.8 | 4143.6 | 4162 | 4283.1 | 3353.2 | 3434.6 | 2186.9 | 2257.5 | 2160.6 | 2210.2 | 2300.8 | 1414.1 | 1440.7
2013-02-11 | 14 | 2013-02-11 14:00 | 33503.0394 | 1853.4016 | 1728.684 | 1728.1907 | 4277.7 | 4469.1 | 4266.8 | 4294.6 | 4420.1 | 3484.7 | 3561.8 | 2342.3 | 2401.9 | 2318.7 | 2357.4 | 2422.7 | 1554.7 | 1575.4
2013-02-11 | 15 | 2013-02-11 15:00 | 33200.0726 | 2134.297 | 2016.1433 | 2015.3584 | 4574.1 | 4801.4 | 4559.6 | 4605.3 | 4740.5 | 3795.3 | 3869.7 | 2482 | 2554.9 | 2449.4 | 2496.3 | 2562.6 | 1691.6 | 1709.4
2013-02-11 | 16 | 2013-02-11 16:00 | 33250.6828 | 2670.3711 | 2531.006 | 2521.6891 | 4760 | 5031.9 | 4729.5 | 4785 | 4933.6 | 3974.7 | 4058.7 | 2695 | 2773.4 | 2637.5 | 2697.6 | 2789.4 | 1891.1 | 1920.2
2013-02-11 | 17 | 2013-02-11 17:00 | 33718.4298 | 3066.5287 | 2829.9179 | 2829.4806 | 4874.1 | 5171 | 4821.8 | 4890.2 | 5057.8 | 4080.2 | 4183.2 | 3154.5 | 3262.9 | 3063.4 | 3143.5 | 3280.3 | 2336.4 | 2408.6
2013-02-11 | 18 | 2013-02-11 18:00 | 34752.9411 | 3491.0262 | 3196.3289 | 3191.6932 | 4767.1 | 5076.6 | 4671.6 | 4764.4 | 4963.6 | 3952.9 | 4087.6 | 3820 | 3931 | 3735.3 | 3812 | 3966.9 | 3001.6 | 3092
2013-02-11 | 19 | 2013-02-11 19:00 | 36621.9642 | 3894.5147 | 3527.5589 | 3528.5208 | 5045.7 | 5379.4 | 4948.5 | 5044.1 | 5262.3 | 4232.5 | 4386 | 4159.4 | 4297.2 | 4021.6 | 4122.7 | 4312 | 3311.6 | 3436.4
2013-02-11 | 20 | 2013-02-11 20:00 | 36875.0323 | 4766.1506 | 4393.6386 | 4394.0507 | 5510.2 | 5860.9 | 5420.1 | 5534.7 | 5777.7 | 4724.7 | 4903.3 | 4464.8 | 4640.4 | 4321.6 | 4429.8 | 4623 | 3619.8 | 3748.5
2013-02-11 | 21 | 2013-02-11 21:00 | 36180.3594 | 5411.0653 | 5125.2685 | 5128.8097 | 5859.6 | 6210.6 | 5842.2 | 5953.6 | 6205.3 | 5143 | 5330.4 | 4488.9 | 4645 | 4328 | 4451.4 | 4650.1 | 3639.8 | 3774
2013-02-11 | 22 | 2013-02-11 22:00 | 34728.1546 | 5248.6398 | 4932.2911 | 4934.3592 | 5867.2 | 6220.6 | 5876.2 | 5979.4 | 6246.1 | 5167.3 | 5371.5 | 4563.1 | 4730.6 | 4411.8 | 4531.2 | 4735.4 | 3718.5 | 3858.2
2013-02-11 | 23 | 2013-02-11 23:00 | 32115.6642 | 4475.0717 | 4066.7664 | 4067.2471 | 5582.3 | 5911.9 | 5605.6 | 5702.4 | 5943.3 | 4890.4 | 5072 | 3731 | 3856.3 | 3651.4 | 3728.3 | 3841.4 | 2919 | 2979.8
2013-02-11 | 24 | 2013-02-12 | 29530.0254 | 4050.3822 | 3701.3846 | 3705.7464 | 5261.9 | 5540.8 | 5301.9 | 5378.8 | 5568.2 | 4566.8 | 4706 | 3574.6 | 3678.5 | 3555.7 | 3594 | 3697.9 | 2781.9 | 2827.3
2013-02-12 | 1 | 2013-02-12 01:00 | 28003.6685 | 4218.9317 | 4007.7548 | 4007.7653 | 2868.6 | 3031.7 | 2693.7 | 2769.2 | 2902.3 | 1957.7 | 2038.1 | 3141.5 | 3242.6 | 3133.4 | 3174.2 | 3274 | 2363.6 | 2400.9
2013-02-12 | 2 | 2013-02-12 02:00 | 27232.602 | 3722.7519 | 3556.0291 | 3561.0299 | 2518.7 | 2634.4 | 2398.1 | 2475.4 | 2553.8 | 1666.3 | 1701.8 | 2897.2 | 2982.7 | 2923 | 2942.5 | 3013 | 2133.1 | 2149.2
2013-02-12 | 3 | 2013-02-12 03:00 | 26763.9437 | 2276.4562 | 2167.4082 | 2172.1019 | 2332.4 | 2439.2 | 2289.9 | 2353.8 | 2424.3 | 1549.2 | 1588.4 | 3216.8 | 3277.3 | 3212.3 | 3217.3 | 3263 | 2412.4 | 2425.8
2013-02-12 | 4 | 2013-02-12 04:00 | 26704.3768 | 1727.7466 | 1634.0379 | 1638.7876 | 2245.8 | 2340 | 2168.9 | 2211.7 | 2265.8 | 1414.2 | 1434.8 | 3214.3 | 3272.5 | 3240.2 | 3226.1 | 3268.3 | 2425.9 | 2432.6
2013-02-12 | 5 | 2013-02-12 05:00 | 27461.1978 | 1447.5059 | 1272.1275 | 1278.542 | 2420.7 | 2518.4 | 2290.8 | 2323.3 | 2381.5 | 1537.7 | 1565.9 | 3153 | 3259.6 | 3178.5 | 3178.6 | 3246.7 | 2385.5 | 2423.8
2013-02-12 | 6 | 2013-02-12 06:00 | 29893.3656 | 1367.5941 | 1190.9187 | 1195.5679 | 2467.8 | 2587.4 | 2366.6 | 2369.3 | 2447.3 | 1584.3 | 1635.2 | 2398.8 | 2520.6 | 2399.8 | 2436.2 | 2517.4 | 1646.2 | 1700.1
2013-02-12 | 7 | 2013-02-12 07:00 | 33924.7332 | 1278.9285 | 1145.1503 | 1172.1794 | 2536.1 | 2649.7 | 2457.8 | 2463.8 | 2527.8 | 1687.9 | 1726 | 2292.2 | 2445.1 | 2302.2 | 2349.7 | 2454.1 | 1545.7 | 1615.9
2013-02-12 | 8 | 2013-02-12 08:00 | 35146.9436 | 1284.8883 | 1180.8799 | 1215.8593 | 2921.4 | 3042.5 | 2850.9 | 2857.4 | 2933.2 | 2083.6 | 2132.6 | 2311.7 | 2449.7 | 2293.4 | 2343.3 | 2448 | 1546.2 | 1606.3
2013-02-12 | 9 | 2013-02-12 09:00 | 34539.0495 | 1218.371 | 1151.6455 | 1213.8852 | 4009.3 | 4144.8 | 3963.7 | 3961.2 | 4047.1 | 3165.7 | 3218.1 | 2676.1 | 2824.4 | 2645.6 | 2676.4 | 2769.1 | 1899.5 | 1946.5
2013-02-12 | 10 | 2013-02-12 10:00 | 34588.9481 | 1292.6715 | 1175.68 | 1247.9717 | 4758.8 | 4899.3 | 4718.7 | 4690.6 | 4777.5 | 3888.6 | 3937.1 | 2976.2 | 3124 | 2936.6 | 2988.9 | 3092.2 | 2196.9 | 2251.6
2013-02-12 | 11 | 2013-02-12 11:00 | 34595.9706 | 1951.3175 | 1792.3199 | 1990.1478 | 4738.6 | 4899.5 | 4752.6 | 4740.2 | 4845.2 | 3926.4 | 3991.8 | 3620.9 | 3781.5 | 3585.6 | 3622.6 | 3771.2 | 2825 | 2920.7
2013-02-12 | 12 | 2013-02-12 12:00 | 34308.2166 | 2886.6213 | 2680.4839 | 2860.2429 | 4820.8 | 5017.1 | 4857.5 | 4894.7 | 5033.9 | 4082.5 | 4166.8 | 3379.6 | 3534.7 | 3313.3 | 3356.2 | 3523 | 2571.3 | 2675.8
2013-02-12 | 13 | 2013-02-12 13:00 | 33985.7947 | 3446.1359 | 3275.9997 | 3431.3775 | 5163.8 | 5378.8 | 5189.4 | 5226.3 | 5384.6 | 4417.7 | 4518.8 | 3253.5 | 3403.7 | 3148 | 3196.6 | 3368.4 | 2414 | 2527.2
2013-02-12 | 14 | 2013-02-12 14:00 | 33822.6611 | 4053.0296 | 3901.1658 | 3930.1931 | 5480.9 | 5707.3 | 5482.1 | 5495.6 | 5664.3 | 4684.1 | 4795 | 3576.9 | 3747 | 3496.4 | 3559.9 | 3753.1 | 2758.4 | 2887
2013-02-12 | 15 | 2013-02-12 15:00 | 33444.8508 | 4524.2685 | 4339.6003 | 4364.6342 | 5485.2 | 5724.7 | 5478.4 | 5494.9 | 5670 | 4681.8 | 4798.5 | 4176.3 | 4352.9 | 4092.2 | 4163.5 | 4377.2 | 3352.2 | 3501.3
2013-02-12 | 16 | 2013-02-12 16:00 | 33324.5378 | 5508.8614 | 5272.8135 | 5362.7354 | 5515.7 | 5787.2 | 5527.6 | 5558.2 | 5770.7 | 4745.6 | 4896.9 | 4793.4 | 4991.8 | 4642.3 | 4742 | 4978.1 | 3930.2 | 4101.6
2013-02-12 | 17 | 2013-02-12 17:00 | 33595.7289 | 6426.3857 | 6160.2241 | 6265.2291 | 5325.8 | 5618.5 | 5372 | 5421.2 | 5656.7 | 4608.3 | 4779.6 | 5282.5 | 5489 | 5158.6 | 5246.5 | 5489.3 | 4435.9 | 4614.3
2013-02-12 | 18 | 2013-02-12 18:00 | 34235.3389 | 6755.507 | 6317.7065 | 6335.3967 | 5108.5 | 5422 | 5252.9 | 5307.8 | 5572.6 | 4496.1 | 4701.2 | 4770.2 | 4979.4 | 4555 | 4628.3 | 4750.9 | 3831.1 | 3900.9
2013-02-12 | 19 | 2013-02-12 19:00 | 35930.1337 | 5672.9844 | 5207.092 | 5218.2217 | 5074.7 | 5381.3 | 5075.2 | 5186.2 | 5456.2 | 4376.1 | 4588.4 | 4841 | 5065.4 | 4699 | 4825.6 | 5057.5 | 4015.1 | 4182.3
2013-02-12 | 20 | 2013-02-12 20:00 | 36579.0059 | 4949.6712 | 4449.3247 | 4459.9631 | 5048.4 | 5365.7 | 4990.1 | 5136.3 | 5419.8 | 4325.4 | 4544.3 | 4755.5 | 4976.7 | 4600 | 4749.5 | 5010.8 | 3939.3 | 4136.1
2013-02-12 | 21 | 2013-02-12 21:00 | 36084.0069 | 4135.1693 | 3696.7921 | 3708.3428 | 4895.7 | 5244.1 | 4801.3 | 4997.1 | 5325.4 | 4186.5 | 4450.2 | 4654.5 | 4859.9 | 4492.4 | 4633.6 | 4891.7 | 3824.1 | 4017.6
2013-02-12 | 22 | 2013-02-12 22:00 | 34749.6724 | 3061.7757 | 2692.3383 | 2714.3739 | 4615.4 | 4961.4 | 4474.9 | 4681.3 | 5011.9 | 3871.1 | 4136.9 | 3957.6 | 4107.5 | 3771.7 | 3920.6 | 4137.5 | 3112.7 | 3265.1
2013-02-12 | 23 | 2013-02-12 23:00 | 32592.1998 | 2109.8602 | 1700.5067 | 1708.8664 | 4363.9 | 4694.2 | 4220.7 | 4433 | 4739.1 | 3622.1 | 3863.7 | 3078.9 | 3249.5 | 2855.2 | 3021.9 | 3216.6 | 2228.9 | 2359
2013-02-12 | 24 | 2013-02-13 | 30337.9065 | 1955.9318 | 1527.9941 | 1521.6906 | 4035.8 | 4349.9 | 3842.5 | 4051.9 | 4347 | 3240.7 | 3471.1 | 2809.5 | 2950.3 | 2621.1 | 2780.2 | 2990.4 | 1978.4 | 2124.2
2013-02-13 | 1 | 2013-02-13 01:00 | 28940.133 | 1757.9701 | 1391.4941 | 1391.0778 | 3541.9 | 3833.3 | 3220.6 | 3422.4 | 3699.7 | 2614.2 | 2827.1 | 2718.1 | 2896.4 | 2430.7 | 2653 | 2937.1 | 1863.5 | 2083
2013-02-13 | 2 | 2013-02-13 02:00 | 28368.3497 | 1588.3323 | 1306.6096 | 1305.3673 | 3343 | 3671.6 | 3025.2 | 3258 | 3563.6 | 2451 | 2692.1 | 2376 | 2638.9 | 2077 | 2315.6 | 2629.9 | 1545.1 | 1794.7
2013-02-13 | 3 | 2013-02-13 03:00 | 28296.9761 | 1516.3181 | 1252.1952 | 1262.9451 | 3210 | 3550.6 | 2971.6 | 3154.5 | 3463.7 | 2354.3 | 2599 | 2319.8 | 2601.9 | 2032.3 | 2279.5 | 2603 | 1518.1 | 1777.1
2013-02-13 | 4 | 2013-02-13 04:00 | 28640.5477 | 1835.3283 | 1501.1816 | 1499.3768 | 3193.8 | 3579.4 | 2987.5 | 3193.5 | 3547.3 | 2399.3 | 2688.6 | 2165.4 | 2503.2 | 1860.1 | 2096.4 | 2424.2 | 1363.6 | 1626.8
2013-02-13 | 5 | 2013-02-13 05:00 | 29765.3254 | 2211.9402 | 1791.4864 | 1790.8056 | 3245.6 | 3654.9 | 3074.7 | 3273.7 | 3659.2 | 2475.4 | 2796.4 | 1992.5 | 2290 | 1727.3 | 1950.3 | 2266.4 | 1208.2 | 1459.7
2013-02-13 | 6 | 2013-02-13 06:00 | 32598.8151 | 2062.8338 | 1657.1762 | 1810.0427 | 3336 | 3728.6 | 3115.8 | 3325.9 | 3708 | 2523.4 | 2840.8 | 1960.3 | 2270.2 | 1712.6 | 1935.8 | 2257.9 | 1193.2 | 1450.8
2013-02-13 | 7 | 2013-02-13 07:00 | 37173.955 | 2098.7637 | 1626.5502 | 1641.9754 | 3345.4 | 3709.4 | 3102.5 | 3294.3 | 3644.8 | 2486.8 | 2772.8 | 2032.7 | 2397.2 | 1829.4 | 2015.3 | 2341.5 | 1254.7 | 1516.2
2013-02-13 | 8 | 2013-02-13 08:00 | 38483.3541 | 2084.1457 | 1659.5381 | 1667.5278 | 3139.6 | 3471.6 | 2907 | 3061.2 | 3379.3 | 2252.1 | 2505.6 | 2298.3 | 2666.3 | 2121.7 | 2281.6 | 2611.3 | 1510.5 | 1775.8
2013-02-13 | 9 | 2013-02-13 09:00 | 37438.1631 | 2118.2976 | 1769.8897 | 1774.269 | 2667.8 | 2943.8 | 2508.9 | 2636.1 | 2908.9 | 1827 | 2035.1 | 2227.2 | 2570.1 | 2042.9 | 2206.5 | 2500.9 | 1446 | 1679.3
2013-02-13 | 10 | 2013-02-13 10:00 | 36683.4389 | 1587.6603 | 1365.1133 | 1375.3166 | 1882.6 | 2071.6 | 1754.7 | 1851.5 | 2032.1 | 1057 | 1176.9 | 1745 | 2035.8 | 1606.3 | 1739.9 | 1933.1 | 993.1 | 1135.5
2013-02-13 | 11 | 2013-02-13 11:00 | 35816.1267 | 1080.4444 | 925.9873 | 941.1343 | 1596.3 | 1736 | 1481.2 | 1555.1 | 1684.2 | 775.7 | 854.8 | 1508.8 | 1743.1 | 1398 | 1512.8 | 1667.8 | 777.6 | 889.9
2013-02-13 | 12 | 2013-02-13 12:00 | 34562.3254 | 764.9882 | 651.1701 | 662.0608 | 1527.4 | 1620.9 | 1424.2 | 1478.6 | 1561.9 | 696.7 | 740.6 | 1445.5 | 1592.9 | 1361 | 1451.3 | 1569.7 | 722 | 802
2013-02-13 | 13 | 2013-02-13 13:00 | 33291.3139 | 843.9521 | 735.7287 | 741.2429 | 1484.6 | 1555.1 | 1404.1 | 1445.2 | 1500.9 | 659.1 | 677.3 | 1349.8 | 1467.3 | 1270.7 | 1348.8 | 1448.7 | 641.3 | 703.3
2013-02-13 | 14 | 2013-02-13 14:00 | 32521.3859 | 1002.5861 | 893.1832 | 894.6736 | 1439.8 | 1500.9 | 1362.6 | 1395.9 | 1441.4 | 603.2 | 608.8 | 1277.8 | 1395.8 | 1206 | 1276.7 | 1372.8 | 568.5 | 626.8
2013-02-13 | 15 | 2013-02-13 15:00 | 31829.4785 | 1136.001 | 1037.0024 | 1034.7716 | 1406.7 | 1467.3 | 1338.9 | 1372.4 | 1414.1 | 573.9 | 575 | 1158.1 | 1264.6 | 1087.3 | 1162 | 1257 | 441.7 | 495.6
2013-02-13 | 16 | 2013-02-13 16:00 | 31395.1765 | 1239.9679 | 1100.5512 | 1094.1527 | 1372 | 1431.7 | 1306.9 | 1345.8 | 1382.2 | 541.7 | 541.7 | 1086.2 | 1180 | 1038.6 | 1099.4 | 1180.7 | 395.4 | 437.1
2013-02-13 | 17 | 2013-02-13 17:00 | 31342.4713 | 1050.4317 | 919.7905 | 918.1502 | 1305.7 | 1360.5 | 1250.1 | 1281.1 | 1310.9 | 507.8 | 507.8 | 1120.2 | 1214 | 1057 | 1123.4 | 1203.4 | 422.5 | 465.5
2013-02-13 | 18 | 2013-02-13 18:00 | 31742.1177 | 701.5964 | 624.9653 | 623.9131 | 1134.4 | 1173 | 1079.7 | 1108.2 | 1130.9 | 406.4 | 406.4 | 974.4 | 1092.7 | 908.9 | 978.6 | 1065.4 | 318.1 | 364.2
2013-02-13 | 19 | 2013-02-13 19:00 | 34050.7314 | 427.8388 | 345.2337 | 349.9124 | 1125 | 1159.3 | 1065.7 | 1088.3 | 1111.6 | 400.3 | 400.3 | 1032.6 | 1151.9 | 957.6 | 1023.2 | 1108.1 | 323 | 357.3
2013-02-13 | 20 | 2013-02-13 20:00 | 35340.9745 | 408.4946 | 349.2161 | 357.6653 | 1249.4 | 1283.2 | 1194.9 | 1207.4 | 1227.9 | 492.5 | 492.5 | 1101.4 | 1186.3 | 1010.1 | 1092.2 | 1186.7 | 351.6 | 381.5
2013-02-13 | 21 | 2013-02-13 21:00 | 35477.7951 | 670.6386 | 607.2049 | 614.7697 | 1511.6 | 1555.9 | 1450.2 | 1462.3 | 1479.7 | 702.9 | 702.9 | 1372.6 | 1464.6 | 1271 | 1373.7 | 1483.9 | 588.4 | 634
2013-02-13 | 22 | 2013-02-13 22:00 | 34911.5243 | 1410.4663 | 1285.2412 | 1295.5468 | 1838.2 | 1891.4 | 1787.2 | 1806.5 | 1826.5 | 1010.8 | 1010.8 | 1544.1 | 1631.8 | 1401 | 1526 | 1641.3 | 713.7 | 764.3
2013-02-13 | 23 | 2013-02-13 23:00 | 33030.8316 | 2146.5021 | 1950.5506 | 1972.0748 | 2280.9 | 2335.1 | 2240 | 2255.5 | 2282.8 | 1443.5 | 1443.5 | 1909.6 | 2006 | 1758.3 | 1893.7 | 2018.1 | 1082.4 | 1142.3
2013-02-13 | 24 | 2013-02-14 | 30949.9191 | 2883.6451 | 2621.9188 | 2641.0848 | 2579.3 | 2650 | 2513.8 | 2537.2 | 2586.6 | 1716 | 1716.1 | 2187.7 | 2287.2 | 2048.6 | 2173.2 | 2288.9 | 1363.1 | 1414.1
2013-02-14 | 1 | 2013-02-14 01:00 | 29719.3152 | 3563.4173 | 3244.8725 | 3261.5354 | 2622.7 | 2753.8 | 2563.3 | 2661.8 | 2781 | 1852.8 | 1907.5 | 2830 | 2929.3 | 2686.6 | 2806.8 | 2910.5 | 2004 | 2043.4
2013-02-14 | 2 | 2013-02-14 02:00 | 29345.6752 | 4197.4654 | 3890.8889 | 3895.3741 | 2803.1 | 2912.6 | 2799.7 | 2875.9 | 2969.5 | 2070.9 | 2109.3 | 3011.8 | 3106.1 | 2921 | 3003.7 | 3094.8 | 2199.1 | 2228.2
2013-02-14 | 3 | 2013-02-14 03:00 | 29430.5643 | 4435.1711 | 4167.5919 | 4172.5843 | 2918.3 | 3004.5 | 2959.6 | 3002.4 | 3066.9 | 2198.7 | 2225.4 | 3113.2 | 3188.3 | 3074.1 | 3134.8 | 3210.1 | 2342.4 | 2362.4
2013-02-14 | 4 | 2013-02-14 04:00 | 29950.9871 | 4204.5014 | 3937.4109 | 3941.0091 | 3014.5 | 3094.1 | 3041.9 | 3075.9 | 3130.5 | 2278 | 2300.4 | 3543.2 | 3618.1 | 3532 | 3572.2 | 3636.3 | 2772.4 | 2788.9
2013-02-14 | 5 | 2013-02-14 05:00 | 31194.9983 | 3900.6948 | 3611.622 | 3615.8017 | 3063 | 3139.8 | 3100 | 3125.4 | 3179.7 | 2331 | 2352.8 | 3923.1 | 3998.7 | 3983.8 | 3993.5 | 4049.1 | 3182.1 | 3199.4
2013-02-14 | 6 | 2013-02-14 06:00 | 34308.6097 | 3721.9947 | 3463.8875 | 3468.5065 | 3001.6 | 3078 | 3064.4 | 3071.4 | 3124.3 | 2281.6 | 2301.2 | 3916.2 | 4000.5 | 4013.8 | 4026.1 | 4097.3 | 3229.3 | 3262.6
2013-02-14 | 7 | 2013-02-14 07:00 | 39172.0675 | 3576.6109 | 3362.0062 | 3366.7837 | 2773.3 | 2842.6 | 2852.4 | 2851.2 | 2895.4 | 2062.8 | 2070.5 | 3471.4 | 3552 | 3527.6 | 3559.4 | 3626.8 | 2758.1 | 2792
2013-02-14 | 8 | 2013-02-14 08:00 | 40021.0624 | 3626.8076 | 3439.1058 | 3441.9788 | 2328.3 | 2386.1 | 2382.7 | 2394.9 | 2428.9 | 1622.2 | 1622.2 | 3433.9 | 3519.2 | 3436.2 | 3477.7 | 3527.7 | 2696 | 2724.9
2013-02-14 | 9 | 2013-02-14 09:00 | 37869.54 | 3041.6629 | 2862.5734 | 2865.9594 | 1760.9 | 1803.4 | 1773.7 | 1788.2 | 1812.9 | 1048 | 1048 | 2587.5 | 2640.6 | 2571.4 | 2599.8 | 2631.3 | 1842.9 | 1852.2
2013-02-14 | 10 | 2013-02-14 10:00 | 36068.9113 | 2123.0728 | 2010.3817 | 2013.7941 | 1124.3 | 1152.7 | 1138 | 1137.5 | 1150.2 | 470.5 | 470.5 | 1764.4 | 1791.4 | 1757.4 | 1758.8 | 1773.5 | 1038 | 1038
2013-02-14 | 11 | 2013-02-14 11:00 | 34601.6335 | 1467.0586 | 1405.7828 | 1410.5017 | 823.5 | 847.4 | 822 | 819.8 | 830.2 | 196 | 196 | 1568.1 | 1594.9 | 1580 | 1579 | 1589.2 | 873.2 | 873.2
2013-02-14 | 12 | 2013-02-14 12:00 | 33294.9522 | 1036.688 | 971.3737 | 975.0945 | 745.2 | 770.6 | 727.5 | 726.2 | 740.2 | 119.8 | 119.8 | 1416.2 | 1443 | 1450.4 | 1435.9 | 1443.3 | 724.2 | 724.2
2013-02-14 | 13 | 2013-02-14 13:00 | 32211.9122 | 900.9949 | 849.9031 | 852.5165 | 778.8 | 811.3 | 748 | 752.1 | 773.2 | 128.8 | 132.2 | 1139.4 | 1166.5 | 1162.8 | 1150.8 | 1161.2 | 468 | 468
2013-02-14 | 14 | 2013-02-14 14:00 | 31746.0366 | 925.1738 | 874.7163 | 875.34 | 841.1 | 883.6 | 799.9 | 813.4 | 844.6 | 154.8 | 159.3 | 996.6 | 1032.9 | 1008.7 | 1016.4 | 1035.4 | 327.7 | 327.7
2013-02-14 | 15 | 2013-02-14 15:00 | 31285.4593 | 1231.005 | 1170.5941 | 1171.2675 | 869.6 | 919.3 | 817.4 | 839.7 | 880.1 | 154 | 157.6 | 920 | 972.9 | 900.6 | 929.9 | 968.1 | 213.3 | 215.2
2013-02-14 | 16 | 2013-02-14 16:00 | 30995.53 | 1321.4289 | 1243.7748 | 1248.1327 | 911.9 | 972.2 | 855.4 | 885 | 936.2 | 178.4 | 182 | 1086.5 | 1148.8 | 1055.9 | 1096.5 | 1149.8 | 366 | 381.7
2013-02-14 | 17 | 2013-02-14 17:00 | 30916.8104 | 1240.6987 | 1143.6363 | 1150.8172 | 898 | 971.1 | 831.3 | 870.2 | 935.2 | 170.6 | 184.2 | 1200 | 1290 | 1167.5 | 1227.1 | 1305.6 | 473.6 | 508
2013-02-14 | 18 | 2013-02-14 18:00 | 30998.6047 | 1095.9518 | 944.6091 | 956.3982 | 927.4 | 1020.6 | 848.2 | 894.3 | 982.3 | 199.1 | 227.6 | 1192.5 | 1305.3 | 1119.3 | 1202.8 | 1291.7 | 470.7 | 517.9
2013-02-14 | 19 | 2013-02-14 19:00 | 32738.1613 | 1019.5866 | 707.9012 | 721.668 | 1344.5 | 1468.6 | 1249.6 | 1306.9 | 1428.2 | 541.3 | 599.3 | 1258.1 | 1420.4 | 1108.4 | 1218.8 | 1338.4 | 544 | 601.7
2013-02-14 | 20 | 2013-02-14 20:00 | 33702.1774 | 1442.4551 | 948.666 | 983.0072 | 2170.5 | 2343 | 2050.6 | 2142.2 | 2307.7 | 1349.7 | 1451.3 | 1568.4 | 1756.4 | 1359.7 | 1503.4 | 1674.2 | 820.6 | 927
2013-02-14 | 21 | 2013-02-14 21:00 | 33391.2306 | 2327.725 | 1728.1646 | 1782.7711 | 2874.7 | 3107.7 | 2713.4 | 2861.1 | 3091.8 | 2053 | 2219.1 | 1764.1 | 2029.5 | 1515.8 | 1691.1 | 1955 | 1052.7 | 1252.1
2013-02-14 | 22 | 2013-02-14 22:00 | 32358.2306 | 3572.0348 | 2952.4671 | 2992.5231 | 3603.8 | 3875.9 | 3417.7 | 3604.3 | 3874.5 | 2790 | 2995.7 | 2659.8 | 2987.6 | 2428.1 | 2612.8 | 2947.6 | 1905.6 | 2175.7
2013-02-14 | 23 | 2013-02-14 23:00 | 30571.2384 | 5662.0275 | 5039.5475 | 5071.3992 | 4254.2 | 4559.4 | 4051.9 | 4247.1 | 4548.8 | 3427.7 | 3664.7 | 4374.6 | 4744.9 | 4152.2 | 4344.5 | 4710.7 | 3528.1 | 3829.7
2013-02-14 | 24 | 2013-02-15 | 28758.4232 | 7326.0618 | 6655.5282 | 6763.9255 | 4515.1 | 4814.3 | 4270.5 | 4472.1 | 4762.8 | 3651.9 | 3877.9 | 6065.9 | 6438.7 | 5822.2 | 6052.4 | 6417.6 | 5232.5 | 5533.1
2013-02-15 | 1 | 2013-02-15 01:00 | 27716.6481 | 7701.7421 | 7054.268 | 7120.2645 | 5336.7 | 5650.5 | 5165.8 | 5399.6 | 5716.3 | 4577.2 | 4829.4 | 6325.2 | 6651.8 | 6096.2 | 6320.5 | 6670.6 | 5502.3 | 5787.6
2013-02-15 | 2 | 2013-02-15 02:00 | 27316.5961 | 7765.8067 | 7144.3111 | 7254.0301 | 5407.5 | 5697.1 | 5292.5 | 5500.7 | 5786.5 | 4677.6 | 4898.9 | 6672.8 | 7003.9 | 6513.2 | 6700.1 | 7011.4 | 5877.8 | 6124.5
2013-02-15 | 3 | 2013-02-15 03:00 | 27299.8726 | 7577.9432 | 6993.7771 | 7297.1583 | 5360 | 5624.9 | 5309.4 | 5499.1 | 5733.6 | 4677.1 | 4847.1 | 7108.1 | 7390.3 | 6976.8 | 7141.5 | 7404.9 | 6319.3 | 6518
2013-02-15 | 4 | 2013-02-15 04:00 | 27599.5893 | 7401.6056 | 6912.9542 | 7148.526 | 5170.1 | 5395 | 5178.3 | 5343.1 | 5541.5 | 4520.8 | 4659.5 | 6901.7 | 7155.4 | 6797 | 6949.1 | 7175.8 | 6126.8 | 6290.6
2013-02-15 | 5 | 2013-02-15 05:00 | 28698.9501 | 7402.0204 | 6940.4631 | 7050.2235 | 4832.7 | 5038.4 | 4849.5 | 4995.9 | 5186 | 4177.5 | 4312.6 | 6687.6 | 6940.9 | 6556.7 | 6701.3 | 6922.4 | 5878.3 | 6039.2
2013-02-15 | 6 | 2013-02-15 06:00 | 31339.8481 | 7220.509 | 6761.0988 | 6783.8825 | 4467.9 | 4674 | 4479.7 | 4587.6 | 4784.6 | 3781.6 | 3930.5 | 6401.8 | 6634.2 | 6262.8 | 6408.8 | 6629.7 | 5585.6 | 5743
2013-02-15 | 7 | 2013-02-15 07:00 | 35752.0661 | 6573.1781 | 6152.262 | 6178.7079 | 4256.5 | 4462.4 | 4303.8 | 4377.1 | 4575.2 | 3585.1 | 3738.7 | 6043 | 6246.2 | 5913.7 | 6051.6 | 6257.6 | 5241.4 | 5384.2
2013-02-15 | 8 | 2013-02-15 08:00 | 36994.0056 | 5586.6517 | 5257.2387 | 5272.0194 | 3915 | 4093.3 | 3897.9 | 3970.8 | 4138.5 | 3188.6 | 3313.1 | 5657.7 | 5832.5 | 5574.3 | 5673.6 | 5844.5 | 4887.4 | 5001
2013-02-15 | 9 | 2013-02-15 09:00 | 36105.563 | 5222.336 | 4887.5141 | 4889.4267 | 3466.9 | 3623.9 | 3431.1 | 3491.4 | 3629.8 | 2712.5 | 2807.2 | 5406 | 5554 | 5335.7 | 5411.5 | 5565.7 | 4629.9 | 4731.6
2013-02-15 | 10 | 2013-02-15 10:00 | 35697.5908 | 4888.3953 | 4667.4611 | 4862.0257 | 3158.6 | 3278.9 | 3147.6 | 3200.6 | 3304.1 | 2428.6 | 2490.9 | 4719.4 | 4836.4 | 4667.7 | 4717.9 | 4835.3 | 3926.8 | 4000.4
2013-02-15 | 11 | 2013-02-15 11:00 | 35281.5195 | 4916.8299 | 4689.1653 | 4692.8741 | 2760.9 | 2852.5 | 2759.5 | 2797.9 | 2873.9 | 2010.6 | 2049.3 | 3912.4 | 4009.8 | 3860.3 | 3898.9 | 3987.2 | 3105.4 | 3150.5
2013-02-15 | 12 | 2013-02-15 12:00 | 34595.2234 | 4547.8499 | 4332.3045 | 4335.9795 | 2335.6 | 2414.8 | 2356.3 | 2384.3 | 2448.6 | 1589.5 | 1613.3 | 3538.8 | 3623.5 | 3538.9 | 3571.2 | 3639.8 | 2780.4 | 2808.7
2013-02-15 | 13 | 2013-02-15 13:00 | 34016.9684 | 3887.3937 | 3679.3005 | 3680.3236 | 1914.5 | 2001 | 1911.5 | 1952 | 2023.3 | 1152 | 1170 | 3059.2 | 3137.4 | 3056.6 | 3088.3 | 3150.4 | 2280.1 | 2298.2
2013-02-15 | 14 | 2013-02-15 14:00 | 33725.3415 | 3393.1936 | 3147.8623 | 3147.2237 | 1747 | 1860.1 | 1713.7 | 1776.3 | 1869.2 | 976.3 | 1012.5 | 2943 | 3035.6 | 2897.6 | 2947.4 | 3019.5 | 2140.2 | 2160.4
2013-02-15 | 15 | 2013-02-15 15:00 | 33315.187 | 3255.0134 | 2972.0069 | 2970.5136 | 1629.9 | 1767.2 | 1582.5 | 1656.2 | 1776.6 | 863.2 | 922.5 | 2680.2 | 2801.9 | 2611.7 | 2673.1 | 2773.3 | 1883.2 | 1931.1
2013-02-15 | 16 | 2013-02-15 16:00 | 32873.6963 | 3084.8976 | 2767.7885 | 2765.8875 | 1593.4 | 1761.9 | 1542.5 | 1615.4 | 1765.6 | 829.1 | 914.9 | 2489.7 | 2666.4 | 2366 | 2470.3 | 2646.5 | 1694 | 1814.7
2013-02-15 | 17 | 2013-02-15 17:00 | 32993.3205 | 2691.6254 | 2321.3228 | 2320.8212 | 1489.4 | 1677.6 | 1416.1 | 1498.8 | 1668.5 | 718.1 | 826.4 | 2167.7 | 2382 | 2025 | 2154.3 | 2342.7 | 1384.4 | 1521.6
2013-02-15 | 18 | 2013-02-15 18:00 | 33505.0257 | 2319.8873 | 1917.9525 | 1915.7153 | 1393.1 | 1606.7 | 1301.8 | 1384.5 | 1578.8 | 602.6 | 738.8 | 2176.9 | 2412.4 | 2019.6 | 2154.8 | 2366.8 | 1398.1 | 1561.6
2013-02-15 | 19 | 2013-02-15 19:00 | 35551.5662 | 1711.4822 | 1406.9586 | 1410.8339 | 1355.2 | 1562.8 | 1223.9 | 1327.6 | 1515.3 | 556.3 | 691.6 | 1876.6 | 2100.9 | 1684.6 | 1830.4 | 2053.9 | 1077.6 | 1252.8
2013-02-15 | 20 | 2013-02-15 20:00 | 36341.3697 | 1019.54 | 758.7973 | 772.0387 | 1356.9 | 1561.7 | 1182.6 | 1306.7 | 1495.4 | 547.2 | 689.1 | 1535.2 | 1707.5 | 1321 | 1452.9 | 1664 | 737.6 | 902.3
2013-02-15 | 21 | 2013-02-15 21:00 | 36056.8367 | 839.4932 | 612.2112 | 614.6768 | 1412.4 | 1627.4 | 1186.8 | 1338.8 | 1520.2 | 626.6 | 754.2 | 1382.1 | 1503.3 | 1207.8 | 1336 | 1515 | 654.5 | 789.9
2013-02-15 | 22 | 2013-02-15 22:00 | 35393.179 | 693.9149 | 505.7944 | 515.1826 | 1804.3 | 2020.8 | 1536.3 | 1698.1 | 1885.5 | 982.6 | 1114.3 | 1216.9 | 1389.3 | 1064.3 | 1171.2 | 1332.1 | 543.3 | 651.3
2013-02-15 | 23 | 2013-02-15 23:00 | 34165.6964 | 883.0098 | 687.9993 | 696.6451 | 1881 | 2119 | 1601.1 | 1778.9 | 2016.4 | 1066 | 1246.3 | 1232.3 | 1405 | 1062 | 1189.1 | 1341 | 655.3 | 752.5
2013-02-15 | 24 | 2013-02-16 | 32676.6919 | 1033.3393 | 765.7457 | 782.7557 | 1994.7 | 2262.3 | 1702 | 1884 | 2159.5 | 1166.4 | 1377.2 | 1367.9 | 1576.4 | 1192.9 | 1338.5 | 1519.1 | 764.6 | 882.3
2013-02-16 | 1 | 2013-02-16 01:00 | 31587.6639 | 1524.2007 | 1319.4801 | 1327.6259 | 2574.3 | 2955.3 | 2250.4 | 2476.7 | 2830.5 | 1668.8 | 1957.8 | 1678.3 | 1909.4 | 1462.5 | 1640.4 | 1862.6 | 976.3 | 1134
2013-02-16 | 2 | 2013-02-16 02:00 | 31187.8438 | 1719.0802 | 1467.2363 | 1488.2287 | 2978.8 | 3445.9 | 2684 | 2917.8 | 3347.3 | 2103.7 | 2468.8 | 2169.9 | 2492.5 | 1903.6 | 2148.6 | 2510.9 | 1380.9 | 1678.7
2013-02-16 | 3 | 2013-02-16 03:00 | 31122.0498 | 2131.2574 | 1711.3396 | 1735.13 | 3402.8 | 3869.4 | 3154.4 | 3367.3 | 3801.6 | 2555.8 | 2925.5 | 2753.7 | 3166.8 | 2511.3 | 2755.5 | 3154.3 | 1972 | 2306.1
2013-02-16 | 4 | 2013-02-16 04:00 | 31415.8092 | 2324.267 | 1838.174 | 1841.0841 | 3754.7 | 4202.1 | 3554.4 | 3751.1 | 4170.5 | 2934.4 | 3290.4 | 3178.3 | 3597.6 | 2966.3 | 3178.3 | 3559.4 | 2371.5 | 2689.1
2013-02-16 | 5 | 2013-02-16 05:00 | 32183.2725 | 2441.1862 | 2013.0008 | 2020.5365 | 3888.6 | 4269 | 3758.3 | 3914.2 | 4267.6 | 3095.7 | 3392.1 | 3023.8 | 3403.6 | 2856.7 | 3037.2 | 3332.5 | 2221.1 | 2456.8
2013-02-16 | 6 | 2013-02-16 06:00 | 33758.896 | 2313.9271 | 2045.413 | 2055.3555 | 3932.8 | 4243.3 | 3803 | 3960.3 | 4242.7 | 3142.1 | 3365.2 | 2703.5 | 3033 | 2566.5 | 2713.4 | 2916.2 | 1895.9 | 2042.1
2013-02-16 | 7 | 2013-02-16 07:00 | 35886.7318 | 2200.4394 | 2014.0702 | 2013.8155 | 3872.5 | 4119.8 | 3765.9 | 3900 | 4116.6 | 3082.5 | 3239.5 | 2579.9 | 2821.7 | 2463.3 | 2582.2 | 2750.9 | 1771.3 | 1882.9
2013-02-16 | 8 | 2013-02-16 08:00 | 37356.0896 | 2155.4055 | 1925.0133 | 1949.1717 | 3719 | 3889.5 | 3645.1 | 3734.8 | 3883 | 2917.6 | 3009.9 | 2749.4 | 2932.4 | 2644.8 | 2748.6 | 2895.9 | 1950.1 | 2040.4
2013-02-16 | 9 | 2013-02-16 09:00 | 37498.913 | 1533.1197 | 1474.4946 | 1478.5699 | 3238.5 | 3372.9 | 3202 | 3256.9 | 3372.9 | 2455.8 | 2526.9 | 2312 | 2434 | 2229.2 | 2310.8 | 2432.1 | 1534.8 | 1601.6
2013-02-16 | 10 | 2013-02-16 10:00 | 36655.9602 | 1136.414 | 1082.1379 | 1089.8344 | 2419.1 | 2527.7 | 2387.2 | 2431.1 | 2527.3 | 1675.5 | 1735.8 | 1575.2 | 1664.5 | 1476.4 | 1555.8 | 1644.5 | 798.3 | 839.7
2013-02-16 | 11 | 2013-02-16 11:00 | 35249.7728 | 1010.3252 | 879.0025 | 884.8487 | 2137.1 | 2217.9 | 2113.7 | 2144.4 | 2213.5 | 1403.3 | 1435.7 | 1266.7 | 1349.6 | 1126.7 | 1204.1 | 1286.2 | 463.7 | 507.5
2013-02-16 | 12 | 2013-02-16 12:00 | 33571.1095 | 946.3706 | 836.6482 | 829.8603 | 2185.2 | 2254.8 | 2169.1 | 2193.7 | 2252.6 | 1445 | 1466.1 | 1475.3 | 1559.3 | 1409.5 | 1464 | 1546.7 | 716.1 | 762.8
2013-02-16 | 13 | 2013-02-16 13:00 | 31934.8138 | 1413.4929 | 1310.9632 | 1303.0958 | 2465.3 | 2532.4 | 2474.8 | 2490.5 | 2547.2 | 1730.2 | 1739.1 | 1844.3 | 1946.2 | 1803.9 | 1851 | 1952 | 1101.6 | 1164.7
2013-02-16 | 14 | 2013-02-16 14:00 | 30478.8735 | 2274.6454 | 2185.5231 | 2186.0916 | 2834.4 | 2903.8 | 2839.8 | 2850.5 | 2911.3 | 2071.5 | 2081.5 | 2246.6 | 2346.6 | 2208.2 | 2250 | 2348.8 | 1499.7 | 1551.8
2013-02-16 | 15 | 2013-02-16 15:00 | 29355.7111 | 2271.7198 | 2181.4549 | 2181.815 | 3174.7 | 3247.1 | 3182.4 | 3191 | 3257.6 | 2419 | 2439.7 | 2251.7 | 2346.2 | 2208.6 | 2240.8 | 2333.8 | 1481.9 | 1525.4
2013-02-16 | 16 | 2013-02-16 16:00 | 28775.4657 | 1864.5854 | 1751.4569 | 1753.1611 | 3237.5 | 3309.3 | 3243 | 3244.9 | 3313.3 | 2471.7 | 2499.5 | 2240.7 | 2326.3 | 2204.3 | 2228.6 | 2312.2 | 1470.2 | 1502.3
2013-02-16 | 17 | 2013-02-16 17:00 | 28649.7183 | 1578.2412 | 1467.124 | 1472.7948 | 3092 | 3144.6 | 3094.3 | 3087.3 | 3137.9 | 2317.8 | 2333.4 | 2227 | 2290.9 | 2213.4 | 2222 | 2284.4 | 1478.9 | 1491.8
2013-02-16 | 18 | 2013-02-16 18:00 | 29087.0182 | 1180.4309 | 1089.3442 | 1090.138 | 2660.6 | 2701.7 | 2657.2 | 2649.2 | 2689.6 | 1875.8 | 1884.3 | 2010.3 | 2093.7 | 1983.8 | 2002.6 | 2085.9 | 1252.7 | 1282.3
2013-02-16 | 19 | 2013-02-16 19:00 | 31284.3561 | 1203.4056 | 1082.8569 | 1088.6555 | 3028.2 | 3111.2 | 2999.5 | 3011.7 | 3094.1 | 2231.1 | 2272.5 | 1949.1 | 2050 | 1919.7 | 1952.1 | 2058.4 | 1163.5 | 1205.4
2013-02-16 | 20 | 2013-02-16 20:00 | 32741.2139 | 1956.5049 | 1788.1461 | 1794.6028 | 3851.1 | 4023.7 | 3758.1 | 3821.7 | 3983 | 3026.2 | 3146.2 | 2673.4 | 2811.6 | 2592.5 | 2667.4 | 2811.1 | 1848.6 | 1927.7
2013-02-16 | 21 | 2013-02-16 21:00 | 32803.9687 | 2951.2689 | 2681.1775 | 2733.6371 | 4681.8 | 4925 | 4585.9 | 4681.2 | 4903.7 | 3883.3 | 4064.6 | 3548.2 | 3734.5 | 3417.2 | 3527.9 | 3722 | 2705.6 | 2835
2013-02-16 | 22 | 2013-02-16 22:00 | 32529.9463 | 4970.3833 | 4521.1937 | 4560.9609 | 5317.7 | 5613.1 | 5235.1 | 5349.4 | 5621.6 | 4549.4 | 4778.2 | 4264.5 | 4489 | 4101.2 | 4236.6 | 4469.1 | 3414.4 | 3582.3
2013-02-16 | 23 | 2013-02-16 23:00 | 31704.4308 | 6555.1862 | 5980.4306 | 6018.349 | 6012.3 | 6342.9 | 5940.2 | 6057.8 | 6366.2 | 5256.3 | 5522.5 | 5071.7 | 5307.1 | 4901.9 | 5045.2 | 5305.8 | 4223.5 | 4419.6
2013-02-16 | 24 | 2013-02-17 | 30677.3681 | 7252.4986 | 6615.1835 | 6789.6977 | 6507.6 | 6856.6 | 6437.2 | 6552.4 | 6880.6 | 5748.7 | 6031.9 | 5803.6 | 6084 | 5615.3 | 5804.5 | 6102.8 | 4982.5 | 5216.3
2013-02-17 | 1 | 2013-02-17 01:00 | 29719.8085 | 7596.3208 | 6920.3849 | 7095.8184 | 6120.4 | 6399.7 | 6093.2 | 6247.4 | 6521.5 | 5425.8 | 5635.4 | 6638.5 | 6965.1 | 6491.2 | 6673.1 | 7003.4 | 5850.2 | 6115.9
2013-02-17 | 2 | 2013-02-17 02:00 | 29238.6153 | 7777.534 | 7038.7146 | 7239.9584 | 6174.4 | 6457.3 | 6151.7 | 6312.1 | 6602.6 | 5489.2 | 5715.1 | 6896.5 | 7221.9 | 6845.9 | 7023.5 | 7340.7 | 6200.4 | 6453
2013-02-17 | 3 | 2013-02-17 03:00 | 29192.0492 | 7685.6746 | 7071.483 | 7117.6096 | 6221.4 | 6502.4 | 6170.7 | 6354.5 | 6648.1 | 5532.8 | 5761.9 | 6994.9 | 7315.2 | 6824.5 | 7010.3 | 7314 | 6187.8 | 6427
2013-02-17 | 4 | 2013-02-17 04:00 | 29332.4639 | 7544.2179 | 6915.503 | 6975.2749 | 6154.1 | 6429.3 | 6085.4 | 6286.3 | 6579.7 | 5465 | 5693.6 | 6935.7 | 7276.5 | 6752.7 | 6949.4 | 7264.3 | 6127.2 | 6377.7
2013-02-17 | 5 | 2013-02-17 05:00 | 29780.0143 | 7347.5466 | 6699.0963 | 6750.6474 | 6073.7 | 6357.9 | 5991 | 6207.8 | 6508.1 | 5386.7 | 5622.6 | 6862.2 | 7261.9 | 6642 | 6862.3 | 7204.1 | 6040 | 6317.3
2013-02-17 | 6 | 2013-02-17 06:00 | 30881.8671 | 7319.3199 | 6622.7004 | 6687.2426 | 6050.3 | 6334.7 | 5958.5 | 6173.8 | 6471.4 | 5352 | 5585 | 6808 | 7224.7 | 6589.5 | 6825.9 | 7205.1 | 6003 | 6317.7
2013-02-17 | 7 | 2013-02-17 07:00 | 32308.0205 | 7099.9567 | 6409.6761 | 6454.5937 | 5975.6 | 6261 | 5867.6 | 6087.4 | 6383.4 | 5267.3 | 5498.9 | 6743.4 | 7160.7 | 6508.2 | 6762.4 | 7164.4 | 5939.4 | 6276.8
2013-02-17 | 8 | 2013-02-17 08:00 | 33185.7725 | 7077.2147 | 6356.0833 | 6394.1653 | 5969.5 | 6277.3 | 5845.1 | 6071.2 | 6379.1 | 5250.7 | 5494.1 | 6654.7 | 7053.5 | 6395.3 | 6657.6 | 7045.9 | 5834.9 | 6158.7
2013-02-17 | 9 | 2013-02-17 09:00 | 33381.5473 | 6462.2046 | 5769.9897 | 5827.574 | 5582.8 | 5876 | 5457.9 | 5665.1 | 5936 | 4847 | 5053.3 | 6286.7 | 6627 | 6084.7 | 6288.8 | 6581.7 | 5468.6 | 5697.1
2013-02-17 | 10 | 2013-02-17 10:00 | 32558.0096 | 6005.0238 | 5285.4157 | 5304.1251 | 4801.8 | 5052.4 | 4654.1 | 4813.9 | 4991.2 | 4005.6 | 4118.4 | 5629.8 | 5912.3 | 5427.3 | 5622.8 | 5846.1 | 4801.4 | 4960.1
2013-02-17 | 11 | 2013-02-17 11:00 | 31306.6337 | 6844.4493 | 6036.5053 | 6049.4189 | 4777.1 | 5111.7 | 4546.5 | 4753.4 | 5011.3 | 3945.9 | 4143.1 | 5454.8 | 5835.4 | 5225.7 | 5442.9 | 5724.5 | 4621 | 4837.9
2013-02-17 | 12 | 2013-02-17 12:00 | 30230.5059 | 7616.4288 | 6812.1235 | 6819.2826 | 4945.6 | 5347.4 | 4678.9 | 4900.3 | 5224.8 | 4082.4 | 4342.4 | 5579.3 | 6007.3 | 5331.1 | 5575.1 | 5946.3 | 4752.3 | 5058.9
2013-02-17 | 13 | 2013-02-17 13:00 | 29453.6245 | 8016.6367 | 7148.6532 | 7162.6091 | 5298 | 5749.6 | 5012.2 | 5251.3 | 5640.6 | 4429.3 | 4754 | 5763.9 | 6246.2 | 5497.1 | 5764.1 | 6210.4 | 4943.6 | 5325.3
2013-02-17 | 14 | 2013-02-17 14:00 | 28801.8441 | 8243.9021 | 7376.026 | 7450.962 | 5606.3 | 6105.8 | 5304.7 | 5561.1 | 6002.7 | 4739.1 | 5116.1 | 6530.6 | 7053.4 | 6260.7 | 6543.8 | 7033.8 | 5724.5 | 6149.9
2013-02-17 | 15 | 2013-02-17 15:00 | 28416.4646 | 8501.9576 | 7698.8011 | 7866.4184 | 6067.4 | 6628.6 | 5782.9 | 6047.3 | 6549.5 | 5224.2 | 5661.8 | 7093.6 | 7686.3 | 6817 | 7110.5 | 7675.3 | 6291.2 | 6791.3
2013-02-17 | 16 | 2013-02-17 16:00 | 28201.2531 | 8556.0011 | 7748.2847 | 8224.1226 | 6483.4 | 7091.7 | 6204.6 | 6488.4 | 7040.2 | 5665.6 | 6152.8 | 7447.3 | 8067.6 | 7159.1 | 7458.9 | 8059.5 | 6638.1 | 7174.1
2013-02-17 | 17 | 2013-02-17 17:00 | 28356.0464 | 8619.891 | 7812.6639 | 8495.9815 | 6892.4 | 7512.1 | 6625.7 | 6917.9 | 7479.8 | 6095.7 | 6592.9 | 7819.5 | 8450 | 7525.3 | 7829.1 | 8454.2 | 7006.2 | 7566.6
2013-02-17 | 18 | 2013-02-17 18:00 | 29010.4021 | 8646.3259 | 7842.5115 | 8516.27 | 6925.5 | 7544.1 | 6628.8 | 6936.3 | 7498.7 | 6113.6 | 6611.6 | 7979.8 | 8612.9 | 7683.4 | 7991 | 8617.4 | 7168.1 | 7730
2013-02-17 | 19 | 2013-02-17 19:00 | 31086.6369 | 8834.3658 | 7909.824 | 8444.514 | 7532.9 | 8186 | 7254.2 | 7578.1 | 8165.2 | 6755.2 | 7277.8 | 8398.1 | 9050.8 | 8113.4 | 8423.6 | 9058.6 | 7601.2 | 8171.7
2013-02-17 | 20 | 2013-02-17 20:00 | 32262.4094 | 8924.5542 | 7964.7066 | 8654.1167 | 8394.8 | 9102.1 | 8149.1 | 8462.1 | 9092.1 | 7639.7 | 8205.2 | 9004.6 | 9673.3 | 8714.3 | 9022.6 | 9677.9 | 8200.5 | 8791.3
2013-02-17 | 21 | 2013-02-17 21:00 | 31758.3252 | 8892.201 | 7928.8113 | 8854.9324 | 8993.3 | 9741.5 | 8777.8 | 9090.5 | 9760 | 8271.5 | 8876.5 | 9236.9 | 9907 | 8950.2 | 9251.5 | 9905 | 8432.9 | 9021.8
2013-02-17 | 22 | 2013-02-17 22:00 | 30780.4405 | 8822.5491 | 7877.6064 | 8821.7247 | 9108 | 9869.4 | 8885.1 | 9195.5 | 9878.9 | 8377.1 | 8996 | 9236.7 | 9910.4 | 8931.1 | 9232.8 | 9898.3 | 8413.9 | 9014.7
2013-02-17 | 23 | 2013-02-17 23:00 | 29067.6502 | 8646.3904 | 7839.8171 | 8781.6405 | 9088.4 | 9839.5 | 8861.1 | 9171.8 | 9844.1 | 8353.5 | 8961.3 | 9263.8 | 9934.5 | 8969.8 | 9269.1 | 9922.8 | 8451.4 | 9040.4
2013-02-17 | 24 | 2013-02-18 | 27044.6443 | 8366.8503 | 7566.434 | 8789.1393 | 9047.3 | 9792.9 | 8812.8 | 9123.9 | 9797.2 | 8305.2 | 8914 | 9301.1 | 9970 | 9013.1 | 9310.9 | 9964.2 | 8492.6 | 9081.5
2013-02-18 | 1 | 2013-02-18 01:00 | 25594.286 | 7898.0762 | 7115.3729 | 8689.7058 | 8834.2 | 9573.9 | 8671.4 | 8971.1 | 9646.5 | 8149 | 8759.8 | 9115.2 | 9780.7 | 8918.1 | 9213.8 | 9869.5 | 8397.2 | 8988.2
2013-02-18 | 2 | 2013-02-18 02:00 | 24798.7281 | 7714.6842 | 6973.4784 | 8441.3586 | 8672.1 | 9395.3 | 8481 | 8786.4 | 9465.9 | 7965 | 8579.9 | 9032.3 | 9685.4 | 8817.7 | 9115.7 | 9766 | 8297 | 8882.7
2013-02-18 | 3 | 2013-02-18 03:00 | 24368.9297 | 7486.2231 | 6750.6862 | 8267.4805 | 8536.7 | 9271.6 | 8361.9 | 8663.5 | 9356.5 | 7844.1 | 8472.6 | 8937 | 9597.2 | 8760.9 | 9058.7 | 9695.8 | 8239.5 | 8812
2013-02-18 | 4 | 2013-02-18 04:00 | 24379.3003 | 7401.3823 | 6680.445 | 8145.3806 | 8480.3 | 9209.5 | 8307.6 | 8606.7 | 9296.5 | 7787.2 | 8412.2 | 8840.4 | 9500.3 | 8669.6 | 8969.2 | 9598.7 | 8150.3 | 8715.2
2013-02-18 | 5 | 2013-02-18 05:00 | 24927.7841 | 7597.4261 | 6893.5875 | 7847.7628 | 8357.8 | 9081.5 | 8186.3 | 8487 | 9164.4 | 7667.2 | 8280 | 8645.5 | 9282.5 | 8460.6 | 8762.6 | 9387.9 | 7943.5 | 8504.3
2013-02-18 | 6 | 2013-02-18 06:00 | 26829.7103 | 7830.2621 | 7094.0645 | 7521.1303 | 8056.7 | 8775.4 | 7880.2 | 8189.3 | 8860.3 | 7369.8 | 7976.2 | 8428 | 9063 | 8238.3 | 8547.1 | 9138.5 | 7727.9 | 8254.9
2013-02-18 | 7 | 2013-02-18 07:00 | 29899.2023 | 8002.7429 | 7200.363 | 7310.8371 | 7684.7 | 8380.3 | 7512.5 | 7827.9 | 8476.4 | 7008.6 | 7592.5 | 8012.2 | 8624.9 | 7836.8 | 8131.1 | 8678.5 | 7312.1 | 7794.8
2013-02-18 | 8 | 2013-02-18 08:00 | 31004.9298 | 7466.4781 | 6699.0735 | 6770.2892 | 7262.5 | 7927.4 | 7085.3 | 7399.1 | 8014.7 | 6576.2 | 7131.5 | 7435.6 | 8016.5 | 7245.7 | 7542.6 | 8056.9 | 6721.6 | 7171.3
2013-02-18 | 9 | 2013-02-18 09:00 | 31205.7907 | 6672.2745 | 5881.0016 | 5905.0886 | 6642.8 | 7321.2 | 6461.3 | 6783.4 | 7418.1 | 5961.2 | 6539.4 | 6683.8 | 7292.7 | 6452 | 6776.2 | 7340.7 | 5954.4 | 6454.2
2013-02-18 | 10 | 2013-02-18 10:00 | 31821.2031 | 6790.7512 | 5949.3125 | 5959.9638 | 6019.4 | 6694.7 | 5893.1 | 6174.6 | 6801.2 | 5352.4 | 5914.5 | 6205 | 6809.9 | 5956.2 | 6237.3 | 6792 | 5415.5 | 5905.6
2013-02-18 | 11 | 2013-02-18 11:00 | 32588.4224 | 8103.3872 | 7331.9526 | 7490.6021 | 5508.2 | 6189 | 5435.2 | 5661.3 | 6282.4 | 4839.1 | 5395.6 | 5681.9 | 6285.6 | 5489.4 | 5729.1 | 6282.4 | 4907.4 | 5396.2
2013-02-18 | 12 | 2013-02-18 12:00 | 32783.4435 | 7901.6125 | 7170.43 | 7177.4566 | 5136.9 | 5814.9 | 5048.4 | 5279.8 | 5884.1 | 4457.6 | 4997.2 | 4913.9 | 5515 | 4707.5 | 4967.7 | 5520 | 4146.6 | 4634.2
2013-02-18 | 13 | 2013-02-18 13:00 | 32790.1194 | 7575.4491 | 6833.5769 | 6835.884 | 4664.2 | 5311.7 | 4550 | 4796.9 | 5345.1 | 3974.5 | 4458.1 | 4854.4 | 5439.5 | 4596.1 | 4868.8 | 5400.2 | 4048 | 4514.8
2013-02-18 | 14 | 2013-02-18 14:00 | 32957.6843 | 7153.8299 | 6393.9472 | 6396.1312 | 4623.3 | 5208.8 | 4536.5 | 4750.9 | 5192.5 | 3928.8 | 4305.8 | 5445.5 | 5984.1 | 5212 | 5443.6 | 5902.4 | 4623.4 | 5017.7
2013-02-18 | 15 | 2013-02-18 15:00 | 32885.1656 | 7046.9017 | 6264.7856 | 6267.6222 | 4625.4 | 5168.4 | 4567.6 | 4745.2 | 5113.8 | 3923.8 | 4227.7 | 5423.6 | 5931.6 | 5194.2 | 5412 | 5838.9 | 4591 | 4953.2
2013-02-18 | 16 | 2013-02-18 16:00 | 32735.3588 | 6571.6524 | 5809.1299 | 5813.2331 | 4342.1 | 4834.4 | 4290.5 | 4445 | 4755.1 | 3623.8 | 3869.5 | 5101.9 | 5566.4 | 4930.3 | 5098.4 | 5449.3 | 4277.2 | 4563.5
2013-02-18 | 17 | 2013-02-18 17:00 | 32713.114 | 6037.9828 | 5325.4419 | 5331.9867 | 3892.6 | 4336.5 | 3840.6 | 3977.8 | 4241.2 | 3157 | 3355.8 | 4493.4 | 4917.9 | 4317.5 | 4472.6 | 4794.5 | 3651.8 | 3909.1
2013-02-18 | 18 | 2013-02-18 18:00 | 32702.1604 | 5204.5098 | 4498.7355 | 4504.1721 | 3305.4 | 3675.3 | 3259.8 | 3369.1 | 3566.7 | 2547.8 | 2680.8 | 3999.1 | 4367.7 | 3865.2 | 3985.3 | 4263.6 | 3163.9 | 3377.6
2013-02-18 | 19 | 2013-02-18 19:00 | 34080.938 | 4068.3941 | 3453.4091 | 3457.8739 | 3149.9 | 3467.1 | 3139.8 | 3202.4 | 3348.5 | 2382.3 | 2464 | 3451.8 | 3770.7 | 3356.2 | 3441.9 | 3680.7 | 2620.9 | 2795
2013-02-18 | 20 | 2013-02-18 20:00 | 34902.3306 | 4289.9635 | 3708.352 | 3704.8486 | 3304.6 | 3612.9 | 3310 | 3367 | 3535.7 | 2547.1 | 2651.1 | 3293.5 | 3605.1 | 3179 | 3276.8 | 3505.4 | 2457.2 | 2621.2
2013-02-18 | 21 | 2013-02-18 21:00 | 34095.7725 | 4729.3381 | 4209.8467 | 4211.972 | 3380.9 | 3688.4 | 3335 | 3421.5 | 3620.2 | 2607.8 | 2741.8 | 3439.2 | 3719.5 | 3290.3 | 3395.7 | 3613.3 | 2576 | 2728.9
2013-02-18 | 22 | 2013-02-18 22:00 | 32626.8551 | 4293.3646 | 3817.7359 | 3819.934 | 3441.1 | 3728.5 | 3387.4 | 3462 | 3644.9 | 2643 | 2761.2 | 3423 | 3676.7 | 3279.3 | 3367.9 | 3585.9 | 2547.8 | 2701.5
2013-02-18 | 23 | 2013-02-18 23:00 | 30044.2953 | 4024.5416 | 3562.6678 | 3577.7466 | 3477.6 | 3762.7 | 3432.1 | 3474.2 | 3647.3 | 2654.8 | 2763.5 | 3645.3 | 3860.1 | 3514.5 | 3583.2 | 3797.7 | 2762.8 | 2912.5
2013-02-18 | 24 | 2013-02-19 | 27488.1479 | 3876.3938 | 3430.9532 | 3444.7385 | 3578.5 | 3838.2 | 3552.7 | 3596.3 | 3749.6 | 2776.3 | 2866.9 | 3932.9 | 4107.5 | 3821.9 | 3878.1 | 4078.3 | 3058.8 | 3194.4
2013-02-19 | 1 | 2013-02-19 01:00 | 25861.7462 | 3815.8987 | 3449.2382 | 3473.7049 | 3996 | 4158.5 | 3905.3 | 4036.8 | 4174.3 | 3215.9 | 3299.9 | 4077.1 | 4228.3 | 3925.7 | 4037.6 | 4237.5 | 3218 | 3353.4
2013-02-19 | 2 | 2013-02-19 02:00 | 25186.199 | 3611.7334 | 3262.5396 | 3274.5007 | 3986.1 | 4141 | 3893.3 | 4017.1 | 4151.3 | 3196.9 | 3274.6 | 3844.9 | 3980.6 | 3703.4 | 3810.2 | 3989.7 | 2990.1 | 3104.9
2013-02-19 | 3 | 2013-02-19 03:00 | 25002.1626 | 3446.9429 | 3208.1936 | 3214.8353 | 4224.5 | 4369 | 4178.3 | 4254.2 | 4375.4 | 3433 | 3504.7 | 3975 | 4098.8 | 3882.4 | 3971.3 | 4113.7 | 3150.1 | 3227.9
2013-02-19 | 4 | 2013-02-19 04:00 | 25325.1075 | 3039.7466 | 2827.0254 | 2843.3802 | 4441.2 | 4606.4 | 4358 | 4461.4 | 4574.2 | 3640.9 | 3716 | 3931.1 | 4085.3 | 3782.9 | 3908 | 4087.8 | 3086.4 | 3201.5
2013-02-19 | 5 | 2013-02-19 05:00 | 26403.545 | 2469.9492 | 2198.7018 | 2228.7818 | 4663.5 | 4971.8 | 4525.5 | 4685.9 | 4968.7 | 3865.6 | 4083.9 | 3831 | 3997.8 | 3711.9 | 3824.9 | 3994.9 | 3003.1 | 3108.6
2013-02-19 | 6 | 2013-02-19 06:00 | 29295.9879 | 2740.5267 | 2448.4099 | 2449.4288 | 4815.6 | 5169.6 | 4642.4 | 4843.2 | 5171.1 | 4021.9 | 4285.2 | 3935.6 | 4056.3 | 3869.2 | 3934.4 | 4004 | 3112 | 3144.4
2013-02-19 | 7 | 2013-02-19 07:00 | 34106.3113 | 3028.8258 | 2817.3762 | 2813.3738 | 4904.6 | 5271.7 | 4685.5 | 4914.6 | 5254.6 | 4093.1 | 4368.6 | 3843 | 3968.3 | 3707.8 | 3851.2 | 3977.9 | 3030.3 | 3095.7
2013-02-19 | 8 | 2013-02-19 08:00 | 35396.8493 | 3740.1657 | 3437.8219 | 3428.5304 | 5120.4 | 5551.3 | 4877.4 | 5125.4 | 5524.2 | 4304.2 | 4638.4 | 3596.1 | 3774.8 | 3348.1 | 3591.4 | 3801.8 | 2771.5 | 2918.4
2013-02-19 | 9 | 2013-02-19 09:00 | 34385.5759 | 4166.914 | 3809.4664 | 3858.499 | 4616.4 | 5069.1 | 4400.6 | 4661.8 | 5067.5 | 3840.7 | 4181.9 | 3753.1 | 4011.4 | 3525.8 | 3757.1 | 4025.3 | 2937.1 | 3140.6
2013-02-19 | 10 | 2013-02-19 10:00 | 33711.9914 | 4758.7567 | 4403.2955 | 4501.6726 | 4344 | 4727.6 | 4189.1 | 4408.5 | 4738.6 | 3587 | 3852.7 | 3637.2 | 3842 | 3439 | 3653.4 | 3901.4 | 2834.3 | 3021
2013-02-19 | 11 | 2013-02-19 11:00 | 33302.0397 | 4791.6613 | 4368.5004 | 4425.6308 | 4464.4 | 4838.5 | 4358 | 4552.1 | 4867.4 | 3731.9 | 3982.6 | 3891.8 | 4197.1 | 3741.8 | 3912.3 | 4141.1 | 3094.6 | 3261.8
2013-02-19 | 12 | 2013-02-19 12:00 | 32769.8065 | 4815.5727 | 4319.5523 | 4332.0768 | 4574 | 4936.5 | 4501.1 | 4666.9 | 4968.4 | 3847 | 4083.8 | 4095.4 | 4438.2 | 3972.8 | 4127.3 | 4349.5 | 3307 | 3465.4
2013-02-19 | 13 | 2013-02-19 13:00 | 32336.2006 | 5082.308 | 4551.3666 | 4548.7785 | 4684.6 | 5031.7 | 4627.9 | 4778.7 | 5065.8 | 3959.1 | 4181.5 | 4660.5 | 4982.2 | 4523.5 | 4694.9 | 4950.4 | 3874.4 | 4065.5
2013-02-19 | 14 | 2013-02-19 14:00 | 32092.776 | 5737.526 | 5195.9658 | 5223.1337 | 4888.1 | 5232.2 | 4817 | 4963.7 | 5252.4 | 4143.4 | 4367.5 | 4901.4 | 5225.8 | 4737.9 | 4909.2 | 5180.4 | 4088.8 | 4295.5
2013-02-19 | 15 | 2013-02-19 15:00 | 31851.3386 | 6639.3703 | 6017.5089 | 6052.3471 | 5385.5 | 5748.1 | 5313.7 | 5464.2 | 5773.1 | 4643.9 | 4888.2 | 5244.1 | 5643.1 | 5053.3 | 5251.3 | 5594.2 | 4429 | 4707.2
2013-02-19 | 16 | 2013-02-19 16:00 | 31668.0608 | 7107.1406 | 6401.5728 | 6481.7917 | 5825.4 | 6216.3 | 5738.8 | 5897.1 | 6231.3 | 5076.9 | 5346.5 | 5872.9 | 6317.9 | 5684.3 | 5894.1 | 6289.3 | 5071.7 | 5402.3
2013-02-19 | 17 | 2013-02-19 17:00 | 31699.3689 | 7358.0177 | 6601.6208 | 6711.3512 | 6050.5 | 6455.1 | 5970.9 | 6125 | 6466.6 | 5303.6 | 5580.6 | 6143.1 | 6604.8 | 5919.4 | 6146.6 | 6585.3 | 5325.3 | 5699.3
2013-02-19 | 18 | 2013-02-19 18:00 | 32141.1763 | 7095.1238 | 6290.2647 | 6353.0575 | 6071.8 | 6446.1 | 5974.2 | 6136.2 | 6447.3 | 5313.7 | 5560.3 | 6362 | 6846.1 | 6147.5 | 6371.6 | 6841.1 | 5550.3 | 5955.3
2013-02-19 | 19 | 2013-02-19 19:00 | 34338.7496 | 6365.548 | 5652.1064 | 5693.4923 | 6283.3 | 6673.5 | 6186.3 | 6348 | 6677.5 | 5525.2 | 5790.2 | 6520 | 7005.3 | 6280.1 | 6511.5 | 6978.1 | 5690.9 | 6092.9
2013-02-19 | 20 | 2013-02-19 20:00 | 35110.6184 | 5953.3293 | 5243.3575 | 5269.4588 | 7100.6 | 7550.4 | 6972.1 | 7165 | 7552.4 | 6342.5 | 6665.3 | 6503.8 | 7014.2 | 6238.7 | 6501.8 | 6983.6 | 5680.7 | 6098
2013-02-19 | 21 | 2013-02-19 21:00 | 34599.7983 | 5500.4099 | 4721.4592 | 4761.4502 | 7787.2 | 8311.3 | 7636.6 | 7865.2 | 8315.5 | 7042.8 | 7428.6 | 6686.9 | 7153.7 | 6392.8 | 6671.1 | 7165 | 5849.2 | 6278.6
2013-02-19 | 22 | 2013-02-19 22:00 | 33120.9712 | 4553.8476 | 3913.3323 | 3910.3516 | 7920.5 | 8492.1 | 7763.3 | 7992.3 | 8495 | 7169.2 | 7607.3 | 6665.7 | 7151.9 | 6364.5 | 6642.9 | 7158.6 | 5821.2 | 6272.3
2013-02-19 | 23 | 2013-02-19 23:00 | 30687.1983 | 4406.6503 | 3800.8269 | 3828.025 | 7822.4 | 8398.6 | 7657.3 | 7897.7 | 8407.3 | 7075.4 | 7520.4 | 6374.9 | 6842 | 6075.8 | 6336.7 | 6840.6 | 5515.4 | 5954.8
2013-02-19 | 24 | 2013-02-20 | 28325.0079 | 4273.8648 | 3573.3304 | 3599.9286 | 7893.8 | 8426.2 | 7725.6 | 7970.7 | 8433 | 7148.2 | 7546.1 | 6319.5 | 6726.1 | 6124.3 | 6332.4 | 6753.9 | 5510.8 | 5867.7
2013-02-20 | 1 | 2013-02-20 01:00 | 26717.1896 | 4398.7366 | 3714.0795 | 3723.1465 | 6197.8 | 6663.2 | 6090.3 | 6273.1 | 6711.9 | 5451.9 | 5826.1 | 6295.9 | 6658.4 | 6083.6 | 6256.2 | 6628.8 | 5435.8 | 5743.7
2013-02-20 | 2 | 2013-02-20 02:00 | 25973.9311 | 4842.865 | 4222.3767 | 4221.6748 | 6150.3 | 6598.3 | 6035.4 | 6234.7 | 6660.9 | 5413.4 | 5775.1 | 6036.1 | 6327.9 | 5824.5 | 5984 | 6294.6 | 5164.7 | 5410.6
2013-02-20 | 3 | 2013-02-20 03:00 | 25816.0121 | 4162.9823 | 3667.1809 | 3646.6247 | 5994.1 | 6434.7 | 5907.1 | 6092.6 | 6507.5 | 5271.8 | 5622.1 | 5602 | 5932.8 | 5363 | 5565 | 5914.2 | 4744.7 | 5029.3
2013-02-20 | 4 | 2013-02-20 04:00 | 25973.5318 | 2883.608 | 2374.5748 | 2400.3887 | 5588.2 | 6046.6 | 5394.3 | 5616.3 | 6025.8 | 4795.6 | 5140.5 | 5265.1 | 5642.3 | 5007.5 | 5225.8 | 5612.8 | 4405.6 | 4728
2013-02-20 | 5 | 2013-02-20 05:00 | 26807.8435 | 3571.2634 | 3041.4423 | 3141.8009 | 6048.8 | 6529.7 | 5767.7 | 6024.1 | 6461.2 | 5204.4 | 5576.9 | 5763.6 | 6126.1 | 5550.7 | 5758.2 | 6126.2 | 4937.6 | 5241.1
2013-02-20 | 6 | 2013-02-20 06:00 | 29534.7975 | 4399.2439 | 3894.0937 | 3996.7522 | 6130.1 | 6679.9 | 5854.8 | 6118.6 | 6630 | 5298.9 | 5745.6 | 5701 | 6114 | 5512.4 | 5733.3 | 6139 | 4913.7 | 5254.8
2013-02-20 | 7 | 2013-02-20 07:00 | 33907.6443 | 4773.0056 | 4213.6493 | 4303.9579 | 6546.7 | 7067.2 | 6293.4 | 6543.7 | 7025 | 5722.9 | 6139.5 | 5220.4 | 5687.6 | 4980.6 | 5231 | 5679.4 | 4410.6 | 4794.2
2013-02-20 | 8 | 2013-02-20 08:00 | 35281.5515 | 5278.034 | 4502.2955 | 4577.2642 | 6671.5 | 7200 | 6480.5 | 6719.8 | 7210.2 | 5899.5 | 6325.3 | 5496.7 | 5964.2 | 5199.7 | 5470 | 5915.6 | 4648.8 | 5029.9
2013-02-20 | 9 | 2013-02-20 09:00 | 35008.3751 | 5565.8641 | 4741.9265 | 4887.3293 | 6673.1 | 7298.3 | 6387.1 | 6699.8 | 7282.2 | 5878.6 | 6396.5 | 5934.6 | 6443.5 | 5660.7 | 5962.8 | 6452.7 | 5141.2 | 5566.5
2013-02-20 | 10 | 2013-02-20 10:00 | 35154.0403 | 5846.8373 | 4967.7603 | 5106.3904 | 6559.5 | 7235.7 | 6276.3 | 6598.2 | 7228.1 | 5775.7 | 6341 | 6072.8 | 6671.9 | 5767 | 6105.6 | 6670.1 | 5283.2 | 5783.2
2013-02-20 | 11 | 2013-02-20 11:00 | 35417.157 | 6034.1886 | 5243.1127 | 5397.0226 | 6460.5 | 7140.5 | 6184.4 | 6510.3 | 7138.3 | 5687.8 | 6251.3 | 5619.7 | 6252 | 5321.1 | 5647.7 | 6256.7 | 4825 | 5369.4
2013-02-20 | 12 | 2013-02-20 12:00 | 35534.6348 | 6373.0342 | 5595.7755 | 5650.7264 | 6335.8 | 7008.5 | 6061.2 | 6381.6 | 7006.1 | 5558.8 | 6118.6 | 5606.6 | 6240.9 | 5350.7 | 5669.7 | 6280.1 | 4847.4 | 5393.2
2013-02-20 | 13 | 2013-02-20 13:00 | 35539.5403 | 6005.2669 | 5180.0931 | 5299.5041 | 6120.6 | 6795 | 5836.1 | 6148.6 | 6777.1 | 5326 | 5890.1 | 5793.9 | 6433.3 | 5427.2 | 5755.5 | 6379.5 | 4933 | 5492.4
2013-02-20 | 14 | 2013-02-20 14:00 | 35488.2697 | 5989.3295 | 5154.4167 | 5288.4173 | 5903.3 | 6558.7 | 5624.2 | 5921.6 | 6534.7 | 5099.5 | 5647.9 | 5744.7 | 6389.4 | 5487.3 | 5809 | 6440.5 | 4987.3 | 5554.3
2013-02-20 | 15 | 2013-02-20 15:00 | 35182.9421 | 6227.8899 | 5345.2594 | 5472.5192 | 5802.1 | 6446.3 | 5514.9 | 5810.4 | 6412.3 | 4987.8 | 5525.2 | 5964.3 | 6612.6 | 5718.9 | 6023.9 | 6663.2 | 5201.1 | 5775.8
2013-02-20 | 16 | 2013-02-20 16:00 | 35380.9284 | 6320.9651 | 5420.2328 | 5570.222 | 5895.8 | 6539.6 | 5623.1 | 5912.2 | 6510.3 | 5089.8 | 5623.3 | 5944.2 | 6589.3 | 5672.8 | 5989.4 | 6621.5 | 5166.6 | 5733.9
2013-02-20 | 17 | 2013-02-20 17:00 | 36019.0629 | 6471.0914 | 5553.4923 | 5718.5769 | 6154.3 | 6817.9 | 5896.6 | 6195.7 | 6805.4 | 5373.5 | 5918.8 | 6282.2 | 6935.9 | 5973.1 | 6307.5 | 6945.2 | 5485 | 6058.1
2013-02-20 | 18 | 2013-02-20 18:00 | 37088.6148 | 6984.3822 | 6040.1539 | 6252.5788 | 6238.6 | 6912.7 | 5972.5 | 6283.4 | 6916.7 | 5461.2 | 6030 | 6796.4 | 7457.1 | 6492.2 | 6829.7 | 7475.4 | 6007.7 | 6588.9
2013-02-20 | 19 | 2013-02-20 19:00 | 38709.4232 | 7645.0145 | 6703.7556 | 6878.8159 | 6689.3 | 7378.1 | 6433.4 | 6745 | 7384.3 | 5923 | 6497.7 | 7467.5 | 8134 | 7167.9 | 7506.5 | 8156.6 | 6684.4 | 7270
2013-02-20 | 20 | 2013-02-20 20:00 | 38924.051 | 8229.7549 | 7302.5007 | 7487.1595 | 7321.2 | 8052.2 | 7081.1 | 7409.5 | 8076.8 | 6587.7 | 7190.4 | 7816.3 | 8502 | 7493.3 | 7834.8 | 8515.3 | 7012.6 | 7628.5
2013-02-20 | 21 | 2013-02-20 21:00 | 38172.5693 | 8358.4323 | 7427.0938 | 7611.1501 | 7710.5 | 8465.1 | 7410.8 | 7744.8 | 8438.3 | 6922.3 | 7551.1 | 7963.1 | 8660.1 | 7638.7 | 7978.8 | 8676.7 | 7157.5 | 7790.7
2013-02-20 | 22 | 2013-02-20 22:00 | 36577.3348 | 8259.9768 | 7333.8789 | 7482.5307 | 7471 | 8231.5 | 6996.7 | 7462.6 | 8180.5 | 6639.7 | 7293 | 7988.7 | 8689.2 | 7546.7 | 8019.2 | 8731.4 | 7200.4 | 7848.1
2013-02-20 | 23 | 2013-02-20 23:00 | 33767.8204 | 7914.4337 | 7000.0313 | 7096.4499 | 7142.2 | 7902.4 | 6837.6 | 7145.1 | 7855.2 | 6325.6 | 6971.1 | 7658.9 | 8341.2 | 7317.2 | 7655.9 | 8364.2 | 6832.8 | 7476.7
2013-02-20 | 24 | 2013-02-21 | 31092.9661 | 6782.7203 | 5848.9884 | 6002.1847 | 7401.4 | 8117.4 | 7115.3 | 7421.8 | 8080.1 | 6608 | 7201.7 | 7287.3 | 7970.6 | 6959.9 | 7288.1 | 7997.5 | 6467 | 7111.7
2013-02-21 | 1 | 2013-02-21 01:00 | 29313.1466 | 6226.2477 | 5352.4172 | 5406.359 | 7484.9 | 8155.6 | 7171.5 | 7483.1 | 8126.8 | 6663.3 | 7242.5 | 6524.2 | 7178.7 | 6214.3 | 6558.2 | 7213.8 | 5735.5 | 6326.4
2013-02-21 | 2 | 2013-02-21 02:00 | 28339.8329 | 5182.0482 | 4329.5872 | 4491.3533 | 7313 | 7967.5 | 7032.2 | 7331.9 | 7942.3 | 6509.9 | 7055.8 | 6761.7 | 7358.8 | 6497.3 | 6820.2 | 7395.2 | 5998.5 | 6509.1
2013-02-21 | 3 | 2013-02-21 03:00 | 27689.9018 | 5219.3342 | 4439.5693 | 4533.5548 | 7081.4 | 7658.5 | 6769.6 | 7067.2 | 7598.5 | 6244.5 | 6714.5 | 6591.7 | 7161.3 | 6304.4 | 6617.8 | 7158.9 | 5795.9 | 6272.5
2013-02-21 | 4 | 2013-02-21 04:00 | 27664.144 | 6059.7391 | 5205.6182 | 5272.3711 | 7255.7 | 7830.7 | 6975.7 | 7243.2 | 7770.7 | 6420.2 | 6883.9 | 6541.9 | 7110.1 | 6281.6 | 6564.6 | 7112.3 | 5743.2 | 6226.5
2013-02-21 | 5 | 2013-02-21 05:00 | 28306.0981 | 4902.9178 | 4149.5597 | 4235.0528 | 7365 | 7966.7 | 7133 | 7358.9 | 7911.9 | 6536.6 | 7025 | 6375.4 | 6922.5 | 6128.3 | 6404.7 | 6941.1 | 5583.6 | 6055.3
2013-02-21 | 6 | 2013-02-21 06:00 | 30619.6675 | 3860.1232 | 3252.6393 | 3352.565 | 7575 | 8180 | 7404.8 | 7609.5 | 8151 | 6787.2 | 7264.1 | 7254.6 | 7723.2 | 7048.1 | 7234.5 | 7678.5 | 6411.7 | 6791.2
2013-02-21 | 7 | 2013-02-21 07:00 | 34428.0421 | 4006.3197 | 3506.8324 | 3499.997 | 7879 | 8444.5 | 7708.5 | 7883.1 | 8327.2 | 7060.7 | 7440.2 | 7695.2 | 8109.5 | 7567.2 | 7698.4 | 8046.7 | 6876.3 | 7159.9
2013-02-21 | 8 | 2013-02-21 08:00 | 35483.7664 | 5374.0782 | 4849.9013 | 4861.6068 | 7901 | 8426.1 | 7716.1 | 7901 | 8254.5 | 7078.3 | 7372.4 | 7473.7 | 7848.4 | 7354.5 | 7466.8 | 7757.9 | 6643.7 | 6870.3
2013-02-21 | 9 | 2013-02-21 09:00 | 35003.0821 | 6211.0013 | 5739.7254 | 5806.7324 | 8110.7 | 8681.6 | 7962 | 8175.1 | 8561.8 | 7356 | 7678.1 | 6997.7 | 7381 | 6851.8 | 7005.3 | 7292.9 | 6182.7 | 6409.6
2013-02-21 | 10 | 2013-02-21 10:00 | 34972.8318 | 7207.4289 | 6706.8642 | 6778.0956 | 7829.5 | 8460.5 | 7703.1 | 7919.1 | 8346.6 | 7100.1 | 7462.9 | 7222 | 7643.5 | 6997.8 | 7175.8 | 7512.7 | 6353.1 | 6631.3
2013-02-21 | 11 | 2013-02-21 11:00 | 34849.8463 | 8225.9789 | 7722.1449 | 7857.0813 | 7525 | 8146 | 7456.8 | 7610.3 | 8003.3 | 6788.2 | 7116.6 | 7503.8 | 7882.4 | 7347.7 | 7486.7 | 7779.9 | 6667.8 | 6896.4
2013-02-21 | 12 | 2013-02-21 12:00 | 34473.3919 | 8337.5623 | 7812.8726 | 7910.9499 | 7469.1 | 8077.4 | 7440.4 | 7568.1 | 7950.4 | 6746.2 | 7070.9 | 7680.8 | 8001.9 | 7503.8 | 7650.1 | 7987.6 | 6833.9 | 7106.7
2013-02-21 | 13 | 2013-02-21 13:00 | 34098.0858 | 8036.4472 | 7439.2273 | 7548.17 | 7474.6 | 8033.1 | 7459.1 | 7572.5 | 7961.9 | 6750.4 | 7083 | 7770.3 | 8104.2 | 7590.3 | 7733.5 | 8077.1 | 6916.7 | 7195.9
2013-02-21 | 14 | 2013-02-21 14:00 | 33768.6099 | 7759.1149 | 7189.0092 | 7382.5554 | 7591.3 | 8059.8 | 7554.4 | 7667.5 | 8050.2 | 6846.9 | 7170 | 7989.8 | 8375.9 | 7846.3 | 7988.3 | 8354 | 7168.2 | 7469.2
2013-02-21 | 15 | 2013-02-21 15:00 | 33357.2466 | 7432.9462 | 6916.9457 | 7099.2089 | 7645.3 | 8056.9 | 7593.3 | 7730.7 | 8113.9 | 6911.4 | 7230.1 | 7876.9 | 8236 | 7723.3 | 7882.8 | 8269 | 7063.7 | 7385.2
2013-02-21 | 16 | 2013-02-21 16:00 | 33070.9764 | 7220.9034 | 6696.6051 | 6871.3338 | 7512.2 | 7908 | 7456.8 | 7590.3 | 7982.4 | 6770.2 | 7097.9 | 7423.3 | 7745.9 | 7268.4 | 7405.6 | 7759.7 | 6583.2 | 6872.7
2013-02-21 | 17 | 2013-02-21 17:00 | 32833.7887 | 6416.8323 | 5838.8036 | 5999.9092 | 7146.9 | 7524.1 | 7102.8 | 7231.3 | 7589.4 | 6408.6 | 6702.1 | 6421.7 | 6728.4 | 6229.5 | 6394.8 | 6760.5 | 5572.7 | 5873.8
2013-02-21 | 18 | 2013-02-21 18:00 | 32550.4254 | 4199.572 | 3647.1693 | 3700.071 | 6129.8 | 6527.3 | 6083.8 | 6202.1 | 6536 | 5380.7 | 5650.1 | 4444.2 | 4757.7 | 4272.4 | 4424.6 | 4803.5 | 3601.5 | 3915.8
2013-02-21 | 19 | 2013-02-21 19:00 | 33855.9947 | 2362.1878 | 1755.4905 | 1817.4309 | 5741 | 6199 | 5633.4 | 5757 | 6071.3 | 4934.6 | 5184.5 | 3829.7 | 4197.3 | 3626.1 | 3825.6 | 4197.1 | 3003.5 | 3310.5
2013-02-21 | 20 | 2013-02-21 20:00 | 34745.0563 | 2231.5706 | 1677.575 | 1742.5795 | 5781.2 | 6233.3 | 5661.1 | 5801.3 | 6151.3 | 4979 | 5264.4 | 3960.8 | 4284.8 | 3810 | 4002.4 | 4331.8 | 3180.2 | 3444.9
2013-02-21 | 21 | 2013-02-21 21:00 | 34259.0677 | 2839.0937 | 2338.1859 | 2395.4604 | 5914.7 | 6328.1 | 5768.4 | 5912.1 | 6257.3 | 5089.9 | 5370.5 | 3365.9 | 3647.4 | 3150.6 | 3354.9 | 3653.4 | 2533 | 2766.9
2013-02-21 | 22 | 2013-02-21 22:00 | 33065.0297 | 3514.2667 | 2889.7131 | 2911.3235 | 5623 | 5984.1 | 5451.9 | 5615.7 | 5943.7 | 4793.5 | 5057 | 3042.7 | 3257.4 | 2881.8 | 3041.2 | 3268.5 | 2218.9 | 2381.6
2013-02-21 | 23 | 2013-02-21 23:00 | 30783.0845 | 3976.7114 | 3419.1717 | 3463.6266 | 5312.7 | 5651.4 | 5111.2 | 5310.8 | 5604.7 | 4487.9 | 4717.1 | 2960.9 | 3193.7 | 2791.8 | 2966.2 | 3219.4 | 2147.7 | 2336.2
2013-02-21 | 24 | 2013-02-22 | 28630.9963 | 4403.7613 | 3845.9419 | 3898.7543 | 5101.8 | 5417 | 4918.9 | 5096.7 | 5356.9 | 4274.6 | 4470.1 | 3171 | 3376.4 | 2996.4 | 3168 | 3387.9 | 2346.7 | 2502.1
2013-02-22 | 1 | 2013-02-22 01:00 | 27272.3334 | 4710.9982 | 4245.2275 | 4306.5147 | 3269.5 | 3495.8 | 3111.6 | 3274.3 | 3480.3 | 2453.5 | 2594.8 | 3376.2 | 3579 | 3226.9 | 3377.3 | 3594 | 2554.8 | 2706.9
2013-02-22 | 2 | 2013-02-22 02:00 | 26729.5037 | 4270.5904 | 3868.8033 | 3906.0598 | 3073 | 3305.7 | 2921.3 | 3086.3 | 3296.7 | 2264.9 | 2410.6 | 3390.3 | 3612.7 | 3225.3 | 3388.2 | 3616.9 | 2566.1 | 2730.3
2013-02-22 | 3 | 2013-02-22 03:00 | 26739.4942 | 4151.5706 | 3813.3264 | 3843.6227 | 2763.8 | 2984.3 | 2652 | 2792.7 | 2982.6 | 1971.4 | 2096.6 | 3300.6 | 3482.7 | 3204.1 | 3311.4 | 3495.5 | 2489.4 | 2608.9
2013-02-22 | 4 | 2013-02-22 04:00 | 27252.2229 | 3689.2225 | 3419.5312 | 3419.115 | 2537.6 | 2716.5 | 2419.8 | 2531.9 | 2678.3 | 1711.9 | 1793.7 | 3444.1 | 3594.4 | 3364.2 | 3447.9 | 3596.2 | 2627.9 | 2711.7
2013-02-22 | 5 | 2013-02-22 05:00 | 28430.2245 | 2555.1419 | 2350.7944 | 2330.6783 | 2360 | 2493.9 | 2303 | 2402.5 | 2503.6 | 1583.5 | 1625.6 | 3062.2 | 3155.3 | 3006.5 | 3063.6 | 3149.1 | 2244.5 | 2270.6
2013-02-22 | 6 | 2013-02-22 06:00 | 31343.0455 | 2414.5973 | 2248.0332 | 2206.8431 | 2048.3 | 2165.7 | 1991.1 | 2089.6 | 2176.6 | 1271.9 | 1302.4 | 2746.4 | 2845.4 | 2619.3 | 2712.1 | 2825.1 | 1896.5 | 1951.2
2013-02-22 | 7 | 2013-02-22 07:00 | 36118.3548 | 2300.899 | 2170.7351 | 2127.7741 | 1813.5 | 1909.9 | 1754 | 1841 | 1911.7 | 1027.7 | 1050.6 | 2477.8 | 2548.8 | 2373.2 | 2434.1 | 2537.6 | 1625.4 | 1678.2
2013-02-22 | 8 | 2013-02-22 08:00 | 37649.0975 | 2438.1652 | 2308.4564 | 2278.4762 | 1541.5 | 1625.6 | 1451.4 | 1529.5 | 1589.3 | 736.5 | 748.2 | 2106.6 | 2163.7 | 2007.2 | 2063.5 | 2160.3 | 1283.1 | 1334.8
2013-02-22 | 9 | 2013-02-22 09:00 | 37238.016 | 2380.1289 | 2226.9347 | 2215.8604 | 1190.3 | 1258.1 | 1132.6 | 1190.9 | 1244.4 | 431.6 | 432.3 | 2092.8 | 2178.7 | 1979.8 | 2062.9 | 2179.8 | 1294.5 | 1361
2013-02-22 | 10 | 2013-02-22 10:00 | 37084.511 | 2005.1639 | 1869.5665 | 1852.1589 | 1013.9 | 1067.8 | 954.2 | 1014.5 | 1058.9 | 328.2 | 332.7 | 2014.4 | 2081.3 | 1923.8 | 2003.2 | 2107.1 | 1238 | 1287.8
2013-02-22 | 11 | 2013-02-22 11:00 | 36749.1432 | 1677.2018 | 1477.5713 | 1507.0762 | 994.4 | 1064.1 | 917 | 988.3 | 1050.4 | 351.8 | 376 | 1962.2 | 2046 | 1880.4 | 1976.5 | 2048.1 | 1207.2 | 1232.5
2013-02-22 | 12 | 2013-02-22 12:00 | 36042.9641 | 1373.7062 | 1151.1204 | 1180.9578 | 972.2 | 1033.1 | 895.7 | 965.6 | 1020.9 | 368.2 | 388.2 | 1814.2 | 1872.3 | 1722.5 | 1818.3 | 1878.8 | 1066 | 1086.4
2013-02-22 | 13 | 2013-02-22 13:00 | 35110.1887 | 1195.7273 | 1006.0906 | 1034.5628 | 977.7 | 1039.8 | 896.4 | 970.2 | 1025.7 | 396.3 | 416.7 | 1489.3 | 1645.3 | 1358.1 | 1483.8 | 1638.8 | 804.5 | 919.6
2013-02-22 | 14 | 2013-02-22 14:00 | 34359.8095 | 1050.7453 | 817.3599 | 836.7063 | 1029.5 | 1106.5 | 939.5 | 1029.2 | 1106.4 | 457.8 | 498 | 1279.7 | 1506.5 | 1154 | 1278.2 | 1450 | 743.2 | 875.5
2013-02-22 | 15 | 2013-02-22 15:00 | 33452.018 | 1093.3271 | 833.9833 | 858.6122 | 1091.3 | 1190.9 | 1016.2 | 1110.5 | 1208.8 | 539 | 597.2 | 1221.3 | 1483.6 | 1078.5 | 1223.9 | 1435 | 789.8 | 959.8
2013-02-22 | 16 | 2013-02-22 16:00 | 32713.6392 | 1248.5381 | 970.5694 | 990.4935 | 1186.4 | 1312.2 | 1119.3 | 1207 | 1318.2 | 618 | 687.6 | 1218.6 | 1519.1 | 1083.8 | 1219.7 | 1429.2 | 781.6 | 947
2013-02-22 | 17 | 2013-02-22 17:00 | 32477.221 | 1255.026 | 932.3823 | 945.2113 | 1310.3 | 1455.9 | 1241.2 | 1332.1 | 1453.7 | 716.7 | 797.8 | 1202.6 | 1509.3 | 1026.4 | 1192.2 | 1425.5 | 726.4 | 914.5
2013-02-22 | 18 | 2013-02-22 18:00 | 32867.2536 | 1229.4563 | 921.9034 | 931.2683 | 1534 | 1691 | 1450.1 | 1551.6 | 1683.7 | 836.3 | 928.5 | 1289.3 | 1596.1 | 1082.1 | 1268.7 | 1517.7 | 769.6 | 972.6
2013-02-22 | 19 | 2013-02-22 19:00 | 34634.5192 | 1241.1335 | 997.231 | 1000.7552 | 2174.6 | 2355.4 | 2091.8 | 2201.9 | 2350.4 | 1402.3 | 1509.1 | 1639.1 | 1910.5 | 1438.1 | 1613.9 | 1851.6 | 926.2 | 1116.5
2013-02-22 | 20 | 2013-02-22 20:00 | 35548.1973 | 1958.8218 | 1707.6022 | 1718.3454 | 2537 | 2728.2 | 2441.5 | 2574.7 | 2741.9 | 1766.4 | 1884.5 | 2206.1 | 2471.2 | 1999.2 | 2177.7 | 2433.4 | 1416.5 | 1619.1
2013-02-22 | 21 | 2013-02-22 21:00 | 35203.7563 | 2633.3103 | 2340.0551 | 2361.5021 | 2785.1 | 3004.2 | 2640.1 | 2808.1 | 3005.9 | 1992.3 | 2130.1 | 2733.6 | 2963 | 2517.6 | 2700.8 | 2963.4 | 1911.5 | 2119.7
2013-02-22 | 22 | 2013-02-22 22:00 | 34542.1302 | 3124.1572 | 2838.4886 | 2862.7983 | 3025.5 | 3268.3 | 2869.6 | 3047.5 | 3266.8 | 2227.9 | 2382.7 | 2902.3 | 3131.4 | 2668.6 | 2858.4 | 3124.9 | 2044.8 | 2251.7
2013-02-22 | 23 | 2013-02-22 23:00 | 33154.837 | 3092.8026 | 2787.1425 | 2810.618 | 3257.4 | 3515.8 | 3116.2 | 3289.8 | 3527.5 | 2467.6 | 2640.7 | 3661.7 | 4002.8 | 3480.2 | 3730.1 | 4051.6 | 2920.5 | 3185.6
2013-02-22 | 24 | 2013-02-23 | 31497.387 | 2977.7602 | 2584.8286 | 2598.3709 | 3506.7 | 3748.1 | 3394.3 | 3551.1 | 3766.8 | 2728.7 | 2879.7 | 2893.4 | 3118.8 | 2684 | 2881.8 | 3127.7 | 2059 | 2240.2
2013-02-23 | 1 | 2013-02-23 01:00 | 30263.5955 | 2703.3586 | 2316.6869 | 2341.1609 | 2541 | 2725.1 | 2393.1 | 2537.7 | 2717.9 | 1715.7 | 1836.2 | 2859 | 3093.6 | 2647.1 | 2838.8 | 3080.9 | 2017.3 | 2194.9
2013-02-23 | 2 | 2013-02-23 02:00 | 29603.721 | 2574.4565 | 2151.3778 | 2172.711 | 2557.1 | 2738.4 | 2391.9 | 2527.3 | 2686.2 | 1705.8 | 1808.7 | 2663.7 | 2916 | 2464.3 | 2653.5 | 2904 | 1831.3 | 2017.3
2013-02-23 | 3 | 2013-02-23 03:00 | 29433.2799 | 2197.0926 | 1779.1756 | 1801.7943 | 2578.6 | 2754.6 | 2455.6 | 2570.4 | 2715.2 | 1749.5 | 1847.1 | 2484.4 | 2742.4 | 2321.9 | 2503.5 | 2751.9 | 1681.7 | 1867.2
2013-02-23 | 4 | 2013-02-23 04:00 | 29591.0257 | 2106.0955 | 1772.4258 | 1789.4698 | 2835.6 | 3005.4 | 2749.9 | 2831.1 | 2965.7 | 2012.6 | 2102.2 | 2787.9 | 3030 | 2647.1 | 2798.4 | 3021.3 | 1976.2 | 2137.3
2013-02-23 | 5 | 2013-02-23 05:00 | 30152.1981 | 2465.8191 | 2222.9869 | 2217.0726 | 3060.2 | 3213 | 2972.2 | 3030 | 3142.4 | 2218.1 | 2284.2 | 3045.9 | 3302 | 2909.7 | 3063.3 | 3295.9 | 2241 | 2415.4
2013-02-23 | 6 | 2013-02-23 06:00 | 31457.8618 | 2718.8728 | 2383.7607 | 2402.5619 | 3435.2 | 3577.2 | 3404.2 | 3438.1 | 3532.6 | 2628.5 | 2679 | 2410.7 | 2662 | 2276.6 | 2431.3 | 2651.2 | 1640.8 | 1817.9
2013-02-23 | 7 | 2013-02-23 07:00 | 33530.685 | 2320.2077 | 2079.3854 | 2101.2511 | 3337.9 | 3475 | 3343.9 | 3371.8 | 3465.3 | 2558.3 | 2604.5 | 2431.1 | 2630.7 | 2334.7 | 2444.7 | 2616.6 | 1673.5 | 1804.4
2013-02-23 | 8 | 2013-02-23 08:00 | 34827.0369 | 1581.1851 | 1478.9617 | 1485.1946 | 2843.9 | 2954.1 | 2798 | 2828.4 | 2905.3 | 2017.9 | 2043.7 | 2444.8 | 2586.5 | 2368.3 | 2454.6 | 2579.5 | 1689.6 | 1774.6
2013-02-23 | 9 | 2013-02-23 09:00 | 35317.5403 | 1408.4214 | 1270.369 | 1284.2256 | 2524.9 | 2613.8 | 2488.5 | 2501.4 | 2572.1 | 1690.7 | 1705.3 | 2059.9 | 2282.9 | 2008.9 | 2072 | 2159.1 | 1341 | 1391.5
2013-02-23 | 10 | 2013-02-23 10:00 | 34870.2914 | 1405.6002 | 1237.8289 | 1248.6629 | 1938.1 | 1999.4 | 1902 | 1913.4 | 1961.4 | 1112.7 | 1113.9 | 1456.9 | 1675.8 | 1426.2 | 1485.1 | 1554.3 | 811.8 | 845.9
2013-02-23 | 11 | 2013-02-23 11:00 | 33953.9331 | 1751.2468 | 1683.2087 | 1684.9881 | 1748.6 | 1801.1 | 1712.3 | 1722.3 | 1761.2 | 927.9 | 927.9 | 1212.1 | 1322.9 | 1163.4 | 1222.4 | 1291.6 | 662 | 696.9
2013-02-23 | 12 | 2013-02-23 12:00 | 32842.0137 | 1973.2846 | 1915.5183 | 1929.7647 | 1697.1 | 1758.9 | 1660.6 | 1673.2 | 1721.6 | 883.3 | 884.7 | 1127.4 | 1264.4 | 1094.5 | 1131.5 | 1183.5 | 474.5 | 493.3
2013-02-23 | 13 | 2013-02-23 13:00 | 31653.4437 | 2141.9724 | 2064.3638 | 2072.8762 | 1762.1 | 1840.9 | 1708.7 | 1730.7 | 1795.6 | 941 | 955.3 | 1247.5 | 1339.6 | 1199.7 | 1247.6 | 1328.5 | 543.3 | 590.7
2013-02-23 | 14 | 2013-02-23 14:00 | 30484.7626 | 2027.8922 | 1957.4553 | 1966.0938 | 1746.9 | 1830.8 | 1679.8 | 1703.2 | 1774 | 917.2 | 937.5 | 1542.6 | 1631.1 | 1520.1 | 1549.8 | 1612.3 | 831.2 | 858.7
2013-02-23 | 15 | 2013-02-23 15:00 | 29681.2346 | 1750.2414 | 1686.4121 | 1692.3297 | 1736.9 | 1814.1 | 1675.8 | 1692.4 | 1756.4 | 900.7 | 913.9 | 1600.1 | 1646.3 | 1564.4 | 1600.9 | 1662.9 | 881 | 907.5
2013-02-23 | 16 | 2013-02-23 16:00 | 29207.786 | 1495.7334 | 1443.2237 | 1454.1886 | 1758.5 | 1828.1 | 1705.1 | 1713.5 | 1772.1 | 911.7 | 921.2 | 1627.7 | 1687.3 | 1602 | 1627.5 | 1690.8 | 909.7 | 933.9
2013-02-23 | 17 | 2013-02-23 17:00 | 29039.4622 | 1212.4145 | 1135.4339 | 1138.3141 | 1714.8 | 1783.7 | 1650.8 | 1671.1 | 1735.3 | 868.1 | 881.6 | 1588.1 | 1646.9 | 1566.9 | 1597.8 | 1677.1 | 880.9 | 918
2013-02-23 | 18 | 2013-02-23 18:00 | 29320.1272 | 869.8829 | 764.7779 | 773.1874 | 1478.3 | 1541.3 | 1431.3 | 1446.9 | 1507.7 | 687.7 | 699.3 | 1424.7 | 1493.5 | 1401.6 | 1440.9 | 1524.9 | 739.3 | 776.3
2013-02-23 | 19 | 2013-02-23 19:00 | 30970.6479 | 891.8582 | 824.8791 | 835.506 | 1522 | 1590.3 | 1471.4 | 1481.7 | 1548.1 | 741.8 | 762.6 | 1238.9 | 1311.2 | 1210.2 | 1254.5 | 1345.6 | 513.4 | 555
2013-02-23 | 20 | 2013-02-23 20:00 | 32278.5588 | 1859.728 | 1696.6178 | 1706.1244 | 2005.3 | 2116.8 | 1936.8 | 1960.3 | 2067 | 1164.6 | 1216.7 | 1635.8 | 1773.6 | 1580.3 | 1647.1 | 1776 | 831.5 | 900.4
2013-02-23 | 21 | 2013-02-23 21:00 | 32130.4143 | 3501.2763 | 3141.168 | 3146.6584 | 2730.5 | 2909.8 | 2627.5 | 2692.2 | 2861.9 | 1870.3 | 1990.1 | 2671 | 2857 | 2595.1 | 2687.9 | 2879.3 | 1865.6 | 1992.5
2013-02-23 | 22 | 2013-02-23 22:00 | 31653.1446 | 5165.8847 | 4713.5304 | 4715.1569 | 3479.4 | 3712.2 | 3356.5 | 3461.9 | 3677 | 2639.4 | 2802 | 3864.6 | 4079.5 | 3765.8 | 3875.2 | 4090.7 | 3052 | 3202.6
2013-02-23 | 23 | 2013-02-23 23:00 | 30601.9734 | 6849.453 | 6288.0616 | 6470.8479 | 4119.4 | 4419.9 | 4008.8 | 4134.5 | 4409.9 | 3312.1 | 3535.8 | 4937.5 | 5170.3 | 4827.2 | 4959.6 | 5201.7 | 4137.9 | 4315.3
2013-02-23 | 24 | 2013-02-24 | 29407.2805 | 7484.7252 | 6888.9217 | 7267.9405 | 4635.3 | 4960.5 | 4519 | 4656.5 | 4953.3 | 3833.8 | 4084.1 | 5837.8 | 6088.3 | 5754.8 | 5866.6 | 6118.4 | 5044.5 | 5231.6
2013-02-24 | 1 | 2013-02-24 01:00 | 28512.7827 | 7706.9521 | 7126.0257 | 7308.1118 | 5637.6 | 5960.1 | 5546.6 | 5682.2 | 5953.7 | 4859.8 | 5066.6 | 6251.8 | 6523.4 | 6190.9 | 6297.1 | 6553.6 | 5475.6 | 5669.8
2013-02-24 | 2 | 2013-02-24 02:00 | 28019.1227 | 7697.5489 | 7083.3214 | 7187.9234 | 5807.9 | 6121.6 | 5748.3 | 5861.1 | 6117.2 | 5039.4 | 5241.9 | 6775 | 7047.1 | 6728.2 | 6830.8 | 7079.6 | 6008.7 | 6194.2
2013-02-24 | 3 | 2013-02-24 03:00 | 27939.1381 | 7590.2401 | 6958.6858 | 7064.0606 | 5989.4 | 6302.4 | 5935.1 | 6043.9 | 6296.6 | 5221.8 | 5430.8 | 6780.1 | 7053.3 | 6750 | 6840.4 | 7080.5 | 6019 | 6207.5
2013-02-24 | 4 | 2013-02-24 04:00 | 28021.302 | 7432.172 | 6804.3405 | 6905.1486 | 6104 | 6412.5 | 6060.8 | 6157.1 | 6406.3 | 5335.7 | 5541.7 | 6568.9 | 6834.8 | 6495.1 | 6589.8 | 6833.6 | 5767.6 | 5966.2
2013-02-24 | 5 | 2013-02-24 05:00 | 28446.3295 | 7581.1432 | 6962.7988 | 7060.4863 | 6205.1 | 6519.2 | 6154.4 | 6249.9 | 6506.7 | 5428 | 5639.3 | 6427.2 | 6691.6 | 6365.8 | 6463.2 | 6706.8 | 5640.9 | 5838.3
2013-02-24 | 6 | 2013-02-24 06:00 | 29483.9501 | 7611.1404 | 6997.3455 | 7092.9797 | 6310.3 | 6624.9 | 6258.2 | 6365.3 | 6624.3 | 5543.2 | 5746.7 | 6520.3 | 6809.4 | 6459 | 6579.7 | 6833 | 5757.2 | 5961.3
2013-02-24 | 7 | 2013-02-24 07:00 | 30833.389 | 7196.1165 | 6624.0569 | 6750.407 | 6445.9 | 6768.8 | 6375.4 | 6491.6 | 6751.3 | 5669.3 | 5867.8 | 6611.8 | 6904.8 | 6562 | 6670.3 | 6918.3 | 5848.1 | 6044.6
2013-02-24 | 8 | 2013-02-24 08:00 | 31631.1029 | 7120.0342 | 6544.3876 | 6681.0807 | 6373.1 | 6691.8 | 6294.6 | 6422 | 6674.7 | 5599.2 | 5797.8 | 6643.5 | 6937.8 | 6581.3 | 6686 | 6925.3 | 5864.3 | 6049.2
2013-02-24 | 9 | 2013-02-24 09:00 | 31963.6891 | 6520.6074 | 5975.0172 | 6044.1256 | 6110.7 | 6384.9 | 6061.3 | 6160.3 | 6370.9 | 5337.8 | 5505.4 | 6259.9 | 6532.4 | 6206.2 | 6293.1 | 6511.5 | 5474.3 | 5650
2013-02-24 | 10 | 2013-02-24 10:00 | 31526.7929 | 6175.7624 | 5750.139 | 5809.578 | 6046.2 | 6290.2 | 5999.3 | 6085.8 | 6274.2 | 5264.2 | 5409.9 | 5789.9 | 6032.4 | 5723.9 | 5780.5 | 5955.1 | 4959.8 | 5090.3
2013-02-24 | 11 | 2013-02-24 11:00 | 30670.0519 | 6647.8127 | 6178.9483 | 6232.172 | 6036.6 | 6261 | 5967.3 | 6069.9 | 6250.4 | 5247 | 5379.2 | 5453.2 | 5671 | 5431.4 | 5474.7 | 5635.8 | 4661.4 | 4781
2013-02-24 | 12 | 2013-02-24 12:00 | 29703.5986 | 6177.7754 | 5720.8749 | 5736.6369 | 6063.6 | 6311.7 | 5977 | 6077.9 | 6289.1 | 5255.4 | 5415.8 | 4945 | 5152 | 4892.7 | 4955.8 | 5129 | 4139.2 | 4268.7
2013-02-24 | 13 | 2013-02-24 13:00 | 29108.5208 | 4975.6881 | 4548.0174 | 4547.321 | 6044.4 | 6330.5 | 5951.2 | 6066.3 | 6323.9 | 5244.2 | 5442.8 | 4828.7 | 5041.5 | 4757.1 | 4835.6 | 5026.9 | 4013.9 | 4162.6
2013-02-24 | 14 | 2013-02-24 14:00 | 28598.9055 | 4080.8405 | 3680.373 | 3678.132 | 6054 | 6380.6 | 5948.7 | 6070.2 | 6360.1 | 5247.7 | 5474.4 | 4860.2 | 5068.4 | 4764.3 | 4866.1 | 5067.5 | 4044.7 | 4196.5
2013-02-24 | 15 | 2013-02-24 15:00 | 28320.3554 | 3687.1095 | 3241.9456 | 3239.9664 | 6051.3 | 6409.2 | 5966.6 | 6076.3 | 6385.5 | 5253.7 | 5498.4 | 5157.7 | 5408.5 | 5034.3 | 5158.7 | 5407.9 | 4336.8 | 4521.4
2013-02-24 | 16 | 2013-02-24 16:00 | 28175.0441 | 3862.1463 | 3390.204 | 3403.44 | 6081.5 | 6462.8 | 5996.6 | 6105.3 | 6414.7 | 5283.2 | 5529.5 | 4950.3 | 5279.2 | 4810 | 4979 | 5297 | 4156.8 | 4410.2
2013-02-24 | 17 | 2013-02-24 17:00 | 28458.4254 | 4353.3274 | 3831.6541 | 3853.48 | 5785.4 | 6197.8 | 5663.3 | 5792.8 | 6115.2 | 4970.5 | 5228.1 | 4445.2 | 4771.1 | 4288.1 | 4479.8 | 4809.1 | 3658.2 | 3922.8
2013-02-24 | 18 | 2013-02-24 18:00 | 29282.4711 | 4896.5428 | 4362.9445 | 4436.4379 | 4522 | 4928.5 | 4347.9 | 4517.1 | 4853.7 | 3694.7 | 3966.8 | 4055.7 | 4411.5 | 3938.1 | 4124.1 | 4467.7 | 3302.2 | 3581.1
2013-02-24 | 19 | 2013-02-24 19:00 | 31299.3971 | 4706.8366 | 4179.1306 | 4284.2382 | 4324.5 | 4750.1 | 4166.8 | 4355.6 | 4723.9 | 3532.9 | 3836.7 | 4431.8 | 4805.5 | 4274.8 | 4471.9 | 4833.5 | 3649.8 | 3946.9
2013-02-24 | 20 | 2013-02-24 20:00 | 32525.7982 | 5651.7209 | 5045.4022 | 5063.3433 | 4443.1 | 4914.9 | 4303 | 4516.6 | 4920.1 | 3694.7 | 4033.6 | 5375.6 | 5723.8 | 5176.6 | 5392.7 | 5778.9 | 4570.6 | 4892.1
2013-02-24 | 21 | 2013-02-24 21:00 | 32087.4572 | 6911.7267 | 6198.3072 | 6250.091 | 4942.9 | 5473 | 4808.2 | 5051.9 | 5494.4 | 4229.2 | 4607.1 | 5545.5 | 5922.4 | 5334.6 | 5542.4 | 5928.4 | 4719.9 | 5041.3
2013-02-24 | 22 | 2013-02-24 22:00 | 31025.7876 | 7570.175 | 6864.3376 | 7072.2175 | 5460.5 | 6006.8 | 5427.1 | 5653.9 | 6110.2 | 4833 | 5224.8 | 6010 | 6419 | 5800.5 | 6014.1 | 6370.8 | 5191.8 | 5483.8
2013-02-24 | 23 | 2013-02-24 23:00 | 29015.4387 | 7579.1362 | 6883.4492 | 7246.2121 | 5646.6 | 6165.2 | 5537.4 | 5766.7 | 6208.1 | 4944.9 | 5321.8 | 6627.7 | 7074.4 | 6454.2 | 6665 | 7067.6 | 5843.2 | 6181.1
2013-02-24 | 24 | 2013-02-25 | 26987.5025 | 7415.7676 | 6721.3287 | 6945.8422 | 5803.6 | 6232.8 | 5674.2 | 5896.9 | 6256.8 | 5074.7 | 5370 | 6902.7 | 7356.1 | 6772.4 | 7004.5 | 7408.4 | 6182.6 | 6521.7
2013-02-25 | 1 | 2013-02-25 01:00 | 25432.4423 | 7354.8358 | 6663.8542 | 7007.6253 | 5900.5 | 6193.9 | 5807.5 | 6013.6 | 6285.2 | 5190.7 | 5397.7 | 6872 | 7247.6 | 6801.4 | 7024.7 | 7421.6 | 6202.2 | 6534.5
2013-02-25 | 2 | 2013-02-25 02:00 | 24573.6818 | 6902.8796 | 6297.6581 | 6532.6465 | 5656.1 | 5921.6 | 5588 | 5765.9 | 6028.4 | 4943.9 | 5141.8 | 7091.6 | 7442.2 | 7058.7 | 7232 | 7626.5 | 6409.6 | 6739.5
2013-02-25 | 3 | 2013-02-25 03:00 | 24070.8425 | 6072.3764 | 5375.9902 | 5477.3153 | 5754.5 | 6057.7 | 5716 | 5853.9 | 6168.3 | 5032.1 | 5286.6 | 6701.6 | 7043.9 | 6588.3 | 6786.5 | 7216.4 | 5964.1 | 6329.4
2013-02-25 | 4 | 2013-02-25 04:00 | 24025.3587 | 3996.4709 | 3413.9581 | 3518.4315 | 5869.4 | 6205.4 | 5894.9 | 6030.6 | 6389.8 | 5209.3 | 5503.9 | 5998.4 | 6309.1 | 5797.9 | 6021.7 | 6462.4 | 5198.9 | 5574.9
2013-02-25 | 5 | 2013-02-25 05:00 | 24820.6626 | 3206.9431 | 2766.475 | 2885.8271 | 6069.1 | 6474.6 | 5996.5 | 6105.2 | 6407.1 | 5285.4 | 5522.8 | 5544.3 | 5932 | 5245.2 | 5470.4 | 5881.6 | 4647.5 | 4994.1
2013-02-25 | 6 | 2013-02-25 06:00 | 27149.6563 | 3621.1688 | 3224.0173 | 3426.2416 | 6136 | 6680.3 | 6019.7 | 6257 | 6649.6 | 5437.6 | 5765.7 | 5457.7 | 5968.5 | 5174.7 | 5427 | 5913.6 | 4606 | 5027.9
2013-02-25 | 7 | 2013-02-25 07:00 | 31252.5413 | 4632.6204 | 4155.1027 | 4259.8608 | 6317.9 | 6961.2 | 6187.4 | 6477.7 | 7019 | 5658.4 | 6135.2 | 5821.4 | 6372.4 | 5489.8 | 5801.4 | 6358.4 | 4979.8 | 5472.2
2013-02-25 | 8 | 2013-02-25 08:00 | 32741.3895 | 5574.2624 | 5144.9093 | 5278.5549 | 6727.7 | 7452.4 | 6569.5 | 6883.1 | 7549.4 | 6062.9 | 6664.7 | 6325.4 | 6848.7 | 5992.6 | 6317.9 | 6869.3 | 5496.1 | 5983
2013-02-25 | 9 | 2013-02-25 09:00 | 32567.9227 | 6570.3393 | 6153.6543 | 6661.3222 | 7479.9 | 8219.7 | 7269.7 | 7594.4 | 8281.8 | 6773.1 | 7395.9 | 7036 | 7646.6 | 6693.3 | 7047.2 | 7708.9 | 6225.5 | 6822.7
2013-02-25 | 10 | 2013-02-25 10:00 | 32950.995 | 7530.2646 | 6887.0661 | 8153.3196 | 7688.7 | 8400.4 | 7490.5 | 7802.6 | 8459.9 | 6981.1 | 7573.7 | 7555 | 8190.6 | 7217.2 | 7584.9 | 8272.6 | 6763.7 | 7386.9
2013-02-25 | 11 | 2013-02-25 11:00 | 33312.3235 | 8037.8948 | 7339.7558 | 8331.9491 | 7872.8 | 8577.4 | 7686.9 | 7995.6 | 8638.8 | 7174 | 7752.5 | 7882 | 8537.7 | 7553.8 | 7892.9 | 8609.5 | 7071.3 | 7723.4
2013-02-25 | 12 | 2013-02-25 12:00 | 33237.1516 | 8333.6337 | 7633.9786 | 8444.5037 | 7957.6 | 8713.9 | 7792.9 | 8102.3 | 8795.4 | 7279.6 | 7908.2 | 8337 | 8993 | 8093 | 8422.5 | 9146.9 | 7600.5 | 8260.3
2013-02-25 | 13 | 2013-02-25 13:00 | 32991.5782 | 8329.4545 | 7602.6192 | 8098.6945 | 8038 | 8808.7 | 7899.6 | 8216.2 | 8931.5 | 7394.6 | 8045.2 | 8882.9 | 9534 | 8614.2 | 8916.1 | 9634 | 8094 | 8747.3
2013-02-25 | 14 | 2013-02-25 14:00 | 32850.8685 | 8229.7331 | 7475.9805 | 7902.2905 | 8028 | 8817.3 | 7893.3 | 8217 | 8952.6 | 7395.4 | 8066.4 | 8931.3 | 9557.1 | 8638.5 | 8918.3 | 9607.6 | 8095.3 | 8720
2013-02-25 | 15 | 2013-02-25 15:00 | 32553.1723 | 8191.3115 | 7413.5689 | 7864.4052 | 8180.2 | 8983.5 | 8084.3 | 8408.1 | 9158.4 | 7586.4 | 8272.2 | 8864.9 | 9491.7 | 8570 | 8839.5 | 9537.5 | 8017.7 | 8651.2
2013-02-25 | 16 | 2013-02-25 16:00 | 32498.8966 | 8368.8216 | 7539.8173 | 7809.6877 | 8172.6 | 9006.8 | 8105.7 | 8432.6 | 9214.9 | 7611.9 | 8329.7 | 8940.6 | 9602.1 | 8470.7 | 8728.4 | 9474.9 | 7911 | 8593
2013-02-25 | 17 | 2013-02-25 17:00 | 32903.503 | 8586.217 | 7776.2284 | 8149.8306 | 8105.2 | 8939.5 | 8051.2 | 8380.6 | 9159.2 | 7559.6 | 8273.7 | 8749.9 | 9448.2 | 8399.7 | 8704.7 | 9467.9 | 7890.3 | 8588.9
2013-02-25 | 18 | 2013-02-25 18:00 | 33812.291 | 9040.7376 | 8089.4667 | 8413.6018 | 7928.9 | 8741.3 | 7884 | 8215.9 | 8966.4 | 7396.3 | 8082.3 | 8640.2 | 9335 | 8304.3 | 8621.3 | 9381.8 | 7808.2 | 8504.2
2013-02-25 | 19 | 2013-02-25 19:00 | 36480.2327 | 9054.8765 | 8104.5321 | 8388.4067 | 7532.2 | 8292.6 | 7494.3 | 7814.3 | 8492.6 | 6993.7 | 7607.4 | 8375.3 | 9043.1 | 8033.3 | 8353.1 | 9076.5 | 7536.9 | 8195.8
2013-02-25 | 20 | 2013-02-25 20:00 | 38200.7685 | 8951.7275 | 7958.2746 | 8164.9976 | 7226.5 | 7960.3 | 7195.2 | 7502.7 | 8154.2 | 6681.5 | 7268.4 | 8284.8 | 8920.8 | 7961.7 | 8264.8 | 8933.3 | 7449.7 | 8053.5
2013-02-25 | 21 | 2013-02-25 21:00 | 38125.3658 | 8847.2817 | 7888.566 | 8006.4819 | 7102.8 | 7813.3 | 7069.3 | 7376 | 7998.8 | 6553.9 | 7112.1 | 8014.1 | 8622.5 | 7629.7 | 7935.2 | 8553.4 | 7119 | 7672.6
2013-02-25 | 22 | 2013-02-25 22:00 | 37203.1752 | 8664.4221 | 7693.1904 | 7775.7434 | 7014 | 7709.4 | 6968.7 | 7283.4 | 7890.3 | 6464.1 | 7006.3 | 7841 | 8420.4 | 7512.9 | 7813.2 | 8386 | 6992.1 | 7500.3
2013-02-25 | 23 | 2013-02-25 23:00 | 34985.7876 | 8081.8944 | 7159.8229 | 7258.5475 | 6825.6 | 7515.5 | 6765.8 | 7095.9 | 7714.6 | 6276.5 | 6830.8 | 7540.9 | 8113.6 | 7208 | 7513.9 | 8102.5 | 6692.5 | 7216.6
2013-02-25 | 24 | 2013-02-26 | 32638.893 | 7704.2443 | 6726.8212 | 6855.8926 | 6527.9 | 7190.6 | 6485.1 | 6795.4 | 7380.7 | 5976.3 | 6497 | 7162.4 | 7717.7 | 6827.6 | 7130.2 | 7682.6 | 6308.5 | 6796.2
2013-02-26 | 1 | 2013-02-26 01:00 | 31297.2967 | 7126.0983 | 6117.9868 | 6213.4943 | 6417.8 | 7000.8 | 6146.4 | 6423.8 | 6974.1 | 5602.4 | 6088.2 | 6664.1 | 7194.5 | 6384.6 | 6658.1 | 7152.2 | 5837.8 | 6267.4
2013-02-26 | 2 | 2013-02-26 02:00 | 30675.3393 | 6553.253 | 5609.3332 | 5671.0811 | 6214.1 | 6779.2 | 5945.4 | 6204.1 | 6740 | 5383.1 | 5854.4 | 6302.8 | 6724.3 | 6049.6 | 6287.1 | 6722.8 | 5466.1 | 5837.2
2013-02-26 | 3 | 2013-02-26 03:00 | 30527.0505 | 6124.9868 | 5407.4037 | 5468.9094 | 5927.7 | 6455.2 | 5671.1 | 5907.6 | 6406 | 5086.5 | 5520.5 | 5848.9 | 6308.2 | 5618.8 | 5825.8 | 6216.8 | 5005.2 | 5331.6
2013-02-26 | 4 | 2013-02-26 04:00 | 30757.3262 | 5208.5613 | 4434.105 | 4511.7052 | 5614.1 | 6120.1 | 5385.8 | 5609.6 | 6090.9 | 4788.8 | 5205.6 | 5145.1 | 5581.7 | 4955 | 5115.1 | 5461.1 | 4303.5 | 4585.2
2013-02-26 | 5 | 2013-02-26 05:00 | 31949.114 | 3969.4168 | 3209.8672 | 3262.151 | 5133 | 5605.4 | 4917.2 | 5123.7 | 5569 | 4301.9 | 4682.6 | 4234.3 | 4527.8 | 4031.3 | 4173.3 | 4477.9 | 3358.8 | 3601.4
2013-02-26 | 6 | 2013-02-26 06:00 | 34888.0807 | 3097.8165 | 2552.4278 | 2592.1746 | 4759.1 | 5194.2 | 4545.2 | 4723 | 5127.9 | 3902.2 | 4242.4 | 4032.8 | 4268.7 | 3851.6 | 3990.6 | 4298.9 | 3175.9 | 3419.7
2013-02-26 | 7 | 2013-02-26 07:00 | 39542.3472 | 2626.2525 | 2195.7389 | 2235.8291 | 4249.7 | 4634.1 | 4077.2 | 4226.7 | 4574.8 | 3404.7 | 3688.2 | 3482.7 | 3745.5 | 3322.9 | 3454.6 | 3731.2 | 2659.9 | 2872
2013-02-26 | 8 | 2013-02-26 08:00 | 40293.6138 | 2193.8386 | 1840.013 | 1885.1726 | 3398 | 3714.4 | 3208.8 | 3347.4 | 3635.4 | 2539.8 | 2763.3 | 2838.6 | 3098.6 | 2679.9 | 2812.7 | 3052.9 | 2030.8 | 2206.5
2013-02-26 | 9 | 2013-02-26 09:00 | 38836.0289 | 1384.8614 | 1116.6222 | 1165.4488 | 2375.7 | 2586.1 | 2180.6 | 2343.4 | 2534.9 | 1535.5 | 1665.3 | 1799.8 | 1965.9 | 1687.5 | 1791.2 | 1947.9 | 1047.6 | 1144.7
2013-02-26 | 10 | 2013-02-26 10:00 | 37729.9222 | 753.3313 | 566.3921 | 614.59 | 1745.9 | 1888.3 | 1611 | 1719 | 1844.2 | 942.9 | 1027.7 | 1299.2 | 1405.9 | 1243.9 | 1306.7 | 1402.3 | 649.3 | 707.4
2013-02-26 | 11 | 2013-02-26 11:00 | 36478.6128 | 497.2163 | 357.3032 | 406.2937 | 1521.6 | 1624.2 | 1441.6 | 1492.5 | 1579 | 731.3 | 781.3 | 996.6 | 1063.4 | 970.2 | 1004.1 | 1059.1 | 410 | 431.9
2013-02-26 | 12 | 2013-02-26 12:00 | 35137.5792 | 404.5817 | 307.142 | 356.4037 | 1396 | 1483.5 | 1355 | 1386.1 | 1453.9 | 624.8 | 655.1 | 721 | 755.8 | 707.7 | 718.8 | 743.3 | 201.2 | 201.2
2013-02-26 | 13 | 2013-02-26 13:00 | 33922.7458 | 351.2913 | 291.8851 | 336.014 | 1357.5 | 1432.5 | 1338.8 | 1355.9 | 1408.4 | 601 | 616.6 | 592.2 | 612.2 | 594.8 | 601.2 | 613.9 | 112.3 | 112.3
2013-02-26 | 14 | 2013-02-26 14:00 | 33034.6196 | 397.9037 | 372.2873 | 418.7114 | 1485.3 | 1541.5 | 1502.7 | 1505.8 | 1538.6 | 717.3 | 722.5 | 669.1 | 682.9 | 699.9 | 700.8 | 707.2 | 112.3 | 112.3
2013-02-26 | 15 | 2013-02-26 15:00 | 32197.3941 | 463.1701 | 445.9569 | 496.4584 | 1630.6 | 1669.7 | 1650.8 | 1639.5 | 1658.2 | 842.2 | 842.8 | 718.4 | 728.1 | 716.5 | 712.9 | 715.6 | 111 | 111
2013-02-26 | 16 | 2013-02-26 16:00 | 31618.1679 | 527.1356 | 493.257 | 530.7622 | 1771.1 | 1799.9 | 1813.4 | 1794.3 | 1806.3 | 998.7 | 998.7 | 689.7 | 703.6 | 694.2 | 695.5 | 702.8 | 91.6 | 91.6
2013-02-26 | 17 | 2013-02-26 17:00 | 31482.2658 | 742.6913 | 689.2988 | 720.5127 | 1942.1 | 1970.8 | 1994.8 | 1979.4 | 1991.6 | 1183.2 | 1183.2 | 810.9 | 849.6 | 787.8 | 810.1 | 841.2 | 131.9 | 131.9
2013-02-26 | 18 | 2013-02-26 18:00 | 31702.3774 | 1021.4843 | 901.873 | 967.8031 | 1688.6 | 1732.6 | 1710.5 | 1712.5 | 1739.5 | 932.1 | 932.1 | 835.6 | 907.4 | 773.1 | 822.1 | 888.2 | 158.1 | 185.3
2013-02-26 | 19 | 2013-02-26 19:00 | 33849.0462 | 1755.3366 | 1621.2431 | 1673.8178 | 1606.1 | 1668.4 | 1597.2 | 1614 | 1673.6 | 841.6 | 858.7 | 1301.2 | 1397.4 | 1226.4 | 1303.2 | 1401 | 549.4 | 601.4
2013-02-26 | 20 | 2013-02-26 20:00 | 35391.2389 | 2649.8444 | 2451.51 | 2492.085 | 1813.9 | 1910.5 | 1800.1 | 1829 | 1922.2 | 1030.5 | 1073.8 | 2024 | 2133.7 | 1931.2 | 2014 | 2137.1 | 1227.1 | 1299.6
2013-02-26 | 21 | 2013-02-26 21:00 | 35299.5082 | 3955.6091 | 3658.0559 | 3701.9713 | 2290.3 | 2435.8 | 2250.7 | 2321.2 | 2453.8 | 1505.9 | 1576.4 | 3025.1 | 3259.2 | 2950.6 | 3076.5 | 3198.7 | 2277.2 | 2345.8
2013-02-26 | 22 | 2013-02-26 22:00 | 34192.0557 | 5439.6908 | 4976.8143 | 5068.2544 | 2772.1 | 2969.2 | 2724.4 | 2836.5 | 3020.5 | 2014.7 | 2134.1 | 3538.9 | 3828.6 | 3384.2 | 3537 | 3781.2 | 2715.1 | 2894.8
2013-02-26 | 23 | 2013-02-26 23:00 | 32108.3911 | 6384.6846 | 5804.9813 | 5926.7544 | 3550.9 | 3787 | 3481.3 | 3624.3 | 3842.5 | 2804.4 | 2957.9 | 4214.8 | 4533.4 | 4065.9 | 4251 | 4520.6 | 3431.2 | 3636.2
2013-02-26 | 24 | 2013-02-27 | 30002.5091 | 6626.7651 | 5991.0632 | 6034.5581 | 4854.5 | 5113.5 | 4782.4 | 4931.1 | 5162.6 | 4111.6 | 4278.7 | 4762.2 | 5089.7 | 4671.7 | 4855.2 | 5113 | 4035.2 | 4228.5
2013-02-27 | 1 | 2013-02-27 01:00 | 28783.5627 | 5635.1206 | 5089.5406 | 5114.3323 | 5159.1 | 5412.9 | 5044.1 | 5220.8 | 5439.5 | 4400.6 | 4554.8 | 4857.3 | 5175 | 4786.7 | 4966 | 5205.1 | 4145.5 | 4320.2
2013-02-27 | 2 | 2013-02-27 02:00 | 28368.0596 | 5482.2429 | 4939.531 | 5010.9231 | 5028 | 5262 | 5015.5 | 5182.3 | 5391.3 | 4362.4 | 4513.4 | 5138.7 | 5468 | 5111.8 | 5271.9 | 5506.5 | 4451 | 4621.1
2013-02-27 | 3 | 2013-02-27 03:00 | 28409.2591 | 5679.7423 | 5222.4971 | 5353.1172 | 4903.9 | 5152.6 | 4825.7 | 5012 | 5239.7 | 4192.2 | 4362.6 | 4918.9 | 5219.7 | 4859.5 | 5041.7 | 5276.9 | 4219.6 | 4397.4
2013-02-27 | 4 | 2013-02-27 04:00 | 28918.3907 | 6694.2846 | 6253.6254 | 6453.2112 | 5017.4 | 5278.8 | 4984 | 5178 | 5417.3 | 4357.4 | 4539.9 | 4757.1 | 5039.7 | 4611.2 | 4820.9 | 5071.5 | 3998.1 | 4192.4
2013-02-27 | 5 | 2013-02-27 05:00 | 30138.3021 | 5897.849 | 5410.8699 | 5568.436 | 5044.5 | 5309.6 | 5133.2 | 5319.8 | 5562.1 | 4498.4 | 4682 | 5371 | 5649.9 | 5314.9 | 5484.5 | 5714.2 | 4662.1 | 4827.3
2013-02-27 | 6 | 2013-02-27 06:00 | 33129.6076 | 4999.5354 | 4444.27 | 4607.1782 | 4738.9 | 4989.5 | 4697.5 | 4876.5 | 5111.3 | 4053.9 | 4228.9 | 4933.9 | 5203.6 | 4825.2 | 4975 | 5196.2 | 4152.5 | 4309.3
2013-02-27 | 7 | 2013-02-27 07:00 | 37771.5201 | 4626.7896 | 4174.0942 | 4340.9937 | 4195.5 | 4477 | 3775.2 | 3939.8 | 4191.7 | 3117.5 | 3304.8 | 4686.9 | 4915.2 | 4646 | 4725.3 | 4917.7 | 3902 | 4029.8
2013-02-27 | 8 | 2013-02-27 08:00 | 38348.0729 | 4492.3275 | 4067.0175 | 4223.4305 | 3732.5 | 4002.2 | 3264.6 | 3391.1 | 3649.6 | 2576.4 | 2770.2 | 3886.3 | 4028.2 | 3860.6 | 3898.6 | 4077.6 | 3098.2 | 3224.9
2013-02-27 | 9 | 2013-02-27 09:00 | 36775.8158 | 3965.3125 | 3615.5188 | 3776.4331 | 3628 | 3876.3 | 3448.2 | 3633.9 | 3858.4 | 2820.2 | 2980.2 | 3576.9 | 3711.1 | 3448 | 3629.5 | 3797.4 | 2830.6 | 2947.5
2013-02-27 | 10 | 2013-02-27 10:00 | 35676.8496 | 5372.1001 | 4947.3226 | 5119.9774 | 3672.4 | 3917.2 | 3591 | 3787.8 | 4007.2 | 2986.4 | 3158.3 | 3913.5 | 4032 | 3773.7 | 3993.3 | 4163.6 | 3193.9 | 3305.9
2013-02-27 | 11 | 2013-02-27 11:00 | 34851.2324 | 5488.2485 | 4989.6617 | 5145.8814 | 3820.7 | 4051.2 | 3771.5 | 3989.8 | 4197.5 | 3182.6 | 3353.3 | 4420 | 4552 | 4262.4 | 4517.4 | 4674.7 | 3719.5 | 3828.7
2013-02-27 | 12 | 2013-02-27 12:00 | 34020.0653 | 5722.1461 | 5184.6139 | 5330.506 | 3879.2 | 4116.7 | 3820.9 | 4081.6 | 4302 | 3269.5 | 3446.6 | 4210.5 | 4350.9 | 4044.2 | 4308.6 | 4484.5 | 3520.7 | 3642.6
2013-02-27 | 13 | 2013-02-27 13:00 | 33270.3308 | 5696.571 | 5146.6253 | 5294.4175 | 3847.2 | 4081.7 | 3811.1 | 4088.2 | 4309.7 | 3268.2 | 3444.9 | 4538.5 | 4701.4 | 4373.4 | 4661 | 4858.9 | 3866.5 | 4005.6
2013-02-27 | 14 | 2013-02-27 14:00 | 32778.2137 | 5712.7825 | 5125.8686 | 5271.5867 | 3840.8 | 4108.3 | 3739.5 | 4072.6 | 4320.6 | 3252.2 | 3437.6 | 4366.9 | 4567.4 | 4185.8 | 4483.5 | 4720 | 3688.7 | 3860.5
2013-02-27 | 15 | 2013-02-27 15:00 | 32254.3268 | 5900.1405 | 5197.6725 | 5338.1196 | 3747.5 | 4031.5 | 3639 | 3985.5 | 4252.1 | 3165.6 | 3367.6 | 4643.6 | 4926.5 | 4436.8 | 4779.9 | 5098.7 | 3985.2 | 4239.6
2013-02-27 | 16 | 2013-02-27 16:00 | 31874.7826 | 5685.2667 | 4940.1299 | 5060.3724 | 3468.7 | 3738.5 | 3435.5 | 3764.1 | 4021.6 | 2944.9 | 3137.8 | 4445.4 | 4762.7 | 4243 | 4593.3 | 4947.3 | 3798.4 | 4087.9
2013-02-27 | 17 | 2013-02-27 17:00 | 31973.9558 | 5121.8441 | 4375.3191 | 4451.4739 | 3175.1 | 3409.8 | 3186.1 | 3454.7 | 3677.3 | 2636 | 2794.1 | 4310.6 | 4617.4 | 4099.5 | 4443.4 | 4803.7 | 3639.5 | 3935
2013-02-27 | 18 | 2013-02-27 18:00 | 32429.9167 | 4778.7942 | 3947.5439 | 4012.9784 | 2651 | 2819.7 | 2657.7 | 2879.6 | 3039.7 | 2060.5 | 2155.9 | 3935.4 | 4218.7 | 3743.2 | 4040.4 | 4313.8 | 3235.9 | 3444.8
2013-02-27 | 19 | 2013-02-27 19:00 | 34745.711 | 3770.9765 | 3043.1115 | 3100.7898 | 2090 | 2223.9 | 2067.1 | 2253.6 | 2384.8 | 1435.8 | 1502.5 | 3308.8 | 3506.6 | 3096.8 | 3374.8 | 3585.9 | 2569.1 | 2715.7
2013-02-27 | 20 | 2013-02-27 20:00 | 36640.0957 | 3190.9102 | 2605.8029 | 2657.4659 | 2151.7 | 2288.2 | 2218.2 | 2329.7 | 2470.7 | 1514.4 | 1590.8 | 3107 | 3380.8 | 2954.5 | 3134.9 | 3345.2 | 2330.2 | 2475.8
2013-02-27 | 21 | 2013-02-27 21:00 | 36636.1596 | 3034.8179 | 2458.0992 | 2501.8537 | 2233.8 | 2395.7 | 2193.5 | 2365.5 | 2541.3 | 1546.7 | 1657.9 | 2954.5 | 3266.7 | 2792.5 | 3002.7 | 3233.9 | 2197.7 | 2364.2
2013-02-27 | 22 | 2013-02-27 22:00 | 35666.8778 | 2873.2029 | 2325.9086 | 2344.0299 | 2216.5 | 2549.8 | 2081.5 | 2330.9 | 2696.2 | 1514.7 | 1815.5 | 2565.9 | 2887.1 | 2340.1 | 2563.9 | 2828.1 | 1758.8 | 1958.3
2013-02-27 | 23 | 2013-02-27 23:00 | 33712.888 | 2947.6493 | 2448.4928 | 2483.4708 | 2186.7 | 2577.6 | 2019.2 | 2261.8 | 2639.3 | 1466.4 | 1779.3 | 2212.9 | 2534.9 | 1938.9 | 2170.8 | 2452.7 | 1369.6 | 1587.1
2013-02-27 | 24 | 2013-02-28 | 31667.9323 | 3141.8602 | 2544.2869 | 2589.2299 | 2146.9 | 2522.8 | 1960.9 | 2205.4 | 2570.1 | 1422.7 | 1722.8 | 2062.6 | 2378.8 | 1823.8 | 2033.4 | 2284.9 | 1239.9 | 1426.8
2013-02-28 | 1 | 2013-02-28 01:00 | 30668.8242 | 2984.4289 | 2279.1801 | 2307.6518 | 2190.6 | 2423 | 2043.2 | 2225 | 2451.3 | 1428.1 | 1589.7 | 1926.3 | 2240.6 | 1702.6 | 1912.2 | 2148.9 | 1148 | 1320.1
2013-02-28 | 2 | 2013-02-28 02:00 | 30415.7135 | 2688.3105 | 2007.557 | 2060.7251 | 2166 | 2405.4 | 2018.7 | 2213.7 | 2447.5 | 1419.5 | 1588.6 | 1968.3 | 2293.9 | 1729.7 | 1944.9 | 2196.4 | 1175.5 | 1362.5
2013-02-28 | 3 | 2013-02-28 03:00 | 30471.7114 | 2411.8324 | 1799.015 | 1863.7199 | 2088.5 | 2334.3 | 1927.6 | 2115.8 | 2351.5 | 1329.6 | 1500.7 | 2132 | 2461.4 | 1908.3 | 2120.2 | 2392.5 | 1333.6 | 1541.3
2013-02-28 | 4 | 2013-02-28 04:00 | 31001.7407 | 2267.3014 | 1656.5428 | 1722.0771 | 2162.1 | 2384.1 | 1980.5 | 2167.9 | 2379.5 | 1375.4 | 1522.5 | 1780.1 | 2087.5 | 1527.1 | 1742.5 | 1978.3 | 1007.3 | 1178.7
2013-02-28 | 5 | 2013-02-28 05:00 | 32336.4968 | 2259.349 | 1707.4311 | 1774.3965 | 2300.8 | 2502.8 | 2115.3 | 2302.3 | 2493.5 | 1514.4 | 1641.1 | 1985.4 | 2306.3 | 1748.3 | 1962.7 | 2204.6 | 1205 | 1382.3
2013-02-28 | 6 | 2013-02-28 06:00 | 35388.0959 | 2254.3159 | 1736.8735 | 1806.1571 | 2321.7 | 2528.7 | 2186.2 | 2353.8 | 2552.9 | 1563 | 1705 | 2014.9 | 2363.5 | 1751.1 | 1986.2 | 2257 | 1238 | 1444.3
2013-02-28 | 7 | 2013-02-28 07:00 | 40081.2223 | 2136.2159 | 1587.7821 | 1660.2065 | 2295.5 | 2511.5 | 2171.2 | 2325.1 | 2532.5 | 1534.5 | 1683.2 | 2006 | 2377.1 | 1749.6 | 1993.7 | 2279 | 1240.4 | 1461.1
2013-02-28 | 8 | 2013-02-28 08:00 | 40736.9259 | 2089.4205 | 1501.5728 | 1583.2983 | 1973.3 | 2176.2 | 1831.4 | 1980 | 2179.2 | 1243.4 | 1382.3 | 1795 | 2174.5 | 1576.7 | 1811.1 | 2110.5 | 1140.2 | 1377.6
2013-02-28 | 9 | 2013-02-28 09:00 | 39013.6688 | 1847.5921 | 1387.9523 | 1457.5163 | 1538.6 | 1694.7 | 1445.2 | 1551.8 | 1702.9 | 834.5 | 926 | 1641.6 | 1911.3 | 1447 | 1662.4 | 1937.9 | 992.4 | 1204.8
2013-02-28 | 10 | 2013-02-28 10:00 | 37929.9673 | 1859.903 | 1379.1101 | 1449.6789 | 1155.2 | 1275.5 | 1065.2 | 1168.1 | 1279.3 | 515 | 569.9 | 1384.5 | 1615.6 | 1209.2 | 1404 | 1636.5 | 771.6 | 945.7
2013-02-28 | 11 | 2013-02-28 11:00 | 36850.0684 | 2026.1258 | 1577.9597 | 1640.2344 | 1233.5 | 1362 | 1131.3 | 1243.1 | 1365.9 | 586.4 | 653.3 | 1036.2 | 1236 | 875.1 | 1045.4 | 1244.7 | 542 | 684.6
2013-02-28 | 12 | 2013-02-28 12:00 | 35654.2976 | 1783.6651 | 1440.7163 | 1493.2397 | 1363.6 | 1498.9 | 1243.4 | 1364.4 | 1496.6 | 685.4 | 761.9 | 1042.1 | 1220.2 | 910.7 | 1063.8 | 1241.3 | 551.5 | 672.8
2013-02-28 | 13 | 2013-02-28 13:00 | 34429.5681 | 1514.7978 | 1216.8857 | 1266.2054 | 1433.5 | 1585.7 | 1293.8 | 1432.9 | 1586.1 | 745.7 | 842.7 | 995 | 1169 | 858.1 | 1013.3 | 1186.6 | 558.2 | 675.3
2013-02-28 | 14 | 2013-02-28 14:00 | 33398.1186 | 1455.0844 | 1078.4228 | 1135.9324 | 1551.4 | 1734.6 | 1389.5 | 1549.4 | 1737 | 851.3 | 982.5 | 1115.5 | 1282.6 | 990.3 | 1131.3 | 1297.8 | 574.7 | 685.4
2013-02-28 | 15 | 2013-02-28 15:00 | 32486.3833 | 1494.4598 | 1066.0537 | 1115.0131 | 1646.9 | 1856.2 | 1480.8 | 1645.5 | 1859.4 | 944 | 1101.1 | 1186.4 | 1354.5 | 1056.3 | 1204.3 | 1372 | 638.2 | 749.5
2013-02-28 | 16 | 2013-02-28 16:00 | 31882.8706 | 1794.3472 | 1375.9293 | 1419.0404 | 1635.7 | 1854.1 | 1561.1 | 1714.9 | 1935.2 | 1001.6 | 1165.3 | 1060.4 | 1215 | 942 | 1081.1 | 1235.5 | 526.7 | 624.6
2013-02-28 | 17 | 2013-02-28 17:00 | 31848.4338 | 1963.8031 | 1540.6148 | 1588.1049 | 1688.8 | 1885.4 | 1572.6 | 1777 | 1969.5 | 1013.4 | 1149.4 | 1040.2 | 1202.3 | 903.1 | 1063.2 | 1224.1 | 506.9 | 611.3
2013-02-28 | 18 | 2013-02-28 18:00 | 32441.5538 | 1619.1771 | 1296.7393 | 1346.4567 | 1452.5 | 1576.9 | 1369.4 | 1522.6 | 1639.4 | 750.6 | 811 | 923.2 | 1054.2 | 803.4 | 941.4 | 1072.1 | 410.3 | 484
2013-02-28 | 19 | 2013-02-28 19:00 | 34824.421 | 993.9006 | 739.117 | 785.2832 | 1274.4 | 1343.6 | 1240.4 | 1335.6 | 1397.8 | 575 | 583.3 | 1012.8 | 1119.7 | 918.8 | 1028 | 1135.7 | 389.9 | 443.8
2013-02-28 | 20 | 2013-02-28 20:00 | 36881.83 | 542.5055 | 393.0292 | 441.9124 | 1181 | 1223 | 1169.6 | 1225.7 | 1261.3 | 517.1 | 517.7 | 1237.8 | 1316.2 | 1169.6 | 1253 | 1335.7 | 560.6 | 588.5
2013-02-28 | 21 | 2013-02-28 21:00 | 37045.7765 | 530.7113 | 372.8689 | 423.0513 | 1078.5 | 1116.4 | 1082.1 | 1103.9 | 1133 | 441.7 | 448.4 | 1214.7 | 1289 | 1157.8 | 1232 | 1291.4 | 509.2 | 515.5
2013-02-28 | 22 | 2013-02-28 22:00 | 36205.1348 | 640.4867 | 471.4444 | 527.1787 | 1106.4 | 1161.1 | 1070.5 | 1106.8 | 1143 | 433.3 | 450.7 | 1020.4 | 1107.1 | 904.9 | 993.4 | 1060.3 | 306.5 | 317.2
2013-02-28 | 23 | 2013-02-28 23:00 | 34179.6043 | 699.3459 | 598.9939 | 640.4822 | 1094.5 | 1171.7 | 1046.1 | 1087.3 | 1148.3 | 419.7 | 440.4 | 892.5 | 987.3 | 779.1 | 857 | 949.4 | 224.1 | 264.1
2013-02-28 | 24 | 2013-03-01 | 32235.7768 | 618.8697 | 508.2068 | 549.2178 | 1040.2 | 1118.8 | 986.6 | 1023.4 | 1083.7 | 355.6 | 373.9 | 922.1 | 997.4 | 867.2 | 934.3 | 962.8 | 276.5 | 276.5

## SYSTEM-WIDE ERROR TRACKING
SYSTEM-WIDE
Monthly Average | 1011.247 | 1031.8357 | 588.2535 | 625.5364 | Monthly Average | 9.744% | 9.942% | 5.668% | 6.027% | Monthly Average | 45.79% | 11.79% | 43% | 22.86%
MAE [MW] |  |  |  |  | Absolute Percent Error of Inst. Cap [MW] |  |  |  |  | Percent of Hours [MW]
Operating Day | Day-Ahead |  | Hour-Ahead |  | Operating Day | Day-Ahead |  | Hour-Ahead |  | Operating Day | Day-Ahead |  | Hour-Ahead
| STWPF | COP HSL | STWPF | COP HSL |  | STWPF | COP HSL | STWPF | COP HSL |  | Estimated Uncurtailed Output >STWPF | COP HSL-STWPF > 2% Installed Capacity | Estimated Uncurtailed Output >STWPF | COP HSL-STWPF > 2% Installed Capacity
1 | 1137.1798 | 1117.1965 | 705.3894 | 662.6364 | 1 | 10.96% | 10.76% | 6.797% | 6.385% | 1 | 54% | 0% | 67% | 0%
2 | 1164.6865 | 1165.3865 | 545.1375 | 575.1231 | 2 | 11.22% | 11.23% | 5.253% | 5.541% | 2 | 67% | 0% | 33% | 0%
3 | 1318.2672 | 1310.4803 | 697.8224 | 705.9411 | 3 | 12.7% | 12.63% | 6.724% | 6.802% | 3 | 63% | 0% | 63% | 13%
4 | 902.1396 | 970.3869 | 685.775 | 791.4083 | 4 | 8.692% | 9.35% | 6.608% | 7.625% | 4 | 4% | 0% | 17% | 13%
5 | 511.3608 | 544.0494 | 348.7851 | 357.3072 | 5 | 4.927% | 5.242% | 3.361% | 3.443% | 5 | 38% | 0% | 38% | 0%
6 | 566.2435 | 560.5852 | 672.7959 | 704.1828 | 6 | 5.456% | 5.401% | 6.483% | 6.785% | 6 | 63% | 0% | 42% | 17%
7 | 688.2522 | 667.5406 | 304.7252 | 329.4481 | 7 | 6.632% | 6.432% | 2.936% | 3.174% | 7 | 67% | 0% | 46% | 4%
8 | 321.2078 | 315.6219 | 386.7636 | 408.3595 | 8 | 3.095% | 3.041% | 3.727% | 3.935% | 8 | 46% | 0% | 38% | 0%
9 | 935.9546 | 736.6597 | 246.2844 | 248.6384 | 9 | 9.018% | 7.098% | 2.373% | 2.396% | 9 | 100% | 38% | 54% | 38%
10 | 1496.0984 | 1636.5942 | 552.9121 | 631.0383 | 10 | 14.42% | 15.77% | 5.327% | 6.08% | 10 | 0% | 25% | 29% | 21%
11 | 1669.0751 | 1715.9918 | 534.8745 | 626.0345 | 11 | 16.08% | 16.53% | 5.154% | 6.032% | 11 | 0% | 0% | 25% | 17%
12 | 1422.195 | 1465.0158 | 999.0859 | 1005.8817 | 12 | 13.7% | 14.12% | 9.626% | 9.692% | 12 | 21% | 0% | 38% | 8%
13 | 840.113 | 967.5297 | 400.0027 | 512.1611 | 13 | 8.095% | 9.322% | 3.854% | 4.935% | 13 | 4% | 25% | 21% | 25%
14 | 709.2604 | 710.7271 | 411.43 | 364.205 | 14 | 6.834% | 6.848% | 3.964% | 3.509% | 14 | 83% | 4% | 54% | 21%
15 | 1419.1891 | 1440.5641 | 460.8811 | 455.8395 | 15 | 13.67% | 13.88% | 4.441% | 4.392% | 15 | 79% | 17% | 63% | 8%
16 | 1337.8847 | 1410.6597 | 608.3731 | 682.019 | 16 | 12.89% | 13.59% | 5.862% | 6.571% | 16 | 8% | 13% | 13% | 17%
17 | 1054.6472 | 936.3695 | 510.3966 | 484.7391 | 17 | 10.16% | 9.022% | 4.918% | 4.671% | 17 | 88% | 58% | 63% | 75%
18 | 779.8528 | 814.9678 | 772.4814 | 771.7597 | 18 | 7.514% | 7.852% | 7.443% | 7.436% | 18 | 63% | 0% | 58% | 25%
19 | 1349.7995 | 1420.9553 | 938.4274 | 978.4802 | 19 | 13.01% | 13.69% | 9.042% | 9.428% | 19 | 29% | 13% | 46% | 38%
20 | 1083.9492 | 1198.1451 | 752.3088 | 1008.211 | 20 | 10.44% | 11.54% | 7.249% | 9.714% | 20 | 25% | 79% | 8% | 96%
21 | 1973.0192 | 2109.2775 | 1187.0012 | 1319.6492 | 21 | 19.01% | 20.32% | 11.44% | 12.72% | 21 | 13% | 21% | 21% | 29%
22 | 550.6133 | 551.4901 | 345.5047 | 415.3536 | 22 | 5.305% | 5.314% | 3.329% | 4.002% | 22 | 54% | 0% | 29% | 13%
23 | 766.4815 | 786.9498 | 582.4835 | 602.2825 | 23 | 7.385% | 7.582% | 5.612% | 5.803% | 23 | 33% | 0% | 46% | 4%
24 | 1092.7822 | 1070.9883 | 604.8132 | 586.1016 | 24 | 10.53% | 10.32% | 5.828% | 5.647% | 24 | 67% | 0% | 71% | 8%
25 | 919.7619 | 910.7002 | 688.6109 | 783.0638 | 25 | 8.862% | 8.775% | 6.635% | 7.545% | 25 | 63% | 4% | 46% | 83%
26 | 1126.5964 | 1199.3344 | 623.8597 | 671.8305 | 26 | 10.86% | 11.56% | 6.011% | 6.473% | 26 | 29% | 25% | 29% | 13%
27 | 873.3044 | 790.0559 | 583.37 | 512.1683 | 27 | 8.415% | 7.612% | 5.621% | 4.935% | 27 | 92% | 8% | 79% | 21%
28 | 305.0009 | 367.1762 | 320.8032 | 321.1566 | 28 | 2.939% | 3.538% | 3.091% | 3.094% | 28 | 29% | 0% | 67% | 33%

## TOTAL INSTALLED CAPACITY
TOTAL INSTALLED CAPACITY (Sum of RARF #Turbines * Turbine RTG) with few manual corrections | 10378.505
SOUTH-HOUSTON WITHOUT HHGT INSTALLED CAPACITY | 1612.97
WEST_NORTH WITH HHGT INSTALLED CAPACITY | 8765.535
sum check | 10378.505
Sub-Region: Coastal INSTALLED CAPACITY | 1269.63