ERCOT Operations Report

February 2013 ROS & OWG

Frequency Control

| Time | Freq (Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 2/16/2013 17:57 | 59.850 | 220 | Unit runback and trip over a 6 minute period with approximately 1150 MW net. |
| 2/16/2013 20:03 | 59.897 | 20 | Gen Deviation of 455 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

PMU Events

| Date | Events | Duration | Summary |
| --- | --- | --- | --- |
| 2/16/2013 17:57 | Unit trip | Approx. 5 min | The event was caused by the loss of two combined cycles. Units ranback and tripped over a 6 minute period with approximately 1150 MW net. The frequency dropped to 59.85 Hz due to the event. No significant oscillation was observed in this event. |

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 2/16/13 17:59:01 | 2/16/13 18:02:56 | 0:03:55 | 229.02 |  |
| 2/16/13 20:02:32 | 2/16/13 20:06:28 | 0:03:57 | 469.76 |  |

RUC Commitments

SCED Congestion Management Activity

Congestion affected by outages (*) Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days | MP |
| --- | --- | --- | --- |
| Asphalt Mines - Uvalde Aep & Odlaw Switchyard 138kV | Hamilton Road - Maverick 138kV | 21 | N |
| Scurry Switch - Sun Switch 138 kV | Aspermont Aep 138_69T1 138/69kV | 13 | N |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Aspermont Aep 138_69T1 138/69kV | 12 | N |
| Fort Stockton Plant - Barrilla 138kV | Fort Stockton Switch - Barrilla 69 kV | 12 | N |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Aspermont AEP - Aspermont Continental 69kV | 9 | N |
| Basecase | Laquinta - Lobo 138 kV | 9 | N |
| Scurry Switch - Sun Switch 138 kV | Aspermont AEP - Aspermont Continental 69kV | 8 | N |
| Pawnee Switching Station - Lon Hill 345 kV | Rincon - Airco Aep 138kV | 8 | N |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 7 | N |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345kV | Fort Worth Substation - Teasley Substation 138kV | 6 | N |
| Coleto Creek - Pawnee Switching Station 345kV | Coleto Creek - Kenedy Swtich 138kV | 6 | N |
| Basecase | W_TO_N | 5 | N |
| Pawnee Switching Station - Lon Hill 345 kV | Laquinta - Lobo 138 kV | 5 | N |
| DCKT Roanoke Switch - West Denton and Lewisville Switch 345kV | Jim Christal Substation - North Denton Interchange 138 kV | 5 | N |
| Killeen Switch Axfmr2h (3) 345/138kV | Killeen Switch Axfmr1h (3) 345/138kV | 5 | N |
| Bosque Switch - Whitney 138 kV | Lake Whitney Tnp - Whitney 138kV | 4 | N |
| Bosque Switch - Whitney 138 kV | Bosque Switch - Lake Whitney Tnp 138 kV | 4 | N |
| Aspermont Aep - Spur 138KV | Wolfgang - Rotan 69kV | 4 | N |
| Laquinta - Lobo 138 kV | Laquinta - Bruni Tap 138kV | 4 | N |
| Aspermont Aep - Spur 138KV | Spur 138_69_1 138/69kV | 3 | N |
| Comanche Switch (Oncor) - Brown Switch 345kV | Brown Switch - Killeen Switch 345kV (35095) | 3 | N |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Highlands Tnp - West Tnp 138kV | 3 | N |
| DCKT Sweetwater East Switch - Abilene Mulberry Creek & Long Creek 345kV | Radium - Anson 69kV | 3 | N |
| Basecase | Langford Wind Power Llc - Santiago 138kV | 2 |  |
| Pawnee Switching Station - Lon Hill 345 kV | Rincon - Bonnieview 69kV | 2 |  |
| Comanche Switch (Oncor) - Brown Switch 345kV | Brown Switch - Killeen Switch 345kV (35090) | 2 |  |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Rincon - Airco Aep 138kV | 2 |  |
| DCKT Whitepoint - Lon Hill & South Texas Project 345kV | Sinton - Skidmore 69 kV | 2 |  |
| Nelson Sharpe - Lon Hill 345kV | Kingsville - Kleberg Aep 138kV | 2 |  |
| Nelson Sharpe - Lon Hill 345kV | Celanese Bishop - Kleberg Aep 138kv | 2 |  |
| Lobo 2_345_138_H 345/138 kV | Laquinta - Lobo 138 kV | 2 |  |
| DCKT Morgan Creek Ses - China Grove Switch 138kV | Radium - Anson 69kV | 2 |  |
| West Denton - Roanoke Switch 345kV | Fort Worth Substation - Teasley Substation 138kV | 2 |  |
| DCKT Temple Northwest - Belton & Temple North 138kV | Temple Switch - Temple Southeast 138 kV | 2 |  |
| Orange Grove Switching Station - Lon Hill 138 kV | Smith - Edroy 69kV | 2 |  |
| Vernon 138_69t1 138/69 kV | Aspermont AEP - Aspermont Continental 69kV | 2 |  |
| DCKT North Edinburg - Rio Hondo - South Santa Rosa - Harlingen Switch 345kV | Rio Hondo - Burns Sub 138kV | 2 |  |
| Moss Switch - Holt Switch & Amoco North Cowden 138kV | Odessa North - Odessa Basin Switch 69 kV | 2 |  |
| Victoria - Coleto Creek 138kV (Coleto_Victor1) | Victoria - Coleto Creek 138kV (Coleto_Victor2) | 2 |  |
| Scurry Switch - Sun Switch 138 kV | Hamlin Shell - Aspermont Continental 69kV | 1 |  |
| Salt Creek Bepc - Spur And Scurry Switch 138kV | Wolfgang - Rotan 69kV | 1 |  |
| Basecase | Post Oak Wind (Potomes) 138kV | 1 |  |
| Coleto Creek - Pawnee Switching Station 345kV | Fallscty - Kenedy Switch 138kV | 1 |  |
| DCKT Lewisville Switch - Carrollton Northwest 345 kV | Lewisville Switch - Jones Street Tnp 138kV | 1 |  |
| DCKT Graham Ses - Long Creek & Cook Field Road Switch 345kV | Orlando - Vernon 138kV | 1 |  |
| DCKT Graham Ses - Long Creek & Cook Field Road Switch 345kV | Leon Switch - Eastland Tap 69kV | 1 |  |
| DCKT Graham Ses - Long Creek & Cook Field Road Switch 345kV | Brown Switch - Killeen Switch 345kV (35095) | 1 |  |
| Lobo 2_345_138_H 345/138 kV | Asherton - Catarina 138kV (Ashert_Catari0) | 1 |  |
| DCKT Morgan Creek Ses - China Grove Switch 138kV | Morgan Creek Ses Axfmr3h 138/69 kV | 1 |  |
| West Denton - Roanoke Switch 345kV | Jim Christal Substation - North Denton Interchange 138 kV | 1 |  |
| Ajo - Rio Hondo 345 KV | North Edinburg Nedin_XC2 345kV | 1 |  |
| Ajo - Rio Hondo 345 KV | Rio Hondo Riohondo_345L 345kV | 1 |  |
| Ajo - Rio Hondo 345 KV | Las Pulgas - Rio Hondo 138kV | 1 |  |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Asherton - Catarina 138kV (Ashert_Catari0) | 1 |  |
| Lobo - San Miguel 345_138 KV Switchyards 345 KV | Laquinta - Lobo 138 kV | 1 |  |
| DCKT Fayette Plant 2 - Lytton Springs & Holman Aen 345 kV | Austrop - Garfield Lcra 345kV | 1 |  |
| Belton Southwest - Killeen Switch & Belton 138kV | Killeen Elm - Killeen Taft Street 138kV (641_B) | 1 |  |
| Horse Hollow Generation Tie T1h (3) 345/138kV | Horse Hollow Generation Tie T2h (3) 345/138kV | 1 |  |
| Falcon Seaboard - Morgan Creek Ses 345kV | McDonald Road - Forsan Tap 138kV | 1 |  |
| DCKT Temple Switch - Lake Creek Ses & Temple Pecan Creek 345kV | Temple Switch Axfmr1h 345/138kV | 1 |  |
| Lewisville Switch - Carrollton Northwest 345kV (105_A) | Highlands Tnp - West Tnp 138kV | 1 |  |
| DCKT Big Brown SES - Richland Chambers 345 kV | Trinidad Ses Axfmr6 (3) 345/138kV | 1 |  |
| DCKT Austrop - Garfield Lcra & Zorn 345 kV | Garfield Aen Gf_At_2 345/138 kV | 1 |  |
| Weil Tract - Lon Hill 138kV | Weil Tract - Citgo West 138kV | 1 |  |
| DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345kV (240) | 1 |  |
| Falcon Seaboard - Midland East 345kV | McDonald Road - Forsan Tap 138kV | 1 |  |
| Illinois #4 - Fort Lancaster 138kV | Sonora - Friess Ranch 69kV | 1 |  |
| Paloduro Sub - Dilley Switch Aep 138kV | Dilley Switch Aep 138_69A1 138/69kV | 1 |  |
| DCKT Salado Switch - Hutto Switch 345kV | Sandow Switch - Austrop 345kV (450) | 1 |  |
| North Edinburg - Rio Hondo 345 kV | Aderhold - Elsa 138kV | 1 |  |
| Cisco - Putnam 138kV & Leon Switch 138kV | Abilene South - Potosi Tap 138kV | 1 |  |
| Lake Pauline - Munday East 138kV | Lake Pauline 138_69_1 138/69 kV | 1 |  |
| Bosque Switch - Elm Mott 345 kV | Elm Mott - Rogers Hill Bepc 138kV | 1 |  |
| DCKT Grandvew - Highland & Braunig 138kV | Kirby - Holbrook 138kV | 1 |  |
| Odessa North Axfmr1 138/69 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |  |
| Kenedy Switch - Coleto Creek 138kV | Beeville - Normanna 69kV | 1 |  |
| DCKT Comanche Peak Ses Units 1 & 2 | Laquinta - Lobo 138 kV | 1 |  |
| Salado Switch - Temple Switch 345kV | Sandow Switch - Austrop 345kV (450) | 1 |  |
| DCKT South Channel-Pair & Shell 138kV | Conial - Waburn 138kV | 1 |  |
| DCKT Sonora - Friend Ranch 138kV and 69kV | Sonora - Friess Ranch 69kV | 1 |  |
| Haskell - Weinert - Munday Aep 69kV | Munday Aep - Bkem Munday 69kV | 1 |  |
| DCKT Brown Switch - Killeen Switch 345kV | Sonora - Friess Ranch 69kV | 1 |  |
| Bosque Switch - Whitney 345 kV | Elm Mott - Rogers Hill Bepc 138kV | 1 |  |
| North Edinburg - Lon Hill 345kV | Las Pulgas - Rio Hondo 138kV | 1 |  |
| Rodd Field - Holly 138kV | Airline Aep - Cabaniss 138 kV | 1 |  |

Note: MP column refers to Mitigation plans involving load shed and were only listed which met our recurring congestion criteria.

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 5 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

- None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

None

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

02/19 SCED failed but was restored and ran successfully within the same SCED interval.

Communication Issues

None

## ERCOT peak (Unofficial)

02/28 08:00 40,752 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2010 | 2011 | 2012 | 2013 |
| January | 3.78 | 2.91 | 2.94 | 3.50 |
| February | 3.79 | 3.46 | 2.51 | 2.83 |
| March | 2.24 | 2.02 | 3.49 |  |
| April | 2.47 | 3.55 | 2.78 |  |
| May | 2.63 | 3.27 | 3.09 |  |
| June | 2.84 | 2.28 | 2.85 |  |
| July | 2.39 | 1.63 | 2.85 |  |
| August | 2.29 | 2.28 | 2.96 |  |
| September | 3.14 | 2.70 | 3.43 |  |
| October | 2.37 | 3.51 | 2.99 |  |
| November | 3.46 | 3.38 | 2.90 |  |
| December | 2.60 | 2.99 | 3.47 |  |
| Annual Average | 2.83 | 2.83 | 3.02 | 3.17 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 2/10/2013 | 20:08 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None